Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13236 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10466 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.051544 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.13409 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.22557 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.22557 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.22557 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.22557 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.056216 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.074649 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.074649 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.040856 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.27152 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.09003 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.039778 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.039214 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11228 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.079581 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.041915 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.036889 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10062 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.079581 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.039359 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10173 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.17248 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.17248 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.17248 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.17248 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.042711 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.05666 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.05666 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.031229 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.20832 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.068446 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030385 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.086024 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.24633 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.056928 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.35698 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.24633 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.446 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.3777 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.24302 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.14842 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.030165 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.057622 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.039802 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.35036 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.22111 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.055688 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.034907 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.034288 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.11512 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.046661 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.097733 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.060881 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.23361 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.37968 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.09778 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.053623 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.030939 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.049827 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041794 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.035327 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.035327 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.0353 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.044464 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.079581 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.041915 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.036889 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10062 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.079581 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.039359 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10173 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.17248 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.17248 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.17248 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.17248 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.042711 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.05666 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.05666 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.031229 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.20832 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.068446 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030385 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.086024 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.049038 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.045471 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.096904 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55707 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.058029 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.049038 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11271 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.06169 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.069278 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.069278 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.069278 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.069278 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.030851 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040413 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.091834 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.096043 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.096043 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.080633 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.073662 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.058629 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.058449 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.072905 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.068864 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041876 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.14641 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.24633 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.056928 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.35698 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.24633 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.446 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.3777 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.3777 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.3777 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.3777 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.24302 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.14842 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.030165 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.095676 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.091126 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.12329 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.1432 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.095676 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.032995 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.057143 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.12007 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16358 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.15121 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.15121 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.15121 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.15121 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.62565 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24931 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24931 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.058142 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13379 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.034177 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10963 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.048041 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.03111 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.03528 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13751 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.045484 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.64669 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.64669 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.64669 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.045484 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.64669 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.64669 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.64669 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.067136 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.2251 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.19413 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.19413 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.19413 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24757 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24757 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.14891 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.067404 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.067404 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.067136 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.2251 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.64669 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.64669 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.64669 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10364 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10364 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.41411 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.048026 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.061541 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.24721 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.41411 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.037037 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.057527 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.22383 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.19929 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.19929 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.19929 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.19929 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.051943 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10159 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10159 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.034968 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.15721 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.24188 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.086124 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.037758 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.099913 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.10457 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.093483 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.037758 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.044521 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.060619 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11227 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11503 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.10805 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.10805 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.10805 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.036868 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.10805 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.043516 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.24816 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.19689 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.19689 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.086167 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.040103 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10017 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.04481 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.056346 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.062004 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.082143 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.080039 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.045098 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11478 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.033158 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.064256 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.046453 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.35775 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.2283 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.030089 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.062301 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.041717 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.041203 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.12209 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.053426 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.10464 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.032695 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.067556 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.24096 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.38712 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.10466 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.060276 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.037809 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.056469 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.048467 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.042562 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.042562 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.034956 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.42912 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.041648 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.051223 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.037559 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053466 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.096578 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.03128 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.045993 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21146 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18048 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18048 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18048 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18048 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044016 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.090007 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.090007 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12219 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072968 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.034916 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.63048 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.63048 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.63048 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.63048 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.33537 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1182 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.034916 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.63048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.63048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.63048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.63048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.33537 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1182 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.87073 |  | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | TDF Impact | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.081072 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.048606 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.031261 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.098553 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.081072 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.032007 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11454 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.083377 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.083377 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.083377 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.083377 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.050476 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.065499 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.065499 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.045117 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.072052 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.031489 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.032387 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.039354 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.075746 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.035095 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054695 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.037221 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.037586 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.037586 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.037586 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.037586 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.038819 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.046409 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.046409 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.049661 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030139 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11874 |  | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62144 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.030148 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15063 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62144 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035027 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34822 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.070928 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.0361 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.065259 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.090333 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.070928 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.058813 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.099858 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.17986 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.14567 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.14567 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.076698 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.075789 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.07433 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.14223 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048656 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.053496 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.039911 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.045167 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.0725 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.052 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-084 |  | Non-Converged |  |  | 0.039191 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.089656 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-091 |  | Non-Converged |  |  | 0.041576 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.094759 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.044958 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.053536 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.042047 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.041452 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.077171 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.077635 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-175 |  | Non-Converged |  |  | 0.037968 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040668 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-181 |  | Non-Converged |  |  | 0.038391 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.045859 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.10316 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.037415 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.09446 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030784 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.05038 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.043258 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.14184 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.031245 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.036797 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.079599 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.079599 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.047726 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055659 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.078392 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.087785 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.044397 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.10017 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.11411 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.089656 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.045614 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.037559 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053466 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.096578 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.03128 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.045993 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21146 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18048 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18048 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18048 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18048 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044016 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.090007 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.090007 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12219 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072968 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.037559 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053466 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.096578 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.03128 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.045993 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21146 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044016 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.090007 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.090007 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12219 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072968 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11476 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.063712 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14867 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11476 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16689 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.062021 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.085371 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.085371 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10036 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.030092 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.031082 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.037758 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.099913 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.10457 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.093483 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.037758 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.044521 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.060619 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11227 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11503 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.10805 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.10805 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.10805 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.036868 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.10805 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.043516 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.24816 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.19689 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.19689 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.086167 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.040103 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10017 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.04481 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.056346 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.062004 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.082143 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.080039 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.045098 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11478 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11476 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.063712 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14867 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11476 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16689 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.062021 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.085371 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.085371 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10036 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.030092 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.031082 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.089602 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.08586 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11728 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13676 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.089602 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.052359 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11468 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15702 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14409 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14409 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14409 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14409 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24355 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24355 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.053041 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.1265 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10372 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.043212 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.030851 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13142 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.0306 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.034816 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.064915 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.0306 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.043532 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.10445 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.082829 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.063536 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.033011 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.040669 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.10773 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.052637 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.097337 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.04007 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.03686 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.03686 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.067258 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.18419 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.096519 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.033343 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.099778 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.060738 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.032172 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.057329 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.04834 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.083998 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.045029 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.050812 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.057304 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053342 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10478 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.56548 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.057605 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.057304 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036611 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.12066 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.057613 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.039649 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.039649 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.039649 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.037057 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.039649 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.038288 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047946 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.09977 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10417 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10417 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.088404 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.044376 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.066797 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.066079 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.08063 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.076564 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.049424 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.15476 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.032977 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.14223 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.042007 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.053496 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.039911 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.045167 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.062629 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.052 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-084 |  | Non-Converged |  |  | 0.039191 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.089656 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-091 |  | Non-Converged |  |  | 0.041576 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.094759 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.044958 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.053536 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.042047 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.041452 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.062097 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.055089 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-175 |  | Non-Converged |  |  | 0.037968 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040668 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-181 |  | Non-Converged |  |  | 0.038391 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.045859 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.052383 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.037415 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.09446 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030784 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.05038 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.043258 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.14184 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.031245 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.036797 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.079599 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.079599 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.047726 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055659 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.078392 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.087785 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.044397 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.10017 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.044017 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.089656 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.045056 |  | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.090012 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.086253 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11781 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13739 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.090012 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.052599 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11521 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15773 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14475 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14475 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14475 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14475 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24467 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24467 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.053284 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12707 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.1042 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.04341 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.030992 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13202 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.037018 |  | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.036338 |  | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.037258 |  | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.036864 |  | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.042956 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.039338 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.21809 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.052054 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.042956 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.046921 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.055346 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.061499 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.061499 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.061499 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.061499 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044883 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.053452 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.053452 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030475 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.065452 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.042162 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.074433 |  | Single 640065 AXTELL3 345 640312 PAULINE3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.037559 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053466 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.096578 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.03128 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.045993 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21146 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18048 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044016 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.090007 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.090007 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12219 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072968 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.030014 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.14224 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.039952 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.037389 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.030014 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.20514 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.037903 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.039057 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.039057 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.039057 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.039057 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.038035 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.045941 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.045941 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.074526 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.045374 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.034783 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.055498 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.045548 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072253 |  | Single 539679 GRTBEND6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11642 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.06461 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.057972 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14529 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11642 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.061529 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.14744 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.24056 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.24056 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.24056 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.24056 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.066406 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.08575 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.08575 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.050108 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.28702 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10128 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.030033 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.048914 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.048289 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.036892 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12426 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.042956 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.042502 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.24074 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.052054 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.042956 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.048091 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.055346 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044883 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.053452 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.053452 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.037632 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.065452 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.042162 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.074433 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.033602 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.051144 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.097928 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.036626 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.033602 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.15068 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.10804 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054689 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.037328 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038407 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038407 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038407 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.054564 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038407 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.049997 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.038506 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.041081 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.041081 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.047431 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.097682 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.045489 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.16286 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.034495 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.055312 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.04219 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.03945 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.18028 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.061696 |  | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.030329 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.040198 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.070023 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.057782 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.031245 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.035105 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.032932 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.054465 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.074194 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.034502 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.079861 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.031605 |  | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.075257 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.062485 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.079461 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.075257 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.086441 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.055332 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.055332 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.055332 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.055332 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.14774 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.16038 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.16038 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.085212 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041588 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.047082 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.038981 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.037644 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.030634 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.038291 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.043648 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.03536 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.03536 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056551 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.036833 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.072502 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.080843 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.058993 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.030172 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.0306 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.034816 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.064915 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.0306 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.043532 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.10445 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.082829 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.063536 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.033011 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.040669 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.10773 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.052637 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.097337 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.04007 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.03686 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.03686 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.067258 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.18419 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.096519 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.033343 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.099778 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.060738 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.032172 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.057329 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.04834 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.083998 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.045029 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.050812 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62144 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.030148 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15063 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62144 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035027 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34822 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.030014 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.14224 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.039952 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.037389 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.030014 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.20514 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.037903 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.039057 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.039057 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.039057 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.039057 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.038035 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.045941 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.045941 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.074526 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.045374 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.034783 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.055498 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.045548 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072253 |  | Single 532871 CIRCLE6 230 763862 G19-054-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.23836 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.050295 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.34819 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.23836 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.43694 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.36746 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.36746 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.36746 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.36746 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.23241 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.14079 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.034916 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.63048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.63048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.63048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.63048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.33537 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1182 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.089602 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.062485 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13676 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.089602 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15702 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14409 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14409 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14409 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14409 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.14774 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24355 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24355 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10372 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041588 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.089602 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.08586 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11728 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13676 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.089602 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.052359 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11468 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15702 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14409 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14409 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14409 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14409 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.62023 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24355 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24355 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.053041 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.1265 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10372 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.043212 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.030851 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13142 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.1221 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.17836 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.1221 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.22382 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18823 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18823 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18823 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18823 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.37612 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.37612 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.11905 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.072119 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.033158 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.064256 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.046453 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.35775 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.2283 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.030089 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.062301 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.041717 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.041203 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.12209 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.053426 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.10464 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.032695 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.067556 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.24096 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.38712 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.10466 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.060276 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.037809 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.056469 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.048467 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.042562 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.042562 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.034956 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.041648 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.051223 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.090036 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.049984 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.045128 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.11235 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.090036 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.047927 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11392 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18641 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18641 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18641 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18641 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.051494 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.066433 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.066433 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.038989 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.22278 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.078357 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.038018 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.03751 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.096751 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.72851 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.086282 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.72851 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034003 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.058281 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.037418 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.034806 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035793 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.049516 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.044461 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.034387 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.045468 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.058624 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.04881 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.04881 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.068499 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.033053 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.03122 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.034206 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.044688 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.086641 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.096128 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.068115 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.033672 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.040142 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.033514 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.057304 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053342 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10478 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.56548 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.057605 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.057304 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036611 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.12066 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.057613 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.037057 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.061499 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.038288 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047946 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.09977 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10417 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10417 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.088404 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.065452 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.066797 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.066079 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.08063 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.076564 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.049424 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.15476 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.032977 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.036964 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.031542 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.033897 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.040547 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.046456 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.1357 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.031549 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.040608 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.039857 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.14188 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.037031 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.066072 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.066072 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.034023 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.038573 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.068191 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.11232 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.030757 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.15627 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.046456 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62144 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.030148 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15063 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62144 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035027 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34822 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.057304 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053342 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10478 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.057605 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.057304 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036611 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.12066 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.057613 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.039649 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.039649 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.039649 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.037057 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.039649 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.038288 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047946 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.09977 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10417 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10417 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.088404 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.044376 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.066797 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.066079 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.08063 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.076564 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.049424 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.15476 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.032977 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62144 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.030148 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15063 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62144 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.035027 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34822 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.16566 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.075988 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26749 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030799 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.45277 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.54966 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.057304 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053342 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10478 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.56548 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.057605 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.057304 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036611 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.12066 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.057613 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.039649 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.039649 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.039649 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.037057 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.039649 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.038288 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047946 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.09977 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10417 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10417 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.088404 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.044376 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.066797 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.066079 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.08063 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.076564 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.049424 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.15476 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.032977 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.090012 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.086253 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.11781 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13739 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.090012 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.052599 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11521 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15773 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14475 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14475 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14475 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14475 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24467 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24467 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.053284 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12707 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.1042 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.04341 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.030992 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13202 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.16566 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.075988 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26749 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030799 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.45277 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.54966 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.030798 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.053205 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.043978 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.51572 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.046234 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.036838 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.031312 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.1443 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.051894 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.11695 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.030375 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.061939 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.10921 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.055863 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052686 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.046788 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.047778 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.042502 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.24074 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.030822 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.032645 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.048091 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.033985 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.037632 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.031026 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.035999 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.033926 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.031988 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.03154 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.050626 |  | Single 640065 AXTELL3 345 640374 SWEETW3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11642 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.06461 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.057972 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14529 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11642 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.061529 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.14744 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.24056 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.24056 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.24056 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.24056 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.066406 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.08575 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.08575 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.050108 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.28702 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10128 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.030033 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.048914 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.048289 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.036892 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12426 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.037758 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.099913 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.10457 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.093483 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.037758 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.044521 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.060619 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11227 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11503 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.10805 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.10805 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.10805 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.036868 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.10805 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.043516 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.24816 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.19689 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.19689 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.086167 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.040103 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10017 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.04481 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.056346 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.062004 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.082143 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.080039 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.045098 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11478 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.075257 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.062485 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.079461 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.075257 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.086441 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.055332 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.055332 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.055332 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.055332 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.14774 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.16038 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.16038 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.085212 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.041588 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11476 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.063712 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14867 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11476 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16689 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.28634 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.28634 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.28634 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.28634 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.062021 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.085371 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.085371 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10036 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.030092 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.031082 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.16566 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.075988 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26749 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030799 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.45277 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.54966 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.14223 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.042007 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.053496 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.039911 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.045167 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.062629 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.052 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-084 |  | Non-Converged |  |  | 0.039191 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.089656 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-091 |  | Non-Converged |  |  | 0.041576 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.094759 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.044958 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.053536 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.042047 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.041452 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.062097 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.055089 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-175 |  | Non-Converged |  |  | 0.037968 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.040668 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-181 |  | Non-Converged |  |  | 0.038391 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.045859 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.052383 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.037415 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.09446 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030784 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.05038 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.043258 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.14184 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.031245 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.036797 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.079599 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.079599 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.047726 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055659 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.078392 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.087785 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.044397 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.10017 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.044017 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.089656 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.045056 |  | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.042502 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.24074 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.030822 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.032645 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.048091 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.033985 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.037632 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.031026 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.035999 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.033926 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.031988 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.03154 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.050626 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.051778 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.0311 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.039206 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.12605 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.06269 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.051778 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.044256 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.066539 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.078801 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.078801 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.078801 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.078801 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.043648 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.052698 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.052698 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.032809 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.08381 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.048525 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030795 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.067633 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11476 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.063712 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14867 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11476 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16689 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.062021 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.085371 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.085371 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10036 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.030092 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.031082 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.11626 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.16983 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.11626 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21312 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.17923 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.17923 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.17923 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.17923 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.35814 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.35814 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.11336 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.068672 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.090036 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.049984 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.045128 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.11235 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.090036 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.047927 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11392 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18641 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18641 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18641 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18641 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.051494 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.066433 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.066433 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.038989 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.22278 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.078357 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.038018 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.03751 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.096751 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.5146 |  | Single 531365 BIRDCTY3 115 531487 MCDONLD3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.15567 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054804 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26983 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18761 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14462 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.031044 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.047777 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.036252 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.076298 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.036202 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.057579 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.039258 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.030106 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.031646 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.035296 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.055612 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.037204 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.04832 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.03822 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.060817 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.037559 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053466 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.096578 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.03128 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.045993 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21146 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18048 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18048 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18048 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18048 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044016 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.090007 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.090007 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12219 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072968 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.72851 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.086282 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.72851 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034003 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.03289 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.040719 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.084463 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.038051 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.03289 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.092807 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.077886 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.044185 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.039627 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.04418 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.04418 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.04418 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.036609 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.04418 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.034555 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.033032 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.037204 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.037204 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.03678 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.063223 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.050529 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.099798 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.032374 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.039577 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.032744 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.030634 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.1094 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.054682 |  | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62144 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.048026 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.061541 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.24721 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62144 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.037037 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.057527 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.22383 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.19929 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.19929 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.19929 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.19929 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.051943 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10159 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10159 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.034968 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.15721 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34822 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.086124 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.042502 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.24074 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.030822 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.032645 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.048091 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.033985 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.037632 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.031026 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.035999 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.033926 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.031988 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.03154 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.050626 |  | P42:345:NPPD:BKR-SW-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.070928 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.0361 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.065259 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.090333 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.070928 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.058813 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.099858 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.090399 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.17986 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.14567 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.14567 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.076698 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.075789 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.07433 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.037559 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053466 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.34819 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.03128 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.045993 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.43694 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.36746 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.36746 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.36746 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.36746 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044016 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.090007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.090007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.23241 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.072968 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.057304 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053342 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10478 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.56548 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.057605 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.057304 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036611 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.12066 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.057613 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.039649 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.039649 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.039649 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.037057 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.039649 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.038288 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047946 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.09977 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.10417 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.10417 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.088404 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.044376 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.066797 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.066079 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.08063 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.076564 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.049424 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.15476 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.032977 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.41793 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.051809 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.065239 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.25101 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.41793 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040766 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.061295 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.22762 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.20306 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.20306 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.20306 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.20306 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.055777 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.1054 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.1054 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.038772 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.16096 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.2457 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030578 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.089887 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.041552 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.032273 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10378 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.10822 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.097251 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.041552 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.0482 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.064314 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11615 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11879 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.11179 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.11179 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.11179 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.040655 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.11179 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047302 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.25196 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.20067 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.20067 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.090012 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.043804 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10389 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.048478 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.060141 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.065774 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.085984 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.032189 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.083878 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.030342 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.030342 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.048753 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1185 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.030234 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.053576 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.035552 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.34735 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.21787 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.051637 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.030796 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.030344 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.11141 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.042573 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.093956 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056855 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.2305 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.37674 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.094022 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.049542 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.045719 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037623 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.031921 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.031921 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.41877 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.031125 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.040363 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.040978 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.040978 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.040978 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.032543 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.032543 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.032543 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.05177 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.05177 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.05177 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.031464 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.031464 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.031464 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.056718 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.056718 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.056718 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.036643 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.036643 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.036643 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10084 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035479 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21571 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18472 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18472 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18472 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18472 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12641 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.077198 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.03613 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.041813 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.63743 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.63743 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.63743 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.63743 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.34229 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12515 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.03613 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.041813 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.63743 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.63743 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.63743 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.63743 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.34229 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12515 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.030809 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.036817 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.030809 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.040084 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.041578 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.041578 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.041578 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.041578 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.038919 |  | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Add line 659131 LARAMIE_-MB3 345 800120 UNDERWOOD 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.87065 |  | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | TDF Impact | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.072875 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.040373 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.090375 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.072875 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10637 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.075222 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.075222 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.075222 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.075222 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.042271 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.057309 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.057309 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.036976 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.063851 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.059943 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1468 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.081088 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.031641 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.21102 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.16354 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.041775 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.14578 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.050527 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.058101 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.033788 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.033788 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.033788 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.49598 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.033788 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.043159 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.03796 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.40324 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.14993 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.15996 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.058382 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.19804 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.045078 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.29801 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.054333 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.088848 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.059899 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.056909 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.06243 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.06243 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.18854 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.03159 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.046102 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.053082 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.097774 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.059823 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.04399 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.050527 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.033813 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62098 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.051809 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.065239 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.25101 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62098 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040766 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.061295 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.22762 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.20306 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.20306 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.20306 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.20306 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.055777 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.1054 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.1054 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.038772 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.16096 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34775 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.030578 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.089887 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.054946 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.033377 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.094668 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.073036 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.053587 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.030554 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.097747 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.04252 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.087347 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.030043 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057266 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.17438 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.08676 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.089818 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.050717 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.047293 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.038228 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.074263 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.035146 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.04069 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.093177 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.057549 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14031 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.093177 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16055 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14761 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14761 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14761 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14761 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.14286 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24711 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24711 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.1073 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.036642 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.053576 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.035552 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.34735 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.21787 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.051637 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.030796 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.030344 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.11141 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.042573 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.093956 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056855 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.2305 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.37674 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.094022 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.049542 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.045719 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037623 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.031921 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.031921 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.031125 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.040363 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.35256 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035479 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.4413 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.3718 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.3718 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.3718 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.3718 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.23673 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.077198 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.16545 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.075664 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26737 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030868 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.45272 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.54963 |  | Single 539760 BARBER3 115 539674 BARBER4 138 539917 'BARBER-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.041085 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.034118 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.038335 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.11411 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.052265 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.032735 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040599 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.04158 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.044719 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.042527 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.046762 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.065298 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.062022 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.082221 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.15036 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.041117 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.042757 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.078432 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.037217 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.051931 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.050505 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.041159 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.060119 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.045452 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.035437 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.053047 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.041233 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.034506 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.15253 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.053384 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.053384 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.045501 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.0489 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.040048 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.04431 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.046444 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.09709 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.045922 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.040848 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.042527 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.034554 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10551 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053639 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.046978 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13441 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10551 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.05052 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.13657 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.22971 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.22971 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.22971 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.22971 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.055482 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.07485 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.07485 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.039134 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.27619 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.090359 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.037943 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.03732 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11342 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.041552 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.032273 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10378 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.10822 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.097251 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.041552 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.0482 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.064314 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11615 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11879 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.11179 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.11179 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.11179 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.040655 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.11179 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047302 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.25196 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.20067 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.20067 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.090012 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.043804 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10389 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.048478 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.060141 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.065774 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.085984 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.032189 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.083878 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.030342 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.030342 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.048753 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1185 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.030234 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.044544 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.076837 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.031839 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.044544 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.042908 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.093177 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.089563 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.1207 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14031 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.093177 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.031997 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.05584 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11843 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16055 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14761 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14761 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14761 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14761 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.62381 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24711 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24711 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056705 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.033181 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.1073 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.046762 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.034286 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13492 |  | Single 539800 CLARKCOUNTY7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10628 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055182 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14022 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10628 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15844 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053528 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076898 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076898 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091869 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.045243 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.0412 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.092908 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55364 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.05227 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.045243 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.10886 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.055569 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.035885 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.08769 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.092119 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.092119 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.076456 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.065711 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.054726 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.054046 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.068625 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.06453 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037277 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1428 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10084 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035479 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21571 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12641 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.077198 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.24275 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.054737 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.35256 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.24275 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.4413 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.3718 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.3718 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.3718 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.3718 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.23673 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.14519 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.16545 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.075664 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26737 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030868 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.45272 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.54963 |  | Single 539638 FLATRDG4 138 539674 BARBER4 138 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.062778 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.059997 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.053464 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.037828 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.052467 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.056157 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.042343 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.069773 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.043347 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.065441 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.062349 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.06649 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.058728 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.063709 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.039961 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.067933 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13461 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.04222 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.04222 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.04222 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.099351 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.082019 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.04222 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.10036 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.06185 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.063916 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.081348 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.041739 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.042561 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.042561 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.061708 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.07095 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.046709 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.068882 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.062118 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.074225 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.066752 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.058262 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.082902 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.035955 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.062908 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.05646 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.055423 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.074109 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.074109 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.069073 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.067958 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.059636 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.065544 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.067683 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.053476 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.13156 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.067117 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.061755 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.063709 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.053247 |  | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.037743 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.048092 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.185 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.047588 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.037743 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.14781 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.10515 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.051662 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.051175 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.059403 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.059403 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.059403 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.051487 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.059403 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.046911 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.036055 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.045003 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.045003 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.044351 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.09477 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.063121 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.16 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.036028 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.052257 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.03908 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.036324 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.17745 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.063054 |  | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.041085 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.034118 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.038335 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.11411 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.052265 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.032735 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.040599 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.04158 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.044719 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.042527 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.046762 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.065298 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.062022 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.082221 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.15036 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.041117 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.042757 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.078432 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.037217 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.051931 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.050505 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.041159 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.060119 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.045452 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.035437 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.053047 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.041233 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.034506 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.15253 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.053384 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.053384 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.045501 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.0489 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.040048 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.04431 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.046444 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.09709 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.045922 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.040848 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.042527 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.034554 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10084 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035479 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21571 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18472 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12641 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.077198 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62098 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15017 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62098 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034559 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34775 |  | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.041552 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.032273 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.10378 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.10822 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.097251 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.041552 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.0482 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.064314 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11615 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.11879 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.11179 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.11179 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.11179 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.040655 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.11179 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047302 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.25196 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.20067 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.20067 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.090012 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.043804 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.10389 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.048478 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.060141 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.065774 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.085984 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.032189 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.083878 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.030342 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.030342 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.048753 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1185 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.030234 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | Single 533412 ARKVALJ3 115 533413 CIRCLE3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62098 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15017 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62098 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034559 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34775 |  | Single 531510 HARBNGR3 115 531512 HARBNGR7 345 531511 'HARBNGR-1 ' 13 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.081832 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.041739 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.036867 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10417 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.081832 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.039653 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10574 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.17825 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.17825 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.17825 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.17825 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.043287 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.058242 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.058242 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030743 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.21463 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.07015 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.088608 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.059943 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1468 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.081088 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.031641 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.21102 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.16354 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.041775 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.14578 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.050527 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.058101 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.059174 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.059174 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.059174 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.49598 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.059174 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.043159 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.03796 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.40324 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.14993 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.15996 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.058382 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.19804 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.045078 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.29801 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.054333 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.099529 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.059899 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.10206 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.06243 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.06243 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.18854 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.03159 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.046102 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.053082 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.097774 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.059823 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.04399 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.050527 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.033813 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10628 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055182 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14022 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10628 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15844 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053528 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076898 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076898 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091869 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.16545 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.075664 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26737 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.030868 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.45272 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.54963 |  | P12:138:SUNC:BARBER-FLATRIDGE::539638-539674(1):HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.045243 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.0412 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.092908 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55364 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.045587 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.045243 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.10886 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.045609 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.035885 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.08769 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.092119 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.092119 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.076456 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.032445 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.054726 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.054046 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.068625 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.06453 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037277 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1428 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62098 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15017 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62098 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034559 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34775 |  | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10084 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.041813 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21571 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.63743 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.63743 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.63743 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.63743 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.34229 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.12515 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.072614 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.031422 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.03788 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.066865 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.092006 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.072614 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.060625 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10152 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.18155 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.14734 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.14734 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.078347 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.077478 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.075976 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.62098 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.15017 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.62098 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034559 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.34775 |  | Single 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.035324 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.23354 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.040945 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030419 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.043392 |  | 275521 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.72855 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.086318 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.72855 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034033 |  | Single 531405 WALKMYR3 115 531481 HUGOTON3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.081832 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.041739 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.036867 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10417 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.081832 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.039653 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10574 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.17825 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.17825 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.17825 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.17825 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.043287 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.058242 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.058242 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030743 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.21463 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.07015 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.088608 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.093604 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.089973 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.12125 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14095 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.093604 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.032143 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.056095 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11897 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16129 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14829 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14829 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14829 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14829 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24824 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24824 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056964 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13059 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.033333 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10779 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.046976 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.034443 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13553 |  | Single 539800 CLARKCOUNTY7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.030809 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.036817 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.030809 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.040084 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.041578 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.041578 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.041578 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.041578 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.038919 |  | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | Single 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.031313 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.031313 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.031313 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.031313 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.13943 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.040631 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.050367 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.036849 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.042018 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.065181 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.04891 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-084 |  | Non-Converged |  |  | 0.035954 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.086714 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-091 |  | Non-Converged |  |  | 0.038395 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.091851 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.041877 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.050489 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.039133 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.038423 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.069858 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.070304 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-175 |  | Non-Converged |  |  | 0.034687 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.037749 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-181 |  | Non-Converged |  |  | 0.035123 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.043081 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.095926 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.03453 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.091536 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.047298 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.040088 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.13903 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.033779 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.07668 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.07668 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.044614 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.052525 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.075409 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.084852 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.041359 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.097276 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.10685 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.086714 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.041697 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10551 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.053639 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.046978 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.13441 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10551 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.05052 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.13657 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.22971 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.22971 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.22971 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.22971 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.055482 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.07485 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.07485 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.039134 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.27619 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.090359 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.037943 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.03732 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.11342 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.054946 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.033377 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.094668 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.073036 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.053587 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.030554 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.097747 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.04252 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.087347 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.030043 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057266 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.17438 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.08676 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.089818 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.050717 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.047293 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.038228 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.074263 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.035146 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.04069 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.045243 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.0412 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.092908 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55364 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.045587 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.045243 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.10886 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.045609 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.035885 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.08769 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.092119 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.092119 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.076456 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.032445 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.054726 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.054046 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.068625 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.06453 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037277 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1428 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.17998 |  | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.074054 |  | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.30019 |  | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.5149 |  | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.62717 |  | Single 539649 SAWYER3 115 539760 BARBER3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.045243 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.0412 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.092908 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.55364 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.045587 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.045243 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.10886 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.045609 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.035885 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.08769 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.092119 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.092119 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.076456 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.032445 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.054726 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.054046 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.068625 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.06453 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.037277 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.1428 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10084 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035479 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21571 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18472 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18472 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18472 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18472 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12641 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.077198 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.072614 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.031422 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.03788 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.066865 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.092006 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.072614 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.060625 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.10152 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.092056 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.18155 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.14734 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.14734 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.078347 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.077478 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.075976 |  | Single 539800 CLARKCOUNTY7 345 539801 THISTLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.72855 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.086318 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.72855 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.034033 |  | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.060504 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.039603 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.037 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.037989 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.051727 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.030799 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.031287 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.031287 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.031287 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.046704 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.031287 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.036652 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.047713 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.060877 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.051054 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.051054 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.070733 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.035256 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.033433 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.036395 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.046925 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.088885 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.098376 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.070375 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.030994 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.030994 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.035855 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.042359 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.035786 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.13643 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.15079 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.031284 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.033829 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.095274 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.13643 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.03469 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.083818 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.075842 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.075842 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.075842 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.075842 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.047255 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.056666 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.056666 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.062725 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.11677 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.04278 |  | Single 523961 POTTER_CO7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.043151 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.039609 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.23354 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.05227 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.043151 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.047219 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.055569 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.061738 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.061738 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.061738 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.061738 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.045074 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.053658 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.053658 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030717 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.065711 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.042354 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.07469 |  | P42:345:NPPD:BKR-AXT-3308:::: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10628 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055182 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14022 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10628 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15844 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 1 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053528 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076898 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076898 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091869 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.041808 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.057639 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.10084 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.035479 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.050228 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21571 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18472 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18472 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18472 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18472 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.048308 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.094283 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.094283 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030348 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12641 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.077198 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.1184 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.17196 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.1184 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.21525 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.18135 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.18135 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.18135 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.18135 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.36028 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.36028 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.11546 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.070818 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-024 |  | Non-Converged |  |  | 0.058685 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.055904 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.049371 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.033735 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-054 |  | Non-Converged |  |  | 0.048374 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-055 |  | Non-Converged |  |  | 0.052065 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-061 |  | Non-Converged |  |  | 0.03825 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.06568 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-069 |  | Non-Converged |  |  | 0.039255 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.061348 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-074 |  | Non-Converged |  |  | 0.058257 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-076 |  | Non-Converged |  |  | 0.062397 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.054635 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-090 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.035868 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-121 |  | Non-Converged |  |  | 0.06384 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-125 |  | Non-Converged |  |  | 0.13051 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-139 |  | Non-Converged |  |  | 0.095259 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.077926 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.038128 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.096265 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-167 |  | Non-Converged |  |  | 0.057758 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-170 |  | Non-Converged |  |  | 0.059823 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.077255 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.037647 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.038468 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057616 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-209 |  | Non-Converged |  |  | 0.066857 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.042616 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.06479 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-217 |  | Non-Converged |  |  | 0.058026 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.070132 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-253 |  | Non-Converged |  |  | 0.062659 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.054169 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-258 |  | Non-Converged |  |  | 0.078809 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-259 |  | Non-Converged |  |  | 0.031862 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-260 |  | Non-Converged |  |  | 0.058815 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.052367 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.05133 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-276 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-277 |  | Non-Converged |  |  | 0.070016 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-287 |  | Non-Converged |  |  | 0.06498 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.063865 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-289 |  | Non-Converged |  |  | 0.055543 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-319 |  | Non-Converged |  |  | 0.061451 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-320 |  | Non-Converged |  |  | 0.06359 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.049384 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.12747 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-339 |  | Non-Converged |  |  | 0.063024 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-352 |  | Non-Converged |  |  | 0.057662 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-370 |  | Non-Converged |  |  | 0.059616 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-375 |  | Non-Converged |  |  | 0.049154 |  | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.10628 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-006 |  | Non-Converged |  |  | 0.055182 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14022 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.10628 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.15844 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.27791 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.27791 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.27791 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.27791 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.053528 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.076898 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.076898 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.091869 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | Single 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.093177 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.089563 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.1207 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14031 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.093177 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.031997 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.05584 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11843 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16055 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14761 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14761 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14761 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14761 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24711 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24711 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056705 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.033181 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.1073 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.046762 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.034286 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13492 |  | Single 539803 IRONWOOD7 345 539816 SADDLE7 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.1551 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.0541 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.26936 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.18721 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.14425 |  | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.048188 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.040077 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-142 |  | Non-Converged |  |  | 0.038769 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-166 |  | Non-Converged |  |  | 0.031776 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-176 |  | Non-Converged |  |  | 0.039419 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.044782 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.036487 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.036487 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.057667 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.037954 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-257 |  | Non-Converged |  |  | 0.073627 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-272 |  | Non-Converged |  |  | 0.081972 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-274 |  | Non-Converged |  |  | 0.060131 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.031276 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-330 |  | Non-Converged |  |  | 0.030814 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.093604 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.089973 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.12125 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.14095 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.093604 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.032143 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-072 |  | Non-Converged |  |  | 0.056095 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.11897 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.16129 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.14829 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.14829 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.14829 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.14829 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.24824 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.24824 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.056964 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.13059 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.033333 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.10779 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-228 |  | Non-Converged |  |  | 0.046976 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-288 |  | Non-Converged |  |  | 0.034443 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.13553 |  | Single 531469 SPERVIL7 345 763677 G19-030-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.12435 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.1806 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.12435 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.22605 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.19045 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.19045 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.19045 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.19045 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.37837 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.37837 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.12126 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.074373 |  | Single 531469 SPERVIL7 345 765911 G21-068-TAP 345 2 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | ASGI-2024-003 |  | Non-Converged |  |  | 0.049425 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-007 |  | Non-Converged |  |  | 0.036887 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-016 |  | Non-Converged |  |  | 0.12383 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-030 |  | Non-Converged |  |  | 0.060363 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-032 |  | Non-Converged |  |  | 0.049425 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-085 |  | Non-Converged |  |  | 0.041955 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-102 |  | Non-Converged |  |  | 0.06422 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-136 |  | Non-Converged |  |  | 0.076504 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-137 |  | Non-Converged |  |  | 0.076504 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-138 |  | Non-Converged |  |  | 0.076504 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-144 |  | Non-Converged |  |  | 0.076504 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-189 |  | Non-Converged |  |  | 0.041287 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-193 |  | Non-Converged |  |  | 0.050355 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-194 |  | Non-Converged |  |  | 0.050355 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-205 |  | Non-Converged |  |  | 0.030472 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-210 |  | Non-Converged |  |  | 0.081533 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-218 |  | Non-Converged |  |  | 0.046167 |  | 275516 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N0 | GEN-2024-322 |  | Non-Converged |  |  | 0.065346 |  | 275516 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.048131 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.037669 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.037326 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.037653 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.039558 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.039558 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.034594 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030145 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034099 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031311 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038966 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03069 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040365 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.039227 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.037819 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.064848 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050616 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.048779 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.050371 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.034951 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.033081 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031579 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.037854 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033667 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.035231 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049558 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049558 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030228 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042821 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.035419 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034948 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.030798 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042821 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.044704 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.039571 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032989 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.061898 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.039386 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.039473 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.035928 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033765 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.033827 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034595 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.030483 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.042547 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.044834 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.04294 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03069 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032167 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03564 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056094 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032313 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.052074 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035393 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031321 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.036378 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03513 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036889 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031099 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.058708 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031087 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031099 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031442 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03237 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033638 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030484 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036414 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030656 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031093 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031858 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054613 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.053643 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032583 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030271 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030191 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030191 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.045577 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03489 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046588 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.035088 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.047131 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.03331 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.030511 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034591 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.036045 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.041559 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.042784 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.057442 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.057442 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.048148 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.044948 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.044349 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.044867 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.03885 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.037278 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.038266 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031266 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.036586 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.040544 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.037541 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.039081 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.045113 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.045113 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044077 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037077 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.044234 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.035496 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.038616 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.04151 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.036264 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.044234 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.045206 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.044779 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.036938 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.033027 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03526 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.035603 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034912 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034912 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034912 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.050446 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.033306 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.037207 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042642 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.043183 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.038829 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.037581 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.041007 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.036858 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.034278 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.039557 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.041627 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.043358 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.042989 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.042916 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03489 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041139 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.032067 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031799 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.032058 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033704 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033704 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.059494 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.034748 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.051833 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.065884 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031927 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049444 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.049404 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.077347 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.063261 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.062352 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.06316 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.042242 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038774 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.036252 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046897 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039865 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042754 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.071447 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.071447 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032846 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.033582 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.056072 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.04294 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.04462 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.034745 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.056072 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.058883 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.053004 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.0387 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.062555 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031205 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050745 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.051597 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.04384 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039981 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.04052 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04192 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.04071 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.054753 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.059233 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.054909 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.034748 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036639 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.052985 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.033855 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041749 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.055239 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.04458 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.054511 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036228 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034701 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040113 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037871 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.04312 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.044172 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.048477 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.050067 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033573 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031378 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.060874 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.060874 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053081 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050958 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050462 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.050889 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045835 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.044232 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.046602 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033462 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033453 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03917 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043608 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.047455 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044466 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.046071 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034632 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035425 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035425 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.051263 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.051263 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.052976 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.04435 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.051236 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.045833 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036639 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.045504 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033253 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.048894 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043334 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.051236 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.052195 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.05219 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043849 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.040575 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.042512 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.043309 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.042223 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.042223 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.042223 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.033753 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.05554 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.030452 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.040157 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.045483 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.049735 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050352 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045689 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044501 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.048505 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.047356 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.04283 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.046702 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.049452 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.050181 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.049427 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.049594 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041749 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-114 |  | Non-Converged |  |  | 0.76477 |  | Single 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.030492 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036507 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041928 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034102 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040436 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045037 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10077 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040465 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036147 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034827 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039254 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.045722 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.090414 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.059096 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042453 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043803 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033849 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031666 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034344 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038434 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.038849 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038486 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.043093 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.042654 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.05826 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033771 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033659 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.062645 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.042729 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042497 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.04217 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.043117 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034775 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035453 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035453 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037971 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037971 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.048918 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046275 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041662 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.10962 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036507 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042193 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040831 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.045032 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043558 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041662 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041048 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.042442 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.041777 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.048971 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045627 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055261 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.046321 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.046321 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.046321 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034006 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033795 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.037456 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039811 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.059521 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042931 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042923 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041962 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.042383 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.047157 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.10027 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.093592 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.044587 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047171 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041507 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039845 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.041174 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040436 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032389 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035177 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033536 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030048 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.038295 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.038295 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.033249 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031018 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030539 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030953 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030879 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030879 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034259 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031162 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031162 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031994 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032431 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035082 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030345 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030176 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.041843 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.03944 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.041124 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.043761 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.039849 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.040666 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.037137 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.039925 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.038284 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.033323 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034796 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.043043 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.043043 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037997 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.035766 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035287 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.035701 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030824 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030994 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.032339 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.031051 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.035627 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.035627 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.039007 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.03591 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030469 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.03369 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.03591 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036742 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037179 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.030165 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.03983 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030179 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.034522 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035093 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030638 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.033118 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.031707 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.034202 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.034924 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034121 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03437 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.086395 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037634 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.12006 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.13146 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.040298 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030123 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.046705 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.046705 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035981 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031408 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03072 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031317 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031162 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031162 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037688 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.035663 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.061826 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.032719 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041011 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.099765 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.059726 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.035228 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033614 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039116 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.0401 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.049793 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.04929 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.059844 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.032416 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030057 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.037732 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03853 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.037822 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.04583 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04325 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.062201 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.032306 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.032281 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.044577 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.047541 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.043795 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.046297 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.033542 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.034364 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.034364 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033663 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033663 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.13422 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046134 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.057509 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.035663 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044046 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033151 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.058857 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043697 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.057509 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.058966 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.076762 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043163 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.043741 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.044091 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.042124 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.044099 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.044099 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.044099 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.03261 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039577 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.056536 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.055499 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.05883 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.043912 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.043116 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.058564 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.049189 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.068265 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.051128 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040257 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.046616 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041011 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030191 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030191 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03299 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.034484 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031357 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031057 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.059523 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.059523 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044763 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.037799 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.036826 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.037671 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.03045 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037392 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037392 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.033505 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.033505 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.034475 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032302 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046675 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031684 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031871 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.033352 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034421 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.033483 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038745 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.044221 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040729 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.037685 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.039227 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.0604 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.0604 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045744 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.039866 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03895 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.039744 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.040198 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.040198 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047328 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037962 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.039758 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037962 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.038576 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.039876 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048371 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.03846 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.038717 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.041663 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037338 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.036791 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03678 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034524 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034524 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031992 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030707 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.21678 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.30001 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.32739 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030727 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.035037 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034378 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.030822 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030844 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031568 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.0311 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.035052 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.030374 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030978 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.034544 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.0347 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.048131 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.037669 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.037326 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.037653 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.039558 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.039558 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.034594 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030145 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034099 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031311 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.045734 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.042441 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.030971 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030851 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.032679 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.048319 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.031261 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.045105 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.043575 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041139 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.032067 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031799 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.032058 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033704 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033704 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.037252 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.094516 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.085358 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03229 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032167 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03564 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056094 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032313 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.052074 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035393 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031321 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.036378 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03513 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036889 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031099 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.058708 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031087 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031099 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031442 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03237 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033638 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030484 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036414 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030656 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031093 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031858 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054613 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.053643 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032583 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030271 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.030492 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036507 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041928 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034102 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040436 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045037 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10077 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040465 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036147 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034827 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039254 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.045722 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.090414 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.059096 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042453 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043803 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033849 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031666 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034344 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038434 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.038849 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038486 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.043093 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.042654 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.05826 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033771 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033659 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.062645 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.042729 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042497 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.04217 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.043117 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034775 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035453 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035453 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037971 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037971 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.048918 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046275 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041662 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.10962 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036507 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042193 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040831 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.045032 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043558 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041662 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041048 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.042442 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.041777 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.048971 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045627 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055261 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.046321 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.046321 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.046321 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034006 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033795 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.037456 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039811 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.059521 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042931 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042923 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041962 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.042383 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.047157 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.10027 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.093592 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.044587 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047171 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041507 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039845 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.041174 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040436 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.045577 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03489 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046588 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.035088 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.047131 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.03331 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.030511 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034591 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.036045 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.041559 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.042784 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.057442 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.057442 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.048148 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.044948 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.044349 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.044867 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.03885 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.037278 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.038266 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031266 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.036586 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.040544 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.037541 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.039081 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.045113 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.045113 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044077 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037077 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.044234 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.035496 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.038616 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.04151 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.036264 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.044234 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.045206 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.044779 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.036938 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.033027 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03526 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.035603 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034912 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034912 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034912 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.050446 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.033306 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.037207 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042642 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.043183 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.038829 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.037581 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.041007 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.036858 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.034278 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.039557 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.041627 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.043358 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.042989 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.042916 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03489 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.042836 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.031527 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030331 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037699 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037699 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037699 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.031409 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.41573 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.4916 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.53746 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.045734 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.042441 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.030971 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030851 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.032679 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.048319 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.031261 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.045105 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.043575 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032167 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03564 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056094 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032313 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.052074 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035393 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031321 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.036378 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03513 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036889 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031099 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.058708 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031087 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031099 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031442 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03237 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033638 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030484 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036414 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030656 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031093 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031858 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054613 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.053643 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032583 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030271 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030123 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.046705 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.046705 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035981 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031408 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03072 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031317 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031162 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031162 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037688 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034524 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034524 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031992 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030707 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.032832 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038293 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.037516 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.040615 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.15582 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035917 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.032384 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.030772 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.036147 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.048185 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034965 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.060593 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.03914 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041557 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.034037 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.034552 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.034101 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040145 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040225 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.076824 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040503 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.039462 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039454 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040136 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.030697 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.031623 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.031623 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033288 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033288 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.050288 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.045292 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037883 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.35251 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.032832 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.039207 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.037045 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043731 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.041654 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037883 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037194 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.038649 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.039015 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.053294 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045876 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040616 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.047313 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.047313 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.047313 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032057 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.036916 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.067952 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.039721 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.039906 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.038896 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039796 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.050483 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.30097 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.032881 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041797 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047671 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037836 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035766 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.037444 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.037516 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.030492 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036507 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041928 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034102 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040436 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045037 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10077 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040465 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036147 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034827 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039254 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.045722 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.090414 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.059096 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042453 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043803 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033849 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031666 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034344 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038434 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.038849 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038486 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.043093 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.042654 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.05826 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033771 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033659 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.062645 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.042729 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042497 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.04217 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.043117 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034775 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035453 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035453 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037971 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037971 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.048918 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046275 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041662 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.10962 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036507 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042193 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040831 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.045032 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043558 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041662 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041048 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.042442 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.041777 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.048971 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045627 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055261 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.046321 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.046321 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.046321 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034006 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033795 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.037456 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039811 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.059521 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042931 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042923 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041962 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.042383 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.047157 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.10027 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.093592 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.044587 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047171 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041507 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039845 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.041174 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040436 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.030492 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036507 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041928 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034102 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040436 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045037 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10077 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040465 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036147 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034827 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039254 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.045722 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.090414 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.059096 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042453 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043803 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033849 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031666 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034344 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038434 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.038849 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038486 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.043093 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.042654 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.05826 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033771 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033659 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.062645 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.042729 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042497 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.04217 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.043117 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034775 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035453 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035453 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037971 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037971 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.048918 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046275 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041662 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.10962 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036507 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042193 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040831 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.045032 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043558 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041662 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041048 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.042442 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.041777 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.048971 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045627 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055261 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.046321 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.046321 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.046321 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034006 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033795 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.037456 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039811 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.059521 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042931 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042923 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041962 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.042383 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.047157 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.10027 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.093592 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.044587 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047171 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041507 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039845 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.041174 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040436 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03299 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.034484 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031357 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031057 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.059523 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.059523 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044763 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.037799 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.036826 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.037671 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.03045 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037392 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037392 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.033505 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.033505 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.034475 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032302 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046675 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031684 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031871 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.033352 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034421 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.033483 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.037252 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.094516 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.090071 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03229 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041139 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.032067 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031799 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.032058 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033704 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033704 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032994 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035548 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.037693 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033118 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037259 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033503 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031416 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.032411 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.030203 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.030914 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030889 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030908 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030726 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030106 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033975 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.033537 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.031089 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030087 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.03081 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030828 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030828 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036018 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030966 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032236 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037407 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030392 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032309 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.030054 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032236 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032412 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033149 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030301 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030228 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.03299 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.030279 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.030279 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.030279 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030965 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033919 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.032034 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032288 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030391 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030122 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032491 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.036999 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.037567 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.031377 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033174 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031737 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.030882 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03138 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.045734 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.042441 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.030971 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030851 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.032679 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.048319 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.031261 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.045105 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.043575 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032389 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035177 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033536 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030048 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.038295 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.038295 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.033249 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031018 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030539 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030953 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030879 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030879 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034259 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031162 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031162 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031994 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032431 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035082 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030345 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030176 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.042836 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.031527 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030331 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037699 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037699 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037699 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.031409 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041139 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.032067 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031799 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.032058 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033704 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033704 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041139 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.032067 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031799 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.032058 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033704 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033704 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030123 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.046705 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.046705 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035981 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031408 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03072 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031317 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031162 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031162 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037688 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031239 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032963 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.042149 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.031014 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.03031 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.040683 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.034606 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030675 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031345 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030518 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.03018 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.034493 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.035867 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.030145 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.030548 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030078 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030557 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033889 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031235 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030871 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.042972 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030205 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031534 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.030337 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030871 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030827 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.031429 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.031484 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030808 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033934 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.030963 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.030963 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.030963 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.034758 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031027 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031132 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030159 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030133 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031968 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.041553 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.041269 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.031074 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032293 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030623 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.030403 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030123 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.046705 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.046705 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035981 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031408 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03072 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031317 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031162 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031162 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037688 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03299 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.034484 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031357 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031057 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.062365 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.062365 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044763 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.037799 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.036826 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.037671 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.03045 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037392 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037392 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.033505 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.033505 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.034475 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032302 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046675 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031684 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031871 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.033352 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034421 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.033483 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038457 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.037191 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040729 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.033941 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034765 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.0604 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.0604 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045744 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.039866 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03895 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.039744 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030428 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.032699 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.0307 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.040198 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.040198 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032964 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037247 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030423 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032867 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037247 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.038576 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037126 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048371 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.034964 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035533 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030759 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031884 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.030836 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032079 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.036423 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.036791 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.036125 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032167 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03564 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056094 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032313 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.052074 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035393 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031321 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.036378 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03513 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036889 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031099 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.058708 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031087 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031099 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031442 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03237 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033638 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030484 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036414 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030656 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031093 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031858 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054613 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.053643 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032583 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030271 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032389 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035177 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033536 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030048 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.038295 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.038295 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.033249 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031018 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030539 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030953 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030879 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030879 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034259 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031162 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031162 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031994 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032431 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035082 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030345 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030176 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.032832 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038293 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.037516 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.040615 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.15582 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035917 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.032384 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.030772 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.036147 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.048185 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034965 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.060593 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.03914 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041557 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.034037 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.034552 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.034101 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040145 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040225 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.076824 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040503 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.039462 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039454 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040136 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.030697 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.031623 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.031623 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033288 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033288 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.050288 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.045292 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037883 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.35251 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.032832 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.039207 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.037045 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043731 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.041654 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037883 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037194 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.038649 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.039015 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.053294 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045876 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040616 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.047313 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.047313 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.047313 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032057 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.036916 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.067952 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.039721 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.039906 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.038896 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039796 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.050483 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.30097 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.032881 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041797 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047671 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037836 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035766 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.037444 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.037516 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.034217 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035836 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035611 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030252 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031599 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.044367 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.044367 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.03673 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033565 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.032973 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033486 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033541 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033541 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034078 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032981 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030347 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032981 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.033926 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033804 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038766 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031409 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031974 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.030609 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03206 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031547 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031579 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.034217 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035836 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035611 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030252 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031599 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.044367 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.044367 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.03673 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033565 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.032973 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033486 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033541 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033541 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034078 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032981 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030347 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032981 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.033926 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033804 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038766 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031409 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031974 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.030609 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03206 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031547 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031579 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030418 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030353 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.035879 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.035879 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.03059 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.032054 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030377 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030377 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034524 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034524 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031992 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030707 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032389 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035177 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033536 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030048 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.038295 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.038295 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.033249 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031018 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030539 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030953 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030879 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030879 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034259 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031162 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031162 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031994 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032431 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035082 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030345 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030176 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.036053 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.036053 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.032565 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.031713 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033845 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.075749 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.090071 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030033 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.034217 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035836 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035611 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030252 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031599 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.044367 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.044367 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.03673 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033565 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.032973 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033486 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033541 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033541 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034078 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032981 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030347 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032981 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.033926 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033804 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038766 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031409 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031974 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.030609 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03206 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031547 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031579 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056395 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.036118 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.043902 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.043179 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.053856 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033453 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032157 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.072162 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.03088 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.03494 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030758 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.044324 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031677 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031677 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031677 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.043177 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03351 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.081006 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.035702 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.030303 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032687 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.037137 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.039925 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.038284 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034796 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.043043 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.043043 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037997 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.035766 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035287 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.035701 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.035627 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.035627 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.039007 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.03591 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.03591 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036742 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037179 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.03983 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035093 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.034924 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030123 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.046705 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.046705 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035981 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031408 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03072 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031317 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031162 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031162 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037688 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038457 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.037191 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040729 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.033941 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034765 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.0604 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.0604 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045744 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.039866 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03895 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.039744 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030428 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.032699 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.0307 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.040198 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.040198 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032964 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037247 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030423 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032867 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037247 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.038576 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037126 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048371 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.034964 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035533 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030759 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031884 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.030836 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032079 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.036423 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.036791 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.036125 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.059494 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.034748 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.051833 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.065884 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031927 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049444 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.049404 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.077347 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.063261 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.062352 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.06316 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.042242 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038774 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.036252 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046897 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039865 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042754 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.071447 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.071447 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032846 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.033582 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.056072 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.04294 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.04462 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.034745 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.056072 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.058883 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.053004 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.0387 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.062555 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031205 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050745 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.051597 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.04384 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039981 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.04052 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04192 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.04071 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.054753 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.059233 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.054909 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.034748 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030406 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.031332 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.031377 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03038 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.030349 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.030187 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.031661 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041139 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.032067 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031799 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.032058 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033704 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033704 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.030492 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036507 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041928 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034102 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040436 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045037 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10077 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040465 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036147 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034827 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039254 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.045722 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.090414 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.059096 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042453 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043803 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033849 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031666 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034344 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038434 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.038849 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038486 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.043093 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.042654 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.05826 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033771 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033659 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.062645 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.042729 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042497 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.04217 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.043117 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034775 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035453 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035453 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037971 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037971 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.048918 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046275 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041662 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.10962 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036507 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042193 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040831 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.045032 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043558 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041662 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041048 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.042442 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.041777 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.048971 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045627 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055261 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.046321 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.046321 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.046321 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034006 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033795 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.037456 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039811 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.059521 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042931 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042923 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041962 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.042383 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.047157 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.10027 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.093592 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.044587 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.047171 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041507 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039845 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.041174 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040436 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.036639 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.052985 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.033855 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041749 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.055239 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.04458 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.054511 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.036228 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034701 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040113 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037871 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.04312 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.044172 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.048477 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.050067 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033573 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031378 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.084223 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.084223 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053081 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050958 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050462 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.050889 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045835 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.044232 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.046602 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033462 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033453 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03917 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043608 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.047455 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044466 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.046071 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034632 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035425 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035425 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.051263 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.051263 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.052976 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.04435 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.051236 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.045833 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.036639 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.045504 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033253 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.048894 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043334 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.051236 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.052195 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.05219 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043849 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.040575 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.042512 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.043309 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.042223 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.042223 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.042223 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.033753 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.05554 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.030452 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.040157 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.045483 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.049735 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050352 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045689 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044501 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.048505 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.047356 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.04283 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.046702 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.049452 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.050181 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.049427 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.049594 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041749 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.034217 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035836 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035611 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030252 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031599 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.044367 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.044367 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.03673 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033565 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.032973 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033486 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033541 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033541 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034078 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032981 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030347 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032981 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.033926 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033804 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038766 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031409 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031974 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.030609 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03206 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031547 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031579 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032994 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035548 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.037693 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033118 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037259 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033503 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031416 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.032411 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.030203 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.030914 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030889 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030908 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030726 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030106 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033975 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.033537 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.031089 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030087 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.03081 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030828 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030828 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036018 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030966 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032236 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037407 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030392 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032309 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.030054 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032236 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032412 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033149 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030301 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030228 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.03299 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.030279 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.030279 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.030279 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030965 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033919 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.032034 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032288 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030391 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030122 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032491 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.036999 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.037567 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.031377 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033174 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031737 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.030882 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03138 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.030526 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.034549 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.20599 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.20599 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.048582 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038232 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035711 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.03788 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.034512 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.034512 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.0305 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.0305 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.0324 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.074023 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030467 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031388 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.030596 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034524 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034524 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031992 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030707 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.0334 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038745 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.031913 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.035894 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.044221 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.051915 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037995 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.033177 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.032357 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.035118 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.038247 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.051122 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.045658 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.037685 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.039227 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.031757 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030371 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031021 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.034515 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.034818 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.034552 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037731 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.037236 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.045402 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.031712 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.031629 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.04932 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037364 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.037539 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.037038 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037785 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032326 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.032742 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.032742 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.034078 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.034078 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047328 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039329 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037962 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.052781 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.0334 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.037093 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.035557 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.039758 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037726 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037962 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037758 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.039876 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.036779 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.040131 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.038694 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.045319 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.039008 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.039008 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.039008 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.031854 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.031224 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.033583 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.035442 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.045827 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.03846 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.038717 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.036962 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.037089 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.04043 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.050896 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.05162 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038814 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.041663 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037338 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035562 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03678 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.035894 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.036053 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.036053 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.032565 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.031713 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030377 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030377 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.032261 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.039754 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.03038 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.035964 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034404 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040333 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.031983 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.030922 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.03481 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.030054 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.041164 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.039324 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.0302 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.035248 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.035248 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.06139 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050352 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049885 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.050319 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.038925 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.0378 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.03087 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030134 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03012 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.03654 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.040474 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.038071 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.039056 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.030872 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.031372 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.031372 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.050158 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.050158 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032351 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036014 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041707 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.032261 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.039305 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.038081 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.036255 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041707 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041764 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.039848 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.037591 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030732 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034349 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.031364 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033729 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033729 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033729 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.030316 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.047018 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034565 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030245 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.040524 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.040245 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.039637 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.038263 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.036878 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03859 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.03566 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.042794 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046112 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.043882 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.035964 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.032626 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.038947 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.052182 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.036327 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.044176 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.040182 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.053406 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.038561 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.037086 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.042497 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.03318 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.03319 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.052896 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.051357 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.036078 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034089 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.033061 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.033061 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.079421 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.064251 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.062298 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.06399 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.048652 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.046666 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.034193 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035982 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035987 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.045063 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.051453 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.047226 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.048942 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.037014 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.037712 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.037712 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.061409 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.061409 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.032028 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036482 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.04406 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.056498 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.038947 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.048998 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.048396 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.044454 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.056498 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.058332 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.053075 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.046532 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035483 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.041362 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.03538 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.040349 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.040349 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.040349 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.03624 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.073709 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.042139 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033287 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.053084 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.053086 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.049487 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.047329 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.047089 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04845 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043605 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.056149 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.057948 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.056508 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.044176 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.030563 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034707 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.050259 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.031158 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040989 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053987 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.074375 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050384 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034181 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.032215 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039024 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.040328 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.070339 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.054359 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047399 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.049394 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.030803 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.047651 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.047651 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.047265 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.047395 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.0472 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.047367 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045685 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04424 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.055405 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030678 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.030606 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.054054 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043764 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046642 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044126 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045881 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032127 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033094 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033094 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046923 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046923 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.055463 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046469 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049088 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.077175 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034707 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044938 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033188 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.049217 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.04407 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049088 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049475 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050465 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043414 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045515 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.0448 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.053091 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.045043 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.045043 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.045043 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.031028 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048351 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039386 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.055379 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.048626 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.049114 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.044954 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044291 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.050187 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.07302 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.07188 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04718 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.050925 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048223 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04669 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047603 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040989 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Add line 542968 STILWEL7 345 765571 G21-029-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.031089 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.035648 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.045894 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.033694 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.039199 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046953 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.044548 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.046629 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.035359 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034281 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.038075 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.03697 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.044217 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.04225 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.04354 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.044474 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033498 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031873 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.051204 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.051204 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.046524 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045055 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04471 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.045008 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.04198 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040976 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.043253 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033425 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03339 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.040557 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040541 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042919 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041053 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042125 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034233 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.034778 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.034778 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.04464 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.04464 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.030207 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.046068 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.041443 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.045084 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.044336 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.035648 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.041699 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.0335 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043854 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.040517 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.045084 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.045596 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04557 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.040632 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039434 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.040244 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041806 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.040153 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.040153 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.040153 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.033621 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048052 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.031688 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.038162 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.042876 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044282 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.04461 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041793 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041114 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.043794 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.044521 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.044322 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042629 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.044192 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.044504 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.043902 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.044166 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.039199 |  | Single 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Add line 640600 DAYKIN3 345 785610 G24-288-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.036079 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.042493 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.05827 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.039801 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047508 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.05916 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.047369 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.059837 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.042095 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.040598 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.045905 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.042541 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.046893 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.048333 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.054259 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.055484 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.039535 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.037371 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.06992 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.06992 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.06085 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.057584 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.056936 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.057496 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.051561 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.049972 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.050512 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.039437 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.039408 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.043536 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.049224 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.053216 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.050203 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.051797 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.040529 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.041263 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.041263 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.056964 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.056964 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.035141 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.056582 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.049967 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.056939 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.047818 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.042493 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.051276 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.037669 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.054193 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.049019 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.056939 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.057892 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.057451 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049591 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045833 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.04804 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.04755 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.047712 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.047712 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.047712 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.039704 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.06335 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.035182 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.045931 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.0495 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.055372 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.055894 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.051478 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.050258 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.053671 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.049147 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.046571 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.052336 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.054257 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.05603 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.055391 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.055553 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047508 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.033583 |  | Single 532773 SUMMIT7 345 532998 G16-111-TAP 345 1 | TDF Impact | Add line 532773 SUMMIT 7 345 532998 G16-111-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03465 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031314 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030041 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.03516 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030301 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.035867 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034262 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030942 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030942 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053508 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043927 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04355 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043904 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033913 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032928 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031827 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035265 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033164 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034027 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043739 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043739 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031376 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036325 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.034243 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.033185 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.031579 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036325 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036364 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034719 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032743 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.040902 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030088 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035305 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035061 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034533 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033333 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032133 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033623 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031093 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037287 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040195 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.038244 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031314 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.034603 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.031706 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035461 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.033831 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.033505 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.045711 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.045711 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043255 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038253 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03768 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038182 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032122 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.031229 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.030566 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.033241 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.031413 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032246 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037464 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037464 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030092 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030538 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.035014 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.032174 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032544 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.030381 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.035014 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.035483 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034232 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.031065 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.042283 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.03397 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.034029 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.032357 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.031483 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032002 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03222 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031392 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.035048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035805 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.035223 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.034603 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.031706 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035461 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.033831 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.033505 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.045711 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.045711 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043255 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038253 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03768 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038182 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032122 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.031229 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.030566 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.033241 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.031413 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032246 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037464 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037464 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030092 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030538 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.035014 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.032174 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032544 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.030381 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.035014 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.035483 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034232 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.031065 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.042283 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.03397 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.034029 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.032357 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.031483 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032002 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03222 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031392 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.035048 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035805 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.035223 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03678 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.047564 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.080114 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.043302 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.056271 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.072149 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.086008 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.046934 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.044492 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.053448 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.035767 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.034369 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.071085 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.070856 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.042903 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039574 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.032686 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.032686 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.098663 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.084127 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.08321 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.084028 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.064073 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.060383 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037469 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.042772 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.042725 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.057739 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.068414 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.061412 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.064601 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.044374 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.045456 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.045456 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.088604 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.088604 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036107 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.052679 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.055797 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.077749 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.047564 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.064468 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.065941 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.056588 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.077749 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.080416 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.074341 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.060242 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039503 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.05072 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.037755 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.048775 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.048775 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.048775 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.043163 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.078698 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.05282 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03533 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.072498 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.073167 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.065304 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.06152 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.061474 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.064126 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.061429 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.076141 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.079361 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.076143 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.056271 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.033671 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.030813 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.031498 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030026 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.039471 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.039471 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037021 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033323 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.032878 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033267 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.032708 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.032708 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031023 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031023 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031408 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030512 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.03655 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.0302 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030275 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030988 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.03146 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031078 |  | Single 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 1 | TDF Impact | Add line 531449 HOLCOMB7 345 659133 SIDNEY__-MB3 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.042002 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.048717 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.065274 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.045892 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.053935 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.067445 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056508 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.066801 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.048299 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.046731 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.052268 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.049461 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.055091 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.056148 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.060769 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.062372 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.045613 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.043326 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.073112 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.073112 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.065371 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.063194 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.062663 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.063121 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.058127 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.05651 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.058554 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.045509 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.045475 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.051122 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.055825 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.059719 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.056711 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.058368 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.046659 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.047432 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.047432 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.062853 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.062853 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.040972 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.065135 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.05682 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.063547 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057782 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.048717 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.05775 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.044223 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.061183 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.055665 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.063547 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.064496 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.064477 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.05608 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.053016 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.05489 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055027 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.054628 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.054628 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.054628 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.045791 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.067887 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.041549 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.052342 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.057468 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.062059 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.062664 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.057928 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.056764 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.060793 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.059272 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.054791 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.059054 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.061706 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.062455 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.061469 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.061834 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.053935 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.03933 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | Add line 532771 RENO 7 345 532796 WICHITA7 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-114 |  | Non-Converged |  |  | 0.76511 |  | Single 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031343 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03139 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032374 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05606 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05606 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03044 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030131 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030131 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030983 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030574 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038381 |  | P23:345:SUNC:BU_BRK688:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.047263 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.048765 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.050272 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.053276 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.032097 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.051884 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.078167 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.039369 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.096338 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.049168 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.041572 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.041572 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.047263 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.05306 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030971 |  | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.032548 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041172 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.030898 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.035688 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.038465 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.030839 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.042114 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.032304 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.031384 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034692 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031427 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.03164 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033844 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.040098 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.039903 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.030736 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.053111 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.053111 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.049647 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.044601 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.043994 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.044525 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.038228 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.037229 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.034695 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030676 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.030661 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031679 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.036528 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.039443 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03742 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.038368 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.031341 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.031791 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.031791 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043764 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043764 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.036761 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036615 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041456 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.03053 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.032548 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.038243 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.038884 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.036344 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041456 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041983 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.040754 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.037026 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.033223 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035311 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.034208 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034972 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034972 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034972 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.030839 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.049033 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034617 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.034209 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.040331 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.040433 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.038433 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.037495 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.038347 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.030992 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.031365 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038408 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.037801 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041411 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04206 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.041535 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.035688 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03111 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.037766 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033565 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.040425 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.042564 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037876 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030904 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.030137 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.032793 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.033384 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.04212 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038607 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036128 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.037181 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034605 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034605 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034915 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.035623 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035602 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.035619 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.035421 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.034822 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.039104 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038629 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.034683 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035801 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03479 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.035505 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.030104 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.030493 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.030493 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.035574 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.035574 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.040985 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.035743 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036982 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.042358 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03111 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.035091 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.030739 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.037095 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.034782 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036982 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037179 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037936 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.034512 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035341 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035071 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038278 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.035164 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.035164 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.035164 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035566 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.032942 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039021 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036765 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.03704 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.035092 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.034834 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.037353 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.041933 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.042415 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036069 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038039 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.036464 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035597 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.036095 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033565 |  | P12:345:WERE:EMPR-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.41618 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.48935 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.038316 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.53577 |  | 266352_a | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.030853 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.033087 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.037329 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.032073 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.034822 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.038842 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.043344 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037315 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.032936 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.032388 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034284 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.03528 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.042681 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039152 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036447 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.037113 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.031967 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031059 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.035308 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.035308 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035324 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.035946 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035949 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.035945 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.036083 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.035725 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.039198 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.031927 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.031892 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.039895 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.035642 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.03627 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.035664 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.036132 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032366 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.032665 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.032665 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.03592 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.03592 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.030137 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.0393 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.03653 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036869 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.043345 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.033087 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.03584 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033538 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.037153 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.035767 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036869 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036949 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037383 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.035473 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.036641 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.036138 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038875 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.036262 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.036262 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.036262 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.032032 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035809 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032605 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034411 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039311 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036825 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.036976 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.035826 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.035713 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03747 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.042824 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.043011 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036546 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.037804 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03658 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.036009 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03636 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.034822 |  | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.033654 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.030886 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036327 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.0549 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033174 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030066 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.032615 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.051593 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040549 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.032928 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034008 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031345 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031485 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031361 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032751 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.03232 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.0405 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.042232 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032284 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.032784 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.032135 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032802 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031353 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031353 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038232 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.034042 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.033146 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057575 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.032295 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034408 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032604 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.033146 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.033066 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034019 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.031852 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035111 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.033594 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.03984 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033925 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033925 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033925 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030333 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.040841 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.033437 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.033613 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.032221 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.032235 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.035346 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054328 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.052715 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033574 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.035746 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.032813 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031843 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.032503 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.030886 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.033427 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03818 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.0492 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.036173 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041965 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046655 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038179 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050434 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037883 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.036767 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040759 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037359 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.038859 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040768 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047256 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.047434 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.035975 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034367 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.066794 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.066794 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056448 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.051655 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050883 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051552 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045033 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04382 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041858 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035901 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035881 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038145 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043086 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046452 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044034 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045209 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.036715 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.037264 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.037264 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.05053 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.05053 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.03271 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044647 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043359 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049132 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037887 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03818 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044957 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.034052 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.046237 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.042885 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049132 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049887 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.048583 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043564 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039621 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.041825 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040962 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.041476 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.041476 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.041476 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.036101 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.058667 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032353 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.04071 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041282 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.047764 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.047985 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045158 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.0441 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.045733 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.038445 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03859 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04539 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.045264 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048798 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.048965 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048718 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041965 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.031551 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031197 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.04869 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036422 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.047127 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050994 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030797 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034738 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.032252 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.044255 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.045015 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.07014 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.07014 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056047 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050072 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049077 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04994 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040785 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038934 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035136 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037905 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042971 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039333 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041063 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049128 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049128 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.042698 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037923 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047526 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031197 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040694 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043078 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037475 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047526 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048802 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04731 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038671 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.031835 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035615 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.031527 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034995 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034995 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034995 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.059101 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034616 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033613 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045303 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045818 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041011 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039371 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.041982 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041298 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.042121 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.046671 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046629 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.046332 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036422 |  | P23:345:WERE:EMPR-345-300:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.035782 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031527 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.037525 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.045265 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035876 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030648 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031275 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.043932 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.03732 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.034414 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.035326 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034718 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034718 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034309 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.0344 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.03431 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.034387 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033628 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032978 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037735 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.037287 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032766 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.034068 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.032931 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.033717 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.034205 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.034205 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038069 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.033963 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.035208 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.045798 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.033295 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.035229 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032897 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.035208 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.035397 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.035847 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032612 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.033528 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.033217 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036743 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033324 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033324 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033324 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.034894 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030808 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.037749 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.034979 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035208 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.033304 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033003 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.035624 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.044364 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.044559 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034294 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.035998 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.034798 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.034093 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.034508 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031527 |  | Single 541198 PECULR7 345 542968 STILWEL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.032261 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.039754 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.03038 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.035964 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034404 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040333 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.031983 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.030922 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.03481 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.030054 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.041164 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.039324 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.0302 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.035248 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.035248 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.06139 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050352 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049885 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.050319 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.038925 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.0378 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.03087 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030134 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03012 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.03654 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.040474 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.038071 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.039056 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.030872 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.031372 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.031372 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.050158 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.050158 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032351 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036014 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041707 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.032261 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.039305 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.038081 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.036255 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041707 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041764 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.039848 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.037591 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030732 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034349 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.031364 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033729 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033729 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033729 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.030316 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.047018 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034565 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030245 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.040524 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.040245 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.039637 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.038263 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.036878 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03859 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.03566 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.042794 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046112 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.043882 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.035964 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-114 |  | Non-Converged |  |  | 0.038401 |  | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.033427 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03818 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.0492 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.036173 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041965 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046655 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038179 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050434 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037883 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.036767 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040759 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037359 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.038859 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040768 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047256 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.047434 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.035975 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034367 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.066794 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.066794 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056448 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.051655 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050883 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051552 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045033 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04382 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041858 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035901 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035881 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038145 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043086 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046452 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044034 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045209 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.036715 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.037264 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.037264 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.05053 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.05053 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.03271 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044647 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043359 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049132 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037887 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03818 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044957 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.034052 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.046237 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.042885 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049132 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049887 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.048583 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043564 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039621 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.041825 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040962 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.041476 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.041476 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.041476 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.036101 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.058667 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032353 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.04071 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041282 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.047764 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.047985 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045158 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.0441 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.045733 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.038445 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03859 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04539 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.045264 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048798 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.048965 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048718 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041965 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.031551 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03135 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.037764 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043123 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034709 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.042391 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045841 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.16025 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040723 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037317 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.035716 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.041057 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.052778 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.040471 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.065968 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.043816 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.046344 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.034387 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.032175 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.033636 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038748 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.039324 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038821 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.044827 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.045101 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.082552 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.034225 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.034326 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.045342 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.04419 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044273 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.044808 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.035639 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.036571 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.036571 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.038925 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.038925 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.055614 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.050206 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042579 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.35647 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.037764 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.043993 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040998 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.048589 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.046554 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042579 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041956 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.043471 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043846 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.059298 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.051166 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.047242 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.052747 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.052747 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.052747 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034592 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.032817 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.036708 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.041829 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.07335 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044385 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.044635 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.043696 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044666 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055535 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.30477 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.038236 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.046327 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.052797 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.042549 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040756 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.042174 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.042391 |  | P23:345:WERE:N345-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034951 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.046774 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.032846 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.039012 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.041669 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048362 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.03464 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033463 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.037714 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.032682 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.030455 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.03496 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.045098 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.04476 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.032641 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030993 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.072826 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.072826 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.058788 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.05158 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050493 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051437 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.042366 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040978 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.03612 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.032564 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.032554 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031696 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040018 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.044147 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041289 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042567 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.033408 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033977 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033977 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049932 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049932 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038897 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039885 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047245 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034951 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042426 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043141 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.039696 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047245 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048185 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.045969 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.040771 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.03488 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03808 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.035608 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037548 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037548 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037548 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.032772 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.061474 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.037573 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.035403 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045457 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045608 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.042705 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041362 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042332 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042536 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.04124 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.047072 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.047768 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047167 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.039012 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.040916 |  | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.040916 |  | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031481 |  | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033703 |  | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03135 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.037764 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043123 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034709 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.042391 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045841 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.16025 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.040723 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037317 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.035716 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.041057 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.052778 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.040471 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.065968 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.043816 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.046344 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.034387 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.032175 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.033636 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038748 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.039324 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038821 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.044827 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.045101 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.082552 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.034225 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.034326 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.045342 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.04419 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044273 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.044808 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.035639 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.036571 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.036571 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.038925 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.038925 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.055614 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.050206 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042579 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.35647 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.037764 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.043993 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.040998 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.048589 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.046554 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042579 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041956 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.043471 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043846 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.059298 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.051166 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.047242 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.052747 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.052747 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.052747 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034592 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.032817 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.036708 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.041829 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.07335 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044385 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.044635 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.043696 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044666 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055535 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.30477 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.038236 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.046327 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.052797 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.042549 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040756 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.042174 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.042391 |  | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03817 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.043914 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.049702 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.041438 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047931 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053364 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10962 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048212 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.043546 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.042198 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.046728 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.053446 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.099308 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.068585 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049916 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.051503 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.041181 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039007 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034385 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034385 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041827 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045963 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.046416 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04602 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.050494 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.050184 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.067933 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.041091 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.041012 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.072063 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.050299 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.050005 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.049686 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.050514 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.042142 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.042844 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.042844 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046192 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046192 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036786 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.057639 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.053824 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049242 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.1184 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.043914 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.049676 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.047867 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.052824 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.051089 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049242 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048726 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050229 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049288 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.057749 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.053603 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.065894 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.05445 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.05445 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.05445 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.041341 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.041082 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.044679 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.047286 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.06904 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050435 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050535 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.049457 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.049913 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055276 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.109 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.10251 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.051895 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.05536 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.049054 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04755 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048704 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047931 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.035272 |  | Single 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034373 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.044629 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.03248 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.037839 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045492 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.041481 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.045455 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034093 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033046 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.036738 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.035281 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.041205 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.04009 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042207 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.04309 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.032291 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030732 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05086 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05086 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.04566 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043952 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.043577 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043901 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.04058 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.039564 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041211 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.03222 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03219 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.037968 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.039111 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.041566 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039665 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040728 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032999 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033523 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033523 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043524 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043524 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044361 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039879 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.043816 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.041359 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034373 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.04033 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.031904 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.042397 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.039052 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.043816 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.044364 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.044241 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.03925 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.037646 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03866 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.039638 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.038529 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.038529 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.038529 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.03241 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.047261 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.030151 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.036803 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.040752 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.04294 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.043271 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.040436 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039718 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042248 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.041744 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.041218 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041182 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.042627 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.043235 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.042695 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.042907 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.037839 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031004 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.031738 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030161 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030015 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.04029 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.04029 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037573 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033657 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.033185 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033598 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033005 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033005 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031221 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031221 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031632 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030679 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037109 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030346 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030426 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031183 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031683 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031277 |  | Single 640183 GENTLMN3 345 640325 REDWILO3 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03817 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.043914 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.049702 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.041438 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047931 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053364 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10962 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048212 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.043546 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.042198 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.046728 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.053446 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.099308 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.068585 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049916 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.051503 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.041181 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039007 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034385 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034385 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041827 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045963 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.046416 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04602 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.050494 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.050184 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.067933 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.041091 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.041012 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.072063 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.050299 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.050005 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.049686 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.050514 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.042142 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.042844 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.042844 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046192 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046192 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036786 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.057639 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.053824 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049242 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.1184 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.043914 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.049676 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.047867 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.052824 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.051089 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049242 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048726 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050229 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049288 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.057749 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.053603 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.065894 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.05445 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.05445 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.05445 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.041341 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.041082 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.044679 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.047286 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.06904 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050435 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050535 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.049457 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.049913 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055276 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.109 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.10251 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.051895 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.05536 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.049054 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04755 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048704 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047931 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.035272 |  | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031197 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.04869 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036422 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.047127 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050994 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030797 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034738 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.032252 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.044255 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.045015 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.07014 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.07014 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056047 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050072 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049077 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04994 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040785 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038934 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035136 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037905 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042971 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039333 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041063 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049128 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049128 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.042698 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037923 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047526 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031197 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040694 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043078 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037475 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047526 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048802 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04731 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038671 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.031835 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035615 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.031527 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034995 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034995 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034995 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.059101 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034616 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033613 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045303 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045818 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041011 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039371 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.041982 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041298 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.042121 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.046671 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046629 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.046332 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036422 |  | P52:345:WERE:BURNS 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031402 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.035487 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.035487 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.035487 |  | P42:345:OKGE:SB_GRIN7382:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03465 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031314 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030041 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.03516 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030301 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.035867 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034262 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030942 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030942 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053508 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043927 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04355 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043904 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033913 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032928 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031827 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035265 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033164 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034027 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043739 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043739 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031376 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036325 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.034243 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.033185 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.031579 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036325 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036364 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034719 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032743 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.040902 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030088 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035305 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035061 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034533 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033333 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032133 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033623 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031093 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037287 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040195 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.038244 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031314 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.2181 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.29984 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030946 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.32763 |  | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.036079 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.042493 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.05827 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.039801 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047508 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.05916 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.047369 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.059837 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.042095 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.040598 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.045905 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.042541 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.046893 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.048333 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.054259 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.055484 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.039535 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.037371 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.06992 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.06992 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.06085 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.057584 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.056936 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.057496 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.051561 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.049972 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.050512 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.039437 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.039408 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.043536 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.049224 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.053216 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.050203 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.051797 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.040529 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.041263 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.041263 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.056964 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.056964 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.035141 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.056582 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.049967 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.056939 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.047818 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.042493 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.051276 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.037669 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.054193 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.049019 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.056939 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.057892 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.057451 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049591 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045833 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.04804 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.04755 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.047712 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.047712 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.047712 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.039704 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.06335 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.035182 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.045931 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.0495 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.055372 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.055894 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.051478 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.050258 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.053671 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.049147 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.046571 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.052336 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.054257 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.05603 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.055391 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.055553 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047508 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.033583 |  | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.038096 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.049222 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031198 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031189 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032706 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032782 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037254 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.091943 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032381 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.031524 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.031805 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032657 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030041 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037813 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.031794 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.032179 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032713 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.034125 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.031373 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.043896 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03771 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.06503 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.038998 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.038998 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.038998 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041889 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030982 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030533 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.031499 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.032379 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.034044 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034066 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033404 |  | Single 506935 FLINTCR7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034707 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.050259 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.031158 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040989 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053987 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.074375 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050384 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034181 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.032215 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039024 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.040328 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.070339 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.054359 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047399 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.049394 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.030803 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.047651 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.047651 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.047265 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.047395 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.0472 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.047367 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045685 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04424 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.055405 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030678 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.030606 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.054054 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043764 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046642 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044126 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045881 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032127 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033094 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033094 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046923 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046923 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.055463 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046469 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049088 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.077175 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034707 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044938 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033188 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.049217 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.04407 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049088 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049475 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050465 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043414 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045515 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.0448 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.053091 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.045043 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.045043 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.045043 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.031028 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048351 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039386 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.055379 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.048626 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.049114 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.044954 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044291 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.050187 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.07302 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.07188 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04718 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.050925 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048223 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04669 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047603 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040989 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031348 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.047586 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036637 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.049111 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038167 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.04898 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030929 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034946 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031637 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.039211 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038496 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.043636 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.044989 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.057469 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.057469 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.050085 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.046867 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04623 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.046781 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040902 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.039243 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.04057 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.034266 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.038498 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042569 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039468 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041145 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.030034 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.030034 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.0461 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.0461 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047329 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039388 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.046358 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.036304 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031348 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040562 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043734 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.038307 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.046358 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.047285 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.047159 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038824 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035218 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.037377 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038044 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037064 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037064 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037064 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.052269 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034996 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039661 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044817 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045366 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.040758 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039524 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.043242 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.037357 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.039114 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041775 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043964 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.045409 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04464 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.044896 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036637 |  | P23:345:WERE:EMPR-345-210:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.033815 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.037442 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043015 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.035893 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040023 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.048811 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056694 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.042221 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037211 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.036363 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039224 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.042498 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.055897 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.050993 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.041819 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043493 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.035732 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034335 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035146 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.038676 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.039018 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.038719 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.041829 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.041406 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.050808 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035679 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035615 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.054628 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.041545 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.041697 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041197 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041881 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.036329 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.036765 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.036765 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.038816 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.038816 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.032909 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.052178 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043512 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042162 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057713 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.037442 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.04124 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.039382 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.044076 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.04189 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042162 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.042017 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.044193 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.04093 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045007 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.043113 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.051297 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.043515 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.043515 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.043515 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.035831 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.03496 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.037491 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039549 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.05114 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.042613 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042932 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041118 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041261 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.044941 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.055803 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.056363 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042856 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.046205 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.04152 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039887 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.040959 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040023 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.031945 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.048618 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.043333 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.089714 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.10863 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.044431 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030028 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.031904 |  | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.036989 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03196 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034064 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037886 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031028 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036141 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.035826 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.048374 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.048374 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045934 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.040743 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.040152 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04067 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.034344 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.033399 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030506 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032704 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035519 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03359 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034475 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.039931 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.039931 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032383 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032702 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037389 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.03439 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034826 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032514 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037389 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037877 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.036602 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.033219 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.031456 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.030146 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031108 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031108 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031108 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.044859 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.03094 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030035 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036299 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.036367 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034581 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033665 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.034264 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034462 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033656 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037415 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.038192 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.037592 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03196 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034373 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.044629 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.03248 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.037839 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.045492 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.041481 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.045455 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034093 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033046 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.036738 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.035281 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.041205 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.04009 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042207 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.04309 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.032291 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030732 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05086 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05086 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.04566 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043952 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.043577 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043901 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.04058 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.039564 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041211 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.03222 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03219 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.037968 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.039111 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.041566 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039665 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040728 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032999 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033523 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033523 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043524 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043524 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044361 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039879 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.043816 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.041359 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034373 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.04033 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.031904 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.042397 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.039052 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.043816 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.044364 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.044241 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.03925 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.037646 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03866 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.039638 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.038529 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.038529 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.038529 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.03241 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.047261 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.030151 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.036803 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.040752 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.04294 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.043271 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.040436 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039718 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042248 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.041744 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.041218 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041182 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.042627 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.043235 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.042695 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.042907 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.037839 |  | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03817 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.043914 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.049702 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.041438 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047931 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053364 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10962 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048212 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.043546 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.042198 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.046728 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.053446 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.099308 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.068585 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049916 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.051503 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.041181 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039007 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034385 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034385 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041827 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045963 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.046416 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04602 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.050494 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.050184 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.067933 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.041091 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.041012 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.072063 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.050299 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.050005 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.049686 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.050514 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.042142 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.042844 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.042844 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046192 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046192 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036786 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.057639 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.053824 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049242 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.1184 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.043914 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.049676 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.047867 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.052824 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.051089 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049242 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048726 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050229 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049288 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.057749 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.053603 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.065894 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.05445 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.05445 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.05445 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.041341 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.041082 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.044679 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.047286 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.06904 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050435 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050535 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.049457 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.049913 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055276 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.109 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.10251 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.051895 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.05536 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.049054 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04755 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048704 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047931 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.035272 |  | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031348 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.047586 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036637 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.049111 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038167 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.04898 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030929 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034946 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031637 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.039211 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038496 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.043636 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.044989 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.057469 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.057469 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.050085 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.046867 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04623 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.046781 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040902 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.039243 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.04057 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.034266 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.038498 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042569 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039468 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041145 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.030034 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.030034 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.0461 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.0461 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047329 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039388 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.046358 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.036304 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031348 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040562 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043734 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.038307 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.046358 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.047285 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.047159 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038824 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035218 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.037377 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038044 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037064 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037064 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037064 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.052269 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034996 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039661 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044817 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045366 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.040758 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039524 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.043242 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.037357 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.039114 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041775 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043964 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.045409 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04464 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.044896 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036637 |  | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031348 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.047586 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036637 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.049111 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038167 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.04898 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030929 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034946 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031637 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.039211 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038496 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.043636 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.044989 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.057469 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.057469 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.050085 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.046867 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04623 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.046781 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040902 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.039243 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.04057 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.034266 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.038498 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042569 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039468 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041145 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.030034 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.030034 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.0461 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.0461 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047329 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039388 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.046358 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.036304 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031348 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040562 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043734 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.038307 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.046358 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.047285 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.047159 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038824 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035218 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.037377 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038044 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037064 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037064 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037064 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.052269 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034996 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039661 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044817 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045366 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.040758 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039524 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.043242 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.037357 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.039114 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041775 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043964 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.045409 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04464 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.044896 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036637 |  | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.030717 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032367 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.040532 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030656 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.03937 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033657 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030535 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033626 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03496 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033114 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030243 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.040914 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030585 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030243 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030335 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030814 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033331 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033843 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030184 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030362 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031069 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.03973 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03992 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031378 |  | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.036989 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03196 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034064 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037886 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031028 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036141 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.035826 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.048374 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.048374 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045934 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.040743 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.040152 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04067 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.034344 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.033399 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030506 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032704 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035519 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03359 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034475 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.039931 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.039931 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032383 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032702 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037389 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.03439 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034826 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032514 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037389 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037877 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.036602 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.033219 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.031456 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.030146 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031108 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031108 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031108 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.044859 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.03094 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030035 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036299 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.036367 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034581 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033665 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.034264 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034462 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033656 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037415 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.038192 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.037592 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03196 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.060733 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.038288 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03129 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.07402 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045723 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.051214 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.051214 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.051214 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.033592 |  | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031348 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.047586 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036637 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.049111 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038167 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.04898 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030929 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034946 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031637 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.039211 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038496 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.043636 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.044989 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.057469 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.057469 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.050085 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.046867 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04623 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.046781 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040902 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.039243 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.04057 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.034266 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.038498 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042569 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039468 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041145 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.030034 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.030034 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.0461 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.0461 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047329 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039388 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.046358 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.036304 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031348 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040562 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043734 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.038307 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.046358 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.047285 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.047159 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038824 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035218 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.037377 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038044 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037064 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037064 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037064 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.052269 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034996 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039661 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044817 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045366 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.040758 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039524 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.043242 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.037357 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.039114 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041775 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043964 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.045409 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04464 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.044896 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036637 |  | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031343 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03139 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032374 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05606 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05606 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03044 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030131 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030131 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030983 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030574 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038381 |  | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.098411 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.04786 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.03112 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.1335 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.14535 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.050565 |  | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.037442 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.04869 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040023 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.049111 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056694 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050994 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037211 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039224 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.042498 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.055897 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.050993 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.044255 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.045015 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.07014 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.07014 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056047 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050072 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049077 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04994 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.041829 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.041406 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.050808 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.054628 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.041545 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042971 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041197 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041881 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.036765 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.036765 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049128 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049128 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.052178 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043512 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047526 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057713 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.037442 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.04124 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.044076 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.04189 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047526 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048802 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04731 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.04093 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045007 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.043113 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.051297 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.043515 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.043515 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.043515 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.059101 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039549 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.05114 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045303 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045818 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041118 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041261 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.044941 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.055803 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.056363 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042856 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.046205 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.046671 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046629 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.046332 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040023 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.033281 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034959 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.042878 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.0333 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.041668 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035498 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.032098 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.032961 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.031672 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.031672 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031631 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031902 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031844 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031893 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.031435 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030848 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035683 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.036138 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.030663 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.031798 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030781 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.031514 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031745 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031745 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.035594 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031893 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032761 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.043282 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.031103 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032935 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03082 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032761 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032902 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033359 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.030481 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.031698 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.031224 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.035044 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031359 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031359 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031359 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.032114 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.035802 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.032615 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032817 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.0311 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030857 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.033371 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.041985 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.042256 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.032087 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033708 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.032394 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031707 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.032124 |  | Single 541198 PECULR7 345 541200 PHILL7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03465 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031314 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03139 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.03516 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030301 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.035867 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034262 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05606 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05606 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053508 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043927 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04355 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043904 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033913 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032928 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031827 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035265 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033164 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034027 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043739 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043739 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031376 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036325 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.034243 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.033185 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.031579 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036325 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036364 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034719 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032743 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.040902 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030088 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035305 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035061 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034533 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033333 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032133 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033623 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031093 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037287 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040195 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.038244 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031314 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031197 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.04869 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036422 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.047127 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050994 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030797 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034738 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.032252 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.044255 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.045015 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.07014 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.07014 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056047 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050072 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049077 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04994 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040785 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038934 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035136 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037905 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042971 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039333 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041063 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049128 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049128 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.042698 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037923 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047526 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031197 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040694 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043078 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037475 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047526 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048802 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04731 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038671 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.031835 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035615 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.031527 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034995 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034995 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034995 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.059101 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034616 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033613 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045303 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045818 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041011 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039371 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.041982 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041298 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.042121 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.046671 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046629 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.046332 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036422 |  | Single 532796 WICHITA7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.10065 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.1506 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.062456 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.1072 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.1201 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.072513 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.038139 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.032329 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.16567 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.10194 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.03013 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.034725 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035955 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.034893 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.044383 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.047152 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.15982 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.13152 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.048136 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.039564 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.048736 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.043813 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.11973 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.08634 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.08634 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037297 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037297 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.062753 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032766 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.033512 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.10065 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.046567 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031428 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.046231 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.033512 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031698 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03088 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.051851 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03296 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.15199 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.070606 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035088 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.033425 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.046663 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.047427 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.039908 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.035425 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039441 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.036881 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.062456 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.039044 |  | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.033654 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.030886 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036327 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.0549 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033174 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030066 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.032615 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.051593 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040549 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.032928 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034008 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031345 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031485 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031361 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032751 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.03232 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.0405 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.042232 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032284 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.032784 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.032135 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032802 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031353 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031353 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038232 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.034042 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.033146 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057575 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.032295 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034408 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032604 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.033146 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.033066 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034019 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.031852 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035111 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.033594 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.03984 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033925 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033925 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033925 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030333 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.040841 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.033437 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.033613 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.032221 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.032235 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.035346 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054328 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.052715 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033574 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.035746 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.032813 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031843 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.032503 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.030886 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.033427 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03818 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.0492 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.036173 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041965 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046655 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038179 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050434 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037883 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.036767 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040759 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037359 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.038859 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040768 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047256 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.047434 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.035975 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034367 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.066794 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.066794 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056448 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.051655 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050883 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051552 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045033 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04382 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041858 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035901 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035881 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038145 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043086 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046452 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044034 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045209 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.036715 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.037264 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.037264 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.05053 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.05053 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.03271 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044647 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043359 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049132 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037887 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03818 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044957 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.034052 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.046237 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.042885 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049132 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049887 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.048583 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043564 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039621 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.041825 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040962 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.041476 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.041476 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.041476 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.036101 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.058667 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032353 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.04071 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041282 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.047764 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.047985 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045158 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.0441 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.045733 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.038445 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03859 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04539 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.045264 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048798 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.048965 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048718 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041965 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.031551 |  | Single 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031402 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.035487 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.035487 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.035487 |  | P42:345:OKGE:SB_GRIN7312:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034951 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.046774 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.032846 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.039012 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.041669 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048362 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.03464 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033463 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.037714 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.032682 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.030988 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.03496 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.045098 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.04476 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.032641 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030993 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.072826 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.072826 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.058788 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.05158 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050493 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051437 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.042366 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040978 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.03612 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.032564 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.032554 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031696 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040018 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.044147 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041289 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042567 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.033408 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033977 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033977 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049932 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049932 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038897 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039885 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047245 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034951 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042426 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043141 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.039696 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047245 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048185 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.045969 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.040771 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.03488 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03808 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.035608 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037548 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037548 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037548 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.032772 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.061474 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.037573 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.035403 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045457 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045608 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.042705 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041362 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042332 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042536 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.04124 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.047072 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.047768 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047167 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.039012 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034707 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.050259 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.031158 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040989 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053987 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.074375 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050384 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034181 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.032215 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039024 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.040328 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.070339 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.054359 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047399 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.049394 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.030803 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.047651 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.047651 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.047265 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.047395 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.0472 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.047367 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045685 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04424 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.055405 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030678 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.030606 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.054054 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043764 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046642 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044126 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045881 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032127 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033094 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033094 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046923 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046923 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.055463 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046469 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049088 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.077175 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034707 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044938 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033188 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.049217 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.04407 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049088 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049475 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050465 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043414 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045515 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.0448 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.053091 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.045043 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.045043 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.045043 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.031028 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048351 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039386 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.055379 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.048626 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.049114 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.044954 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044291 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.050187 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.07302 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.07188 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04718 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.050925 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048223 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04669 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047603 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040989 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03817 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.043914 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.049702 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.041438 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047931 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053364 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10962 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048212 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.043546 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.042198 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.046728 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.053446 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.099308 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.068585 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049916 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.051503 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.041181 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039007 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034385 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034385 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041827 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045963 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.046416 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04602 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.050494 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.050184 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.067933 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.041091 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.041012 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.072063 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.050299 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.050005 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.049686 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.050514 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.042142 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.042844 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.042844 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046192 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046192 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036786 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.057639 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.053824 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049242 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.1184 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.043914 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.049676 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.047867 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.052824 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.051089 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049242 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048726 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050229 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049288 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.057749 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.053603 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.065894 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.05445 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.05445 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.05445 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.041341 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.041082 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.044679 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.047286 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.06904 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050435 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050535 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.049457 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.049913 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055276 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.109 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.10251 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.051895 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.05536 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.049054 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04755 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048704 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047931 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.035272 |  | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.046149 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.035881 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.048888 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.047284 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034299 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034562 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038261 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042349 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043837 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.051876 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.051876 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.046986 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.044714 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.044206 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.044645 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.039879 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038314 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.039909 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.036161 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037686 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.041358 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.038513 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040107 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.044022 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.044022 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047994 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.038625 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.04493 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.039494 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.042739 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037523 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.04493 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.045753 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.046193 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.037915 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.034815 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.036728 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038975 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.036456 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.036456 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.036456 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048844 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034372 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039118 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.043566 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.04413 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.039655 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.038551 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042195 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.034025 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.040797 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043248 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.04392 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.042921 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.04334 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.035881 |  | P23:345:WERE:WAVS-BKRS:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03465 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031314 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.031706 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.035461 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030301 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.035867 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034262 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.045711 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.045711 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053508 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043927 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04355 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043904 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033913 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032928 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031827 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035265 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033164 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034027 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043739 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043739 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031376 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036325 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.034243 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.033185 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.031579 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036325 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036364 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034719 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032743 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.042283 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030088 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035305 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035061 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034533 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033333 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032133 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033623 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031392 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037287 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040195 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.038244 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031314 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03465 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031314 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030041 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.03516 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030301 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.035867 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034262 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030942 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030942 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053508 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043927 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04355 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043904 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033913 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032928 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031827 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035265 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033164 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034027 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043739 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043739 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031376 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036325 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.034243 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.033185 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.031579 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036325 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036364 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034719 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032743 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.040902 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030088 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035305 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035061 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034533 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033333 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032133 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033623 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031093 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037287 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040195 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.038244 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031314 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-114 |  | Non-Converged |  |  | 0.038401 |  | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031343 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03139 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032374 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05606 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05606 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03044 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030131 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030131 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030983 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030574 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038381 |  | P23:345:SUNC:BU_BRK488:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.052242 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031573 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.0311 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.031463 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.0445 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.10864 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.030847 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.03162 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030129 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030981 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030919 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030981 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030258 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.10374 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.046897 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031862 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031186 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034026 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031019 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.030208 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031013 |  | P12:345:AEPW-GRDA:FLINTCR7:TONECE7::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.033058 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034708 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.03557 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033337 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.035592 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.032323 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.03152 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.03233 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.03314 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.03314 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031984 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031802 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031678 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031784 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030664 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030043 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.032876 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031738 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.031158 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030054 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030752 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031626 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031626 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034735 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030634 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032436 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.034677 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030413 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032086 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032436 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032694 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033064 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.032006 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.032724 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.032739 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.032068 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032308 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030445 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030095 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032188 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.034498 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.035864 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03119 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032654 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.032001 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031393 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031716 |  | P12:345:WERE:JEC-MORR-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043606 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033338 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046345 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.0549 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.044741 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031756 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.032615 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.051593 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040549 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.039806 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041294 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.042171 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.041663 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.042102 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037336 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.035771 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.0405 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.042232 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.035143 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.038815 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03597 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037564 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.041479 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.041479 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.045451 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036082 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042387 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057575 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.036951 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.040196 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03498 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042387 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.04321 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04365 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.035372 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035111 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034185 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.03984 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033925 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033925 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033925 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031829 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.040841 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.041023 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.041587 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.037112 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.036008 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.039652 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.054328 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.052715 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038254 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.040705 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041377 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040379 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.040797 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033338 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.03465 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031314 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030041 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.03516 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.030301 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.035867 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034262 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.030942 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.030942 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.053508 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.043927 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04355 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.043904 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.033913 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032928 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031827 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035265 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.033164 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034027 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.043739 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.043739 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031376 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036325 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.034243 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.033185 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.031579 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036325 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.036364 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034719 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.032743 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.040902 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.030088 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.035305 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.035061 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034533 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033333 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032133 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.033623 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031093 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037287 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040195 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.038244 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031314 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.031089 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.035648 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.045894 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.033694 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.039199 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046953 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.044548 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.046629 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.035359 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.034281 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.038075 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.03697 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.044217 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.04225 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.04354 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.044474 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033498 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031873 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.051204 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.051204 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.046524 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045055 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.04471 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.045008 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.04198 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040976 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.043253 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033425 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03339 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.040557 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040541 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042919 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041053 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042125 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.034233 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.034778 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.034778 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.04464 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.04464 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.030207 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.046068 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.041443 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.045084 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.044336 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.035648 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.041699 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.0335 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043854 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.040517 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.045084 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.045596 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04557 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.040632 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039434 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.040244 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041806 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.040153 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.040153 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.040153 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.033621 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048052 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.031688 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.038162 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.042876 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.044282 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.04461 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041793 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041114 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.043794 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.044521 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.044322 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042629 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.044192 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.044504 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.043902 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.044166 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.039199 |  | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.031197 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.04869 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036422 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.047127 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050994 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030797 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034738 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.032252 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.044255 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.045015 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.07014 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.07014 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056047 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.050072 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.049077 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04994 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.040785 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038934 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035136 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037905 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.042971 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.039333 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.041063 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049128 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049128 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.042698 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037923 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047526 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.031197 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.040694 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043078 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037475 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047526 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048802 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04731 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.038671 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.031835 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035615 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.031527 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.034995 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.034995 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.034995 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.059101 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034616 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033613 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045303 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045818 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.041011 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.039371 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.041982 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.041298 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.042121 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.046671 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.046629 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.046332 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036422 |  | Single 532768 EMPEC7 345 532803 BURNS7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041628 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031519 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.042153 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.034338 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.042946 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.0347 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033499 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.038193 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.03929 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.052951 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.052951 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045084 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.041597 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.040948 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04151 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.03561 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.034053 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035246 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.033303 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.037197 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.034249 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.035837 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.040791 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.040791 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.040315 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.034208 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.040654 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.033361 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.035306 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.038107 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.033152 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.040654 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041513 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.041085 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.033628 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030341 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.032309 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033043 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.032028 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.032028 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.032028 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.047162 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.034492 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.039211 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.039672 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.035495 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.034323 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.037721 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.034012 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.034678 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036408 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038117 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.039871 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039316 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.039467 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031519 |  | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.033427 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03818 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.0492 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.036173 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041965 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046655 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038179 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050434 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037883 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.036767 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040759 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037359 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.038859 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040768 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047256 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.047434 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.035975 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034367 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.066794 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.066794 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056448 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.051655 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050883 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051552 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045033 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04382 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041858 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035901 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035881 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038145 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043086 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046452 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044034 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045209 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.036715 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.037264 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.037264 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.05053 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.05053 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.03271 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044647 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043359 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049132 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037887 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03818 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044957 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.034052 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.046237 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.042885 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049132 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049887 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.048583 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043564 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039621 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.041825 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040962 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.041476 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.041476 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.041476 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.036101 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.058667 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032353 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.04071 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041282 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.047764 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.047985 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045158 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.0441 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.045733 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.038445 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03859 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04539 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.045264 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048798 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.048965 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048718 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041965 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.031551 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.033427 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03818 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.0492 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.036173 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.041965 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046655 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038179 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050434 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037883 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.036767 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.040759 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037359 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.038859 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.040768 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047256 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.047434 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.035975 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.034367 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.066794 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.066794 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.056448 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.051655 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050883 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051552 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045033 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04382 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.041858 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.035901 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.035881 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038145 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043086 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046452 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044034 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045209 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.036715 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.037264 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.037264 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.05053 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.05053 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.03271 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044647 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.043359 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049132 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.037887 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03818 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044957 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.034052 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.046237 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.042885 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049132 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049887 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.048583 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043564 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039621 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.041825 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.040962 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.041476 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.041476 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.041476 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.036101 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.058667 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.032353 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.04071 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041282 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.047764 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.047985 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.045158 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.0441 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.045733 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.038445 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03859 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04539 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.045264 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048798 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.048965 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048718 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.041965 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.031551 |  | Single 640527 MACON3 345 777450 G24-016-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.041628 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.031519 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.042153 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.034338 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.042946 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.0347 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033499 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.038193 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.03929 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.052951 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.052951 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045084 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.041597 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.040948 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04151 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.03561 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.034053 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.035246 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.033303 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.037197 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.034249 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.035837 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.040791 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.040791 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.040315 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.034208 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.040654 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.033361 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.035306 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.038107 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.033152 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.040654 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041513 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.041085 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.033628 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030341 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.032309 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033043 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.032028 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.032028 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.032028 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.047162 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.034492 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.039211 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.039672 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.035495 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.034323 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.037721 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.034012 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.034678 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036408 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038117 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.039871 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039316 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.039467 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.031519 |  | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.052242 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031573 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.0311 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.031463 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.0445 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.10864 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.030847 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.03162 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030129 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030981 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030919 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030981 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030258 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.10863 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.046897 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031862 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031186 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034026 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031019 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.030208 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031013 |  | P23:345:GRDA:TONNECE CB9580:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031343 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03139 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032374 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05606 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05606 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03044 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030131 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030131 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030983 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030574 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038381 |  | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03817 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.043914 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.049702 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.041438 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.047931 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053364 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.10962 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048212 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.043546 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.042198 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.046728 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.053446 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.099308 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.068585 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.049916 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.051503 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.041181 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039007 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034385 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034385 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.041827 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.045963 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.046416 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04602 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.050494 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.050184 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.067933 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.041091 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.041012 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.072063 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.050299 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.050005 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.049686 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.050514 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.042142 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.042844 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.042844 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046192 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046192 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036786 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.057639 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.053824 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049242 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.1184 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.043914 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.049676 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.047867 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.052824 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.051089 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049242 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048726 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050229 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049288 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.057749 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.053603 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.065894 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.05445 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.05445 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.05445 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.041341 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.041082 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.044679 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.047286 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.06904 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.050435 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.050535 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.049457 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.049913 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.055276 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.109 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.10251 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.051895 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.05536 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.049054 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04755 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.048704 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.047931 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.035272 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.038934 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.036489 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038989 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.041051 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.03714 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.037675 |  | Single 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.042002 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.048717 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.065274 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.045892 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.053935 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.067445 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.056508 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.066801 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.048299 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.046731 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.052268 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.049461 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.055091 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.056148 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.060769 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.062372 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.045613 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.043326 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.09072 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.09072 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.065371 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.063194 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.062663 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.063121 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.058127 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.05651 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.058554 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.045509 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.045475 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.051122 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.055825 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.059719 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.056711 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.058368 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.046659 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.047432 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.047432 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.062853 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.062853 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.040972 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.065135 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.05682 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.063547 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.057782 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.048717 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.05775 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.044223 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.061183 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.055665 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.063547 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.064496 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.064477 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.05608 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.053016 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.05489 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.055027 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.054628 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.054628 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.054628 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.045791 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.067887 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.041549 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.052342 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.057468 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.062059 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.062664 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.057928 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.056764 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.060793 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.059272 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.054791 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.059054 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.061706 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.062455 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.061469 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.061834 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.053935 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.03933 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.037905 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.034408 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.04566 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.037386 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.03529 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.043449 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.055575 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.038473 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.034105 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.031283 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.063566 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.063566 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.14971 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.096325 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.094107 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.096112 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.051637 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.049844 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.034036 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.033921 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043859 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.05487 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.050469 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.051609 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.035188 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.035986 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.035986 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.11118 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.11118 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039231 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.048128 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.037905 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.054901 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.035801 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.043303 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.048128 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.043492 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.034433 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.049371 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034654 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031901 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031901 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031901 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.034306 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.077944 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.041919 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.047133 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042893 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.05631 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.051805 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.030381 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.047025 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.058977 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.085042 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.067836 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.04566 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043606 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033338 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046345 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.044741 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031756 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.032019 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035718 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.039806 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041294 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.049333 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.049333 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044443 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.042171 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.041663 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.042102 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037336 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.035771 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037366 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.033618 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.035143 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.038815 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03597 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037564 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.041479 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.041479 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.045451 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036082 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042387 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.036951 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.040196 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03498 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042387 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.04321 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04365 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.035372 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.032272 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034185 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036432 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033913 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033913 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033913 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046301 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031829 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036575 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.041023 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.041587 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.037112 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.036008 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.039652 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.031482 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038254 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.040705 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041377 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040379 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.040797 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033338 |  | Single 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.03678 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.047564 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.080114 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.043302 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.056271 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.072149 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.086008 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.046934 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.044492 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.053448 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.035767 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.034369 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.071085 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.070856 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.042903 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.039574 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.10737 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.10737 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.098663 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.084127 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.08321 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.084028 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.064073 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.060383 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037469 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.042772 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.042725 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.057739 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.068414 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.061412 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.064601 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.044374 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.045456 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.045456 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.088604 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.088604 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.036107 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.052679 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.055797 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.077749 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.047564 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.064468 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.065941 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.056588 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.077749 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.080416 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.074341 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.060242 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039503 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.05072 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.037755 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.048775 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.048775 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.048775 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.043163 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.078698 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.05282 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03533 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.072498 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.073167 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.065304 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.06152 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.061474 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.064126 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.061429 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.076141 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.079361 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.076143 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.056271 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.033671 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.03111 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.037766 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033565 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.040425 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.042564 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037876 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030904 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.030137 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.032793 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.033384 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.04212 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038607 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036128 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.037181 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.034605 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.034605 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.034915 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.035623 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.035602 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.035619 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.035421 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.034822 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.039104 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.038629 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.034683 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035801 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03479 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.035505 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.030104 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.030493 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.030493 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.035574 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.035574 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.040985 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.035743 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.036982 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.042358 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.03111 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.035091 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.030739 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.037095 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.034782 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.036982 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037179 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.037936 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.034512 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.035341 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035071 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038278 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.035164 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.035164 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.035164 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.035566 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.032942 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039021 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036765 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.03704 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.035092 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.034834 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.037353 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.041933 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.042415 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036069 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038039 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.036464 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.035597 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.036095 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033565 |  | P23:345:WERE:EMPR-345-330:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.030717 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032367 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.040532 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.030656 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.03937 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033657 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030535 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033626 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.03496 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033114 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030243 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.040914 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030585 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030243 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030335 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030814 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033331 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033843 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030184 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030362 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031069 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.03973 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.03992 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.031378 |  | Single 541200 PHILL7 345 541201 SIBLEY7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | ASGI-2024-023 |  | Non-Converged |  |  | 0.032314 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034732 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.038646 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.033667 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.036532 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.040531 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.049862 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.038412 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034574 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033995 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.035978 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.037584 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048398 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.042497 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.037984 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.038732 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.033556 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.03261 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.03435 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.03435 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.035853 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.036983 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.037063 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.036992 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037799 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.037489 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042426 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.033516 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.03348 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.043738 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037455 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.037863 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.037379 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037839 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.033971 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.034278 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.034278 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.037004 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.037004 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-232 |  | Non-Converged |  |  | 0.031647 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.041573 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.038579 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.038225 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050693 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034732 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.037502 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.035563 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.038943 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037649 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.038225 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.038211 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.038845 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.037187 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039164 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.038253 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.042118 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.038455 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.038455 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.038455 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.033624 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.036034 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-312 |  | Non-Converged |  |  | 0.034434 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.036148 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.042651 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.038357 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.038494 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.03746 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.037441 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.039475 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.049261 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.048985 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038342 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.039817 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03796 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.037289 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.03773 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.036532 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-376 |  | Non-Converged |  |  | 0.030993 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.030944 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.046149 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.035881 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.048888 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.031593 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.047284 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.030552 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.034299 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.031434 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.034562 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.038261 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.042349 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.043837 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.051876 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.051876 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.046986 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.044714 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.044206 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.044645 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.039879 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.038314 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.039909 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.036161 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.037686 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.041358 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.038513 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040107 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.044022 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.044022 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.047994 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.038625 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.04493 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.030944 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.039494 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.042739 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.037523 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.04493 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.045753 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.046193 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.037915 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.034815 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.036728 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.038975 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.036456 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.036456 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.036456 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048844 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.034372 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.039118 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.043566 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.04413 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.039655 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.038551 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042195 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.03029 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.034025 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.040797 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.043248 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.04392 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.042921 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.04334 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.035881 |  | P12:345:WERE:WAVS-WOLF-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034707 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.050259 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.031158 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.040989 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.053987 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.074375 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.050384 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.034181 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.032215 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.039024 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.040328 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.070339 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.054359 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.047399 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.049394 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.030803 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.047651 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.047651 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.047265 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.047395 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.0472 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.047367 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.045685 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.04424 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.055405 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.030678 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.030606 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.054054 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.043764 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.046642 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.044126 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.045881 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.032127 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033094 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033094 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.046923 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.046923 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.055463 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.046469 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.049088 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.077175 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034707 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.044938 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-243 |  | Non-Converged |  |  | 0.033188 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.049217 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.04407 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.049088 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.049475 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.050465 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.043414 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.045515 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.0448 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.053091 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.045043 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.045043 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.045043 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.031028 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.048351 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.039386 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.055379 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.048626 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.049114 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.044954 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.044291 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.050187 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.07302 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.07188 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.04718 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.050925 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.048223 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.04669 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047603 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.040989 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043606 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033338 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046345 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.044741 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031756 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.032019 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035718 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.039806 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041294 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.049333 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.049333 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044443 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.042171 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.041663 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.042102 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037336 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.035771 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037366 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.033618 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.035143 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.038815 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03597 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037564 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.041479 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.041479 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.045451 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036082 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042387 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.036951 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.040196 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03498 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042387 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.04321 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04365 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.035372 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.032272 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034185 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036432 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033913 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033913 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033913 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046301 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031829 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036575 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.041023 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.041587 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.037112 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.036008 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.039652 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.031482 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038254 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.040705 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041377 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040379 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.040797 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033338 |  | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031343 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.03139 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.032374 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.05606 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.05606 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03044 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030131 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030131 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030983 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030574 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.038381 |  | Single 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.030449 |  | Single 580555 MONETT345 345 800102 NBRAN345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.036772 |  | Single 580555 MONETT345 345 800102 NBRAN345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.039164 |  | Single 580555 MONETT345 345 800102 NBRAN345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.036989 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03196 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034064 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037886 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031028 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036141 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.035826 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.048374 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.048374 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045934 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.040743 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.040152 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04067 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.034344 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.033399 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030506 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032704 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035519 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03359 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034475 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.039931 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.039931 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032383 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032702 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037389 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.03439 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034826 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032514 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037389 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037877 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.036602 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.033219 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.031456 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.030146 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031108 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031108 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031108 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.044859 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.03094 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030035 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036299 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.036367 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034581 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033665 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.034264 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034462 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033656 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037415 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.038192 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.037592 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03196 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.040916 |  | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.040916 |  | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031481 |  | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.033703 |  | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043606 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033338 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046345 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.044741 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031756 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.032019 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035718 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.039806 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041294 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.049333 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.049333 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044443 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.042171 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.041663 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.042102 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037336 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.035771 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037366 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.033618 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.035143 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.038815 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03597 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037564 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.041479 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.041479 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.045451 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036082 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042387 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.036951 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.040196 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03498 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042387 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.04321 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04365 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.035372 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.032272 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034185 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036432 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033913 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033913 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033913 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046301 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031829 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036575 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.041023 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.041587 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.037112 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.036008 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.039652 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.031482 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038254 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.040705 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041377 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040379 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.040797 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033338 |  | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031004 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.031738 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030161 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.030015 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.04029 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.04029 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037573 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.033657 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.033185 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.033598 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.033005 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.033005 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031221 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031221 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031632 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030679 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.037109 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.030346 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030426 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031183 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031683 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031277 |  | P42:345:NPPD:BKR-GGS-3322:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.040486 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.045325 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.03628 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034962 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.21117 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.21117 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.057923 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.047809 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.044925 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.047404 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032021 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030224 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.034908 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030844 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032306 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.04211 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.04211 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.039459 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.032354 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032023 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.039459 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041261 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.036066 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.030277 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.092026 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036524 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.036633 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.032797 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030823 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.030432 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03178 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.039595 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.039977 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.0397 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.031465 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032881 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.039003 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.031402 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037988 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033571 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.030709 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031338 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.030261 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.030266 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.030261 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030367 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030018 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033673 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.034141 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.030541 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030414 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.030211 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.030211 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033493 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030811 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031083 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.039501 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030129 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.031394 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03006 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031083 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031142 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03157 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.030915 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.030424 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.033259 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.030545 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.030545 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.030545 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.030015 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03377 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031061 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031198 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030114 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030005 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.031744 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.038506 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.038415 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.030822 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032028 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.030827 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.030298 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.030629 |  | Single 542940 ATLNTIC7 345 542977 CRAIG7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.060733 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.038288 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03129 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.07402 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.045723 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.051214 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.051214 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.051214 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.033592 |  | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.032019 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.033711 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.054197 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.03082 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.035165 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.038565 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.047524 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.032367 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.033648 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.032591 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.032192 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.046499 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.056472 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.031884 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.032322 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.031528 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.032637 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.037216 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036356 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031874 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.066633 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.031758 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034752 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.033038 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031874 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031462 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032315 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.03098 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.040955 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.035992 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.048666 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037029 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037029 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037029 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.046549 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.032833 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032877 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.031573 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.031938 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.037308 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.074202 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.037977 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034033 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.036623 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031763 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.03054 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031509 |  | Single 549984 BROOKLINE7 345 580555 MONETT345 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.043606 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.033338 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.046345 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.044741 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031756 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.032019 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035718 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.039806 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.041294 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.049333 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.049333 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044443 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.042171 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.041663 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.042102 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.037336 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.035771 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037366 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.033618 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.035143 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.038815 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03597 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.037564 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.041479 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.041479 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.045451 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.036082 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.042387 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.036951 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.040196 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.03498 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.042387 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.04321 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.04365 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.035372 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.032272 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.034185 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036432 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.033913 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.033913 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.033913 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.046301 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.031829 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.036575 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.041023 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.041587 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.037112 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.036008 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.039652 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.031482 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.038254 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.040705 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.041377 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.040379 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.040797 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.033338 |  | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.033058 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034708 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-058 |  | Non-Converged |  |  | 0.03557 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.033337 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.035592 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.032323 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.03152 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.03233 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.03314 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.03314 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.031984 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.031802 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.031678 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.031784 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.030664 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.030043 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.032876 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031738 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.031158 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.030054 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030752 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.031626 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.031626 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034735 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.030634 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.032436 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.034677 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.030413 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.032086 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.032436 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032694 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.033064 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.032006 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.032724 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.032739 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.032068 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032308 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.030445 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.030095 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.032188 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-345 |  | Non-Converged |  |  | 0.034498 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-346 |  | Non-Converged |  |  | 0.035864 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.03119 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.032654 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.032001 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.031393 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031716 |  | P23:345:WERE:JEC-345-20:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-025 |  | Non-Converged |  |  | 0.034951 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.046774 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-044 |  | Non-Converged |  |  | 0.032846 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.039012 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.041669 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.048362 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-068 |  | Non-Converged |  |  | 0.03464 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-071 |  | Non-Converged |  |  | 0.033463 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.037714 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.032682 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.030455 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.03496 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.045098 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.04476 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-122 |  | Non-Converged |  |  | 0.032641 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-123 |  | Non-Converged |  |  | 0.030993 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.072826 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.072826 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.058788 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.05158 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.050493 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.051437 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.042366 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.040978 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.03612 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-177 |  | Non-Converged |  |  | 0.032564 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-178 |  | Non-Converged |  |  | 0.032554 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.031696 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.040018 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.044147 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.041289 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.042567 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-220 |  | Non-Converged |  |  | 0.033408 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-226 |  | Non-Converged |  |  | 0.033977 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-227 |  | Non-Converged |  |  | 0.033977 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.049932 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.049932 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038897 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.039885 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.047245 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-241 |  | Non-Converged |  |  | 0.034951 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.042426 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.043141 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.039696 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.047245 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.048185 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.045969 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.040771 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.03488 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.03808 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.035608 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.037548 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.037548 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.037548 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-305 |  | Non-Converged |  |  | 0.032772 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.061474 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.037573 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.035403 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.045457 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.045608 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.042705 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.041362 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.042332 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.042536 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.04124 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.047072 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.047768 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.047167 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.039012 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.052242 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.031573 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.0311 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.031463 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.0445 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-180 |  | Non-Converged |  |  | 0.10864 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.030847 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.03162 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030129 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030981 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.030919 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030981 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030258 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.10374 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.046897 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.031862 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.031186 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034026 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.031019 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.030208 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.031013 |  | P23:345:AEPW:FLINT CREEK CB 19140 NBTB:::: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-029 |  | Non-Converged |  |  | 0.036989 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-052 |  | Non-Converged |  |  | 0.03196 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.034064 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-062 |  | Non-Converged |  |  | 0.037886 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-083 |  | Non-Converged |  |  | 0.031028 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-119 |  | Non-Converged |  |  | 0.036141 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.035826 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.048374 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.048374 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.045934 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-157 |  | Non-Converged |  |  | 0.040743 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-158 |  | Non-Converged |  |  | 0.040152 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-161 |  | Non-Converged |  |  | 0.04067 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-164 |  | Non-Converged |  |  | 0.034344 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-165 |  | Non-Converged |  |  | 0.033399 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.030506 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-184 |  | Non-Converged |  |  | 0.032704 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-187 |  | Non-Converged |  |  | 0.035519 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03359 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.034475 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-229 |  | Non-Converged |  |  | 0.039931 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-230 |  | Non-Converged |  |  | 0.039931 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032383 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032702 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.037389 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-242 |  | Non-Converged |  |  | 0.03439 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-245 |  | Non-Converged |  |  | 0.034826 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-250 |  | Non-Converged |  |  | 0.032514 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.037389 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.037877 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.036602 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-267 |  | Non-Converged |  |  | 0.033219 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-291 |  | Non-Converged |  |  | 0.031456 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.030146 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.031108 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.031108 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-298 |  | Non-Converged |  |  | 0.031108 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-308 |  | Non-Converged |  |  | 0.044859 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-316 |  | Non-Converged |  |  | 0.03094 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.030035 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-332 |  | Non-Converged |  |  | 0.036299 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.036367 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-337 |  | Non-Converged |  |  | 0.034581 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.033665 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.034264 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034462 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033656 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.037415 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-367 |  | Non-Converged |  |  | 0.038192 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-369 |  | Non-Converged |  |  | 0.037592 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-373 |  | Non-Converged |  |  | 0.03196 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29WP | N0 | GEN-2024-114 |  | Non-Converged |  |  | 0.76399 |  | Single 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | TDF Impact | Add line 505418 JONESBO5 161 774620 G23-132-TAP 161 P2
Non-Converged | 04ALL | 0 | 29WP | N0 | GEN-2024-134 |  | Non-Converged |  |  | 0.04842 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29WP | N0 | GEN-2024-135 |  | Non-Converged |  |  | 0.04842 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.092229 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.055428 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.048718 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.048718 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058141 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.11987 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.11987 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.063275 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.059621 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.056567 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.082181 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.082181 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.058008 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.058008 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059183 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059291 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.061873 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.059294 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.056434 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082421 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082421 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.068506 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059049 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.056692 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057388 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.091253 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.05461 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.055772 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.055413 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.055399 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.08464 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.056902 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.055416 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.056705 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.055386 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.055258 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.054522 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058001 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058001 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.055412 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.055908 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.055908 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.048814 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.056715 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.056692 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.055326 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.055362 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.054149 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.068506 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.055101 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.055101 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062713 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.055436 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059566 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.05714 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.054729 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.054729 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058248 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.071644 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.071644 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.059774 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05863 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057614 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.063948 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.063948 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.058076 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.058076 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.058494 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.058526 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.059268 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058635 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05756 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.064209 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.064209 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061435 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.058448 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057605 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057947 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.05922 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.056802 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057271 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.057141 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.057136 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.065323 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05768 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.05714 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057664 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057129 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057075 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.056766 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058201 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058201 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.05714 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057326 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057326 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.059605 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057613 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057605 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.05711 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.057118 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056651 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061435 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.057034 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.057034 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.061344 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.057149 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055213 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055213 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055213 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.066328 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.066328 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.066328 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.068095 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.068095 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.068095 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.068095 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.068095 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.068095 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.065438 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.065438 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.065438 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.058313 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.058313 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.058313 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.058313 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.058313 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.058313 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.064267 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.064267 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.064267 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.065129 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.065129 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.065129 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.065991 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.065991 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.065991 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.06124 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.06124 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.06124 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.06124 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.06124 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.06124 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.065607 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.065607 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.065607 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.065607 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.065607 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.065607 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.065245 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.065245 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.065245 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.065221 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.065221 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.065221 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.064654 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.064654 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.064654 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.06511 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.06511 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.06511 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.066039 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.066039 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.066039 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.061345 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.061345 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.061345 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.061345 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.061345 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.061345 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.063012 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.063012 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.063012 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.065283 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.065283 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.065283 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066017 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066017 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066017 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.065705 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.065705 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.065705 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055169 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055169 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055169 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.06675 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.06675 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.06675 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06631 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06631 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06631 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066385 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066385 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066385 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066386 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066386 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066386 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.061251 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.061251 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.061251 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.065951 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.065951 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.065951 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.066416 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.066416 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.066416 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.065958 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.065958 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.065958 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.066425 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.066425 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.066425 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.066476 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.066476 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.066476 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.066785 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.066785 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.066785 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.065478 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.065478 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.065478 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.065478 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.065478 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.065478 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.06639 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.06639 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.06639 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.066259 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.066259 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.066259 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.066259 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.066259 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.066259 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065815 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065815 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065815 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.06601 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.06601 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.06601 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066017 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066017 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066017 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.066383 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.066383 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.066383 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.066429 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.066429 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.066429 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.066652 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.066652 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.066652 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.063012 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.063012 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.063012 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.06645 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.06645 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.06645 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.06645 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.06645 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.06645 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062774 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062774 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062774 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.06639 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 507768 SWSHRV9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.06639 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 880 MVAR switched shunt at SWSHRV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.06639 |  | Single 507768 SWSHRV9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.0338 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.051324 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.051324 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.63351 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.63351 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.034041 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.08266 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.088875 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.091399 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.15052 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.067276 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.12349 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.12349 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.15327 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.15039 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.073546 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.19696 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.066491 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.15144 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.088334 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.07202 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.046431 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.065179 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066311 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.067078 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.093805 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.059168 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.067876 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.058703 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057026 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.045122 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.075733 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.075733 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.065039 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.066854 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.066854 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.088911 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.088334 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.07265 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.060227 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.070918 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.065378 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.065378 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.063317 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14156 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14156 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14156 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17492 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17492 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17492 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.08858 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.08858 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.08858 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.08858 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.08858 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.08858 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22341 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22341 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22341 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.19149 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.19149 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.19149 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.19149 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.19149 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.19149 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.2396 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.2396 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.2396 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.217 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.217 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.217 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.20065 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.20065 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.20065 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.25163 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.25163 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.25163 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.25163 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.25163 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.25163 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20627 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20627 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20627 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20627 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20627 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20627 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.2158 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.2158 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.2158 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21623 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21623 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21623 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22245 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22245 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22245 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.22847 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.22847 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.22847 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19859 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19859 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19859 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.26376 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.26376 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.26376 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.26376 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.26376 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.26376 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.27494 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.27494 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.27494 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21484 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21484 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21484 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19538 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19538 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19538 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.2133 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.2133 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.2133 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14109 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14109 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14109 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.17303 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.17303 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.17303 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18725 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18725 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18725 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18085 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18085 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18085 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18032 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18032 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18032 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.30089 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.30089 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.30089 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19717 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19717 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19717 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18318 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18318 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18318 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20271 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20271 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20271 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18284 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18284 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18284 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18112 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18112 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18112 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.1719 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.1719 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.1719 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22279 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22279 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22279 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22279 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22279 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22279 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18122 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18122 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18122 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18907 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18907 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18907 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18907 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18907 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18907 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10217 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10217 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10217 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19557 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19557 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19557 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19538 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19538 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19538 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17752 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17752 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17752 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.1819 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.1819 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.1819 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15132 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15132 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15132 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.27494 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.27494 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.27494 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17642 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17642 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17642 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17642 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17642 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17642 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.20814 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.20814 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.20814 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18221 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18221 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18221 |  | Single 515378 WWRDEHV9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.15182 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.15182 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.15182 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28157 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28157 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28157 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.31094 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.31094 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.31094 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.31094 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.31094 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.31094 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.26647 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.26647 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.26647 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24459 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24459 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24459 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.25995 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.25995 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.25995 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.27657 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.27657 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.27657 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20073 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20073 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20073 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20073 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20073 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20073 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.26911 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.26911 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.26911 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.26911 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.26911 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.26911 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26222 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26222 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26222 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26178 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26178 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26178 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25121 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25121 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25121 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.25999 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.25999 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.25999 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.27743 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.27743 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.27743 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.2026 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.2026 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.2026 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.2026 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.2026 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.2026 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22235 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22235 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22235 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26295 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26295 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26295 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.27691 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.27691 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.27691 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27142 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27142 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27142 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.15159 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.15159 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.15159 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29091 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29091 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29091 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.28247 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.28247 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.28247 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.28342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.28342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.28342 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.28339 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.28339 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.28339 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20101 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20101 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20101 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.27566 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.27566 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.27566 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.28439 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.28439 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.28439 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.27607 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.27607 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.27607 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.28453 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.28453 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.28453 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.28553 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.28553 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.28553 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29158 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29158 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29158 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.26726 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.26726 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.26726 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.26726 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.26726 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.26726 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.2836 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.2836 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.2836 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28152 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28152 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28152 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28152 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28152 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28152 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22561 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22561 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22561 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.27678 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.27678 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.27678 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.27691 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.27691 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.27691 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.28301 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.28301 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.28301 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.28453 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.28453 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.28453 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.28631 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.28631 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.28631 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22235 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22235 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22235 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.28435 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.28435 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.28435 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.28435 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.28435 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.28435 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18177 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18177 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18177 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.2837 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.2837 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.2837 |  | Single 514812 MINCO9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.033762 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.051286 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.051286 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.63347 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.63347 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.034003 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055907 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.092126 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.088761 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.088761 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.094367 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.070673 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.070673 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.092554 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.092838 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.093681 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.084862 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.084862 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.093137 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.093137 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.09305 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.093022 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.091979 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.093932 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.093613 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.086472 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.086472 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.092391 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.093065 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.093223 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.094121 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055713 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.093074 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.093249 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.092846 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.092799 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.090112 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.093213 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.093153 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.093787 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.093143 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.093117 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.09306 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.094419 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.094419 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.092898 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.093287 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.093287 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.081467 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.093222 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.093223 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.092525 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.093064 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.090759 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.092391 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.092609 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.092609 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.083581 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.092992 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14953 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14953 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14953 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.2276 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.2276 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.2276 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24457 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24457 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24457 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24457 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24457 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24457 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.21898 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.21898 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.21898 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16524 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16524 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16524 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16524 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16524 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16524 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20832 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20832 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20832 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.2163 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.2163 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.2163 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.22424 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.22424 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.22424 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.184 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.184 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.184 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.184 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.184 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.184 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.22072 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.22072 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.22072 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.22072 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.22072 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.22072 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21735 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21735 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21735 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21713 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21713 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21713 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.212 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.212 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.212 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21596 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21596 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21596 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.22469 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.22469 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.22469 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1847 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1847 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1847 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1847 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1847 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1847 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19669 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19669 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19669 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21771 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21771 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21771 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.22454 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.22454 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.22454 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.22151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.22151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.22151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14935 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14935 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14935 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.23141 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.23141 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.23141 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22727 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22727 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22727 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.22803 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.22803 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.22803 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22805 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22805 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22805 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.1832 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.1832 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.1832 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.22393 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.22393 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.22393 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22828 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22828 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22828 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.22392 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.22392 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.22392 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22836 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22836 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22836 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22885 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22885 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22885 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.23174 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.23174 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.23174 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21934 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21934 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21934 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21934 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21934 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21934 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22808 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22808 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22808 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2268 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2268 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2268 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2268 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2268 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2268 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.21284 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.21284 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.21284 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.22448 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.22448 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.22448 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.22454 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.22454 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.22454 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22806 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22806 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22806 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22841 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22841 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22841 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.23082 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.23082 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.23082 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19669 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19669 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19669 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22868 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22868 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22868 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22868 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22868 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22868 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18573 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18573 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18573 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22806 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22806 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22806 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.24848 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.24848 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.35865 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.34136 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.3537 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.1165 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.033015 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.13669 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.034566 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.034566 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.11861 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.1165 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.050897 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.068947 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.067327 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.059398 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.059398 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.072175 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.07074 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.066422 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.071695 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.071695 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.068543 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.068543 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070015 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.070082 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.072504 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.069312 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.06636 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.070419 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.070419 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.073968 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.069867 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066869 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.066673 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.050796 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.063913 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06571 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066666 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066798 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.067853 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.067136 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065585 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.066213 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065586 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.065363 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.06376 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067086 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067086 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066482 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.065869 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.065869 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.12211 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.066898 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066869 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.067648 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065781 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071516 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.073968 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.067231 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.067231 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.112 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.066205 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.04447 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040067 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.033721 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.033721 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.043518 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.044857 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.044857 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.044051 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.042681 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.042112 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.045673 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.045673 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.042233 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.042233 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.042689 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.04271 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042851 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.043615 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041983 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.046624 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.046624 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.04625 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.042643 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041712 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.042926 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.04448 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040595 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.041313 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040758 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.040705 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.049401 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041799 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.041055 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.042279 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.041032 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.040946 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.04054 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.043506 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.043506 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.040807 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.041414 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.041414 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041722 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041712 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.040407 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.040944 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.038149 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.04625 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.040385 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.040385 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.035151 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.040909 |  | P42:345:OKGE:SB_REOW7319:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.17561 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.030536 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.14843 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.14843 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.040203 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.033527 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.080528 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.080528 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.030642 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.030642 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.032702 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.032906 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.037845 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.032618 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.078456 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.078456 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.049671 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.032463 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1756 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.076476 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.030283 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.030283 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.049671 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.038169 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.19149 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.11909 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.11909 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.32873 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.10807 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.30791 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18495 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18495 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13376 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13066 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.030207 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18213 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.30433 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.13915 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.24229 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.33034 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.28656 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.27755 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.25545 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.25169 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.23361 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.2812 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.31226 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.28143 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.28106 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.28686 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.34656 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.34656 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.25988 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.27823 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.27823 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.038141 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.24138 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.24229 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.23007 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.27473 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.12403 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.24669 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.24669 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.26734 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.043973 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.059356 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.064764 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.064764 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.056896 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047884 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047884 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056769 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.057822 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057531 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.052886 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.052886 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.057739 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.057739 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057714 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057697 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.057676 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.057145 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.057593 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052641 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052641 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.055134 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057721 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057764 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057103 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.043925 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057793 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057795 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058395 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058459 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.051603 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.057759 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057946 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057368 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057963 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057957 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057787 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.056866 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.056866 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058319 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057774 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057774 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065193 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057763 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057764 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058854 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058062 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.061198 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.055134 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058795 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058795 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062002 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058189 |  | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.041872 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.057255 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.062663 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.062663 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.054795 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.045783 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.045783 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054668 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.055721 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.05543 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.050785 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.050785 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.055638 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.055638 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.055613 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.055596 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055575 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.055044 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.055492 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.05054 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.05054 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.053033 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.05562 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.055663 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.055002 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.041823 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.055692 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.055694 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.056294 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.056358 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.049502 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.055658 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.055845 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.055267 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.055862 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.055856 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.055686 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.054765 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.054765 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.056218 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.055673 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.055673 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.063092 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.055662 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.055663 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.056753 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.055961 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.059097 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.053033 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.056693 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.056693 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.059901 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.056088 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059794 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040747 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.038902 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.038902 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.041553 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053373 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053373 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.042784 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.041868 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.0411 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.047321 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.047321 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.041453 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.041453 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.041762 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.041788 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042402 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.041837 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041062 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.047043 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.047043 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.044102 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.041727 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041107 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.041339 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.059884 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040534 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.040862 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040759 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.040755 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.046765 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041162 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.040765 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.041139 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.040757 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.04072 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.040509 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.041518 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.041518 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.04076 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.040901 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.040901 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.040618 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041113 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041107 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.04073 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.040748 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040374 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.044102 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.040673 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.040673 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.043238 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.040768 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.04447 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040067 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.033721 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.033721 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.043518 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.044857 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.044857 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.044051 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.042681 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.042112 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.045673 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.045673 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.042233 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.042233 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.042689 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.04271 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042851 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.043615 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041983 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.046624 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.046624 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.04625 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.042643 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041712 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.042926 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.04448 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040595 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.041313 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040758 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.040705 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.049401 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041799 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.041055 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.042279 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.041032 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.040946 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.04054 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.043506 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.043506 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.040807 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.041414 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.041414 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041722 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041712 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.040407 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.040944 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.038149 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.04625 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.040385 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.040385 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.035151 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.040909 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059566 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.05714 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.054729 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.054729 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058248 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.071644 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.071644 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.059774 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05863 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057614 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.063948 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.063948 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.058076 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.058076 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.058494 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.058526 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.059268 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058635 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05756 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.064209 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.064209 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061435 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.058448 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057605 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057947 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.05922 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.056802 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057271 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.057141 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.057136 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.065323 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05768 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.05714 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057664 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057129 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057075 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.056766 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058201 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058201 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.05714 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057326 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057326 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.059605 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057613 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057605 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.05711 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.057118 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056651 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061435 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.057034 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.057034 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.061344 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.057149 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18829 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.066761 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.042631 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.054686 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.098075 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.070411 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.070411 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.058686 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.058095 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058249 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.10088 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059886 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.083513 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.073728 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.067794 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.091078 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.1416 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14444 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.081594 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.10676 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.080346 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.10935 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.10416 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.064953 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067796 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067796 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.13549 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.091969 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.091969 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.083316 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.083513 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.1838 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.11484 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.2073 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.2073 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.12649 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.13261 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18043 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.16905 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.16905 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18721 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.15438 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.15438 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.18513 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.18414 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18478 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.17568 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.17568 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18411 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18411 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.18445 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.18444 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18307 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18668 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18455 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17899 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17899 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.18715 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.18443 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18371 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18625 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.13234 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.18235 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18334 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18218 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18206 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18711 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.18378 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18293 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1851 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18289 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18277 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18227 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18728 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18728 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18231 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18349 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18349 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15361 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18372 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18371 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18136 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18269 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.17648 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.18715 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.18146 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.18146 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.16293 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18255 |  | Single 515378 WWRDEHV9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.044874 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.09021 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.11306 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.11306 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.080068 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.051222 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.051222 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.075901 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.08203 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.083344 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.059295 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.059295 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.082955 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.082955 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081992 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081855 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.079891 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.080022 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.083648 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.059968 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.059968 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.06688 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.082116 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.084021 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.081316 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.044808 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.08568 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.084813 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.087057 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.087279 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.058998 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.083847 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.085578 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.082703 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.085657 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.085731 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.085729 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080073 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080073 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.08681 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.084641 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.084641 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.074196 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.084002 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.084021 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.088635 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.086001 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.097222 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.06688 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.088607 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.088607 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.046624 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.086363 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.043973 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.059356 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.064764 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.064764 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.056896 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047884 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047884 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056769 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.057822 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057531 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.052886 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.052886 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.057739 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.057739 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057714 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057697 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.057676 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.057145 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.057593 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052641 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052641 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.055134 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057721 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057764 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057103 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.043925 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057793 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057795 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058395 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058459 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.051603 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.057759 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057946 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057368 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057963 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057957 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057787 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.056866 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.056866 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058319 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057774 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057774 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065193 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057763 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057764 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058854 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058062 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.061198 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.055134 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058795 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058795 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062002 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058189 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.044874 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.09021 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.11306 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.11306 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.080068 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.051222 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.051222 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.075901 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.08203 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.083344 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.059295 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.059295 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.082955 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.082955 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081992 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081855 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.079891 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.080022 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.083648 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.059968 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.059968 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.06688 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.082116 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.084021 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.081316 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.044808 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.08568 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.084813 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.087057 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.087279 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.058998 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.083847 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.085578 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.082703 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.085657 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.085731 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.085729 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080073 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080073 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.08681 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.084641 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.084641 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.074196 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.084002 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.084021 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.088635 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.086001 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.097222 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.06688 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.088607 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.088607 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.046624 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.086363 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.050897 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.068947 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.067327 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.059398 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.059398 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.072175 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.07074 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.066422 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.071695 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.071695 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.068543 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.068543 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070015 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.070082 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.072504 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.069312 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.06636 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.070419 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.070419 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.073968 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.069867 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066869 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.066673 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.050796 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.063913 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06571 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066666 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066798 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.067853 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.067136 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065585 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.066213 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065586 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.065363 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.06376 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067086 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067086 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066482 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.065869 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.065869 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.12211 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.066898 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066869 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.067648 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065781 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071516 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.073968 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.067231 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.067231 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.112 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.066205 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.065187 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.060563 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.060563 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.068633 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.063394 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.065074 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.067953 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.045535 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.045535 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.06566 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.065573 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.062713 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.067285 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.067875 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.048667 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.048667 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061467 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.065743 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.067042 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.068482 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.067707 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.067484 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.06675 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066653 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.055291 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.066933 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.067426 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.068129 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.067417 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.067432 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.067725 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.068797 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.068797 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066865 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.067496 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.067496 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.032385 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.067031 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.067042 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.066084 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.067259 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.062794 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061467 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.066345 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.066345 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.038814 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.067059 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.072776 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0772 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.070856 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.070856 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.08041 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.080243 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.080243 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.085851 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.0823 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.07807 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.090044 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.090044 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080017 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080017 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081726 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081828 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.084392 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.082181 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077872 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.089474 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.089474 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.090936 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.081547 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.07808 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079235 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.072685 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.074662 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.076707 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.076573 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.076592 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.089446 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.078391 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.07626 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078165 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.076226 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.075984 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.074498 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080195 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080195 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.076518 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.076933 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.076933 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15384 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.078113 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.07808 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.076754 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.076245 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.076348 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.090936 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.076407 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.076407 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.11974 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.076469 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.13261 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18043 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.16905 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.16905 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18721 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.15438 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.15438 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.18513 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.18414 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18478 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.17568 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.17568 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18411 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18411 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.18445 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.18444 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18307 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18668 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18455 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17899 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17899 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.18715 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.18443 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18371 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18625 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.13234 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.18235 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18334 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18218 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18206 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18711 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.18378 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18293 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1851 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18289 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18277 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18227 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18728 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18728 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18231 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18349 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18349 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15361 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18372 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18371 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18136 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18269 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.17648 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.18715 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.18146 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.18146 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.16293 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18255 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.04775 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.080626 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.080626 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.62565 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.0571 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055683 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.030687 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.046035 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.046035 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.032127 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.031093 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.030233 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.037914 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.037914 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.030636 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.030636 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.03097 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.031 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.031728 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.031007 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.030194 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.037486 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.037486 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.033603 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.030932 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.030263 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.03047 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055828 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.030001 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.036906 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.030322 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.030272 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.030648 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.030648 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.03004 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.03004 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.030269 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.030263 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.033603 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.032273 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.097024 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.068454 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.038352 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.049735 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.13293 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.12217 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.12217 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070444 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.069796 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.032167 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.055925 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.13905 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.075197 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18252 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.11421 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.46312 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.23246 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.14974 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14688 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17208 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.19913 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.16355 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20888 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20145 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.39927 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.069978 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.069978 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.15546 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2154 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2154 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18137 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18252 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.12845 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.1814 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.037079 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.14393 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.14393 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.16124 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.13588 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.20159 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.20159 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.10107 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.072323 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.097287 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.12004 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.11048 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.11048 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.099972 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.099353 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.086042 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.092786 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.12171 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.035151 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.10107 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.12241 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.10991 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.14473 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.13105 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.13484 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.13505 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.12048 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.1346 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.11865 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.13489 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.13651 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.14582 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.10208 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.10208 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.13481 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.12941 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.12941 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.11621 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.1222 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.12241 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.13601 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.13531 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15075 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.035151 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.13773 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.13773 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.032412 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.13446 |  | Single 515378 WWRDEHV9 765 526001 CRWFSHDRW9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.5344 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.5344 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.040178 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.030906 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.041157 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.041157 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.038434 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10894 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10894 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.05319 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.05319 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.043327 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055683 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.030687 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.046035 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.046035 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.032127 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.031093 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.030233 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.037914 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.037914 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.030636 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.030636 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.03097 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.031 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.031728 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.031007 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.030194 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.037486 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.037486 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.033603 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.030932 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.030263 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.03047 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055828 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.030001 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.036906 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.030322 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.030272 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.030648 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.030648 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.03004 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.03004 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.030269 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.030263 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.033603 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.032273 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.044874 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.09021 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.11306 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.11306 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.080068 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.051222 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.051222 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.075901 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.08203 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.083344 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.059295 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.059295 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.082955 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.082955 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081992 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081855 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.079891 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.080022 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.083648 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.059968 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.059968 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.06688 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.082116 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.084021 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.081316 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.044808 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.08568 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.084813 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.087057 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.087279 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.058998 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.083847 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.085578 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.082703 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.085657 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.085731 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.085729 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080073 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080073 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.08681 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.084641 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.084641 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.074196 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.084002 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.084021 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.088635 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.086001 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.097222 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.06688 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.088607 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.088607 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.046624 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.086363 |  | Single 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.050897 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.068947 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.078716 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.078716 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.067327 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.059398 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.059398 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.072175 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.07074 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.066422 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.071695 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.071695 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.068543 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.068543 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070015 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.070082 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.072504 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.069312 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.06636 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.070419 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.070419 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.073968 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.069867 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066869 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.066673 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.050796 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.067081 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06571 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066666 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066798 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.067853 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.067136 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065791 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.066213 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065841 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.066057 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.067226 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067086 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067086 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066482 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.065869 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.065869 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.12211 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.066898 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066869 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.067648 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065946 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071516 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.073968 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.067231 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.067231 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.112 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.066205 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.066659 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.078716 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.078716 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.060706 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055975 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.060356 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.063612 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.047025 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.047025 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.062248 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.062248 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.060726 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.060616 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.058378 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.059594 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.063869 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.047015 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.047015 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.050151 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.06089 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.06397 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.062019 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.067081 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.065214 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.06605 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066111 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.046356 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.063691 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065791 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.063333 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065841 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.066057 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.067226 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.060841 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.060841 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066009 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.064981 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.064981 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.073695 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.06394 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.06397 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.066443 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065946 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.069638 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.050151 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.066668 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.066668 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.055407 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.065895 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.03804 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.04102 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.039794 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.039794 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.041665 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.04332 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.04332 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.042264 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.041777 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.041298 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.042963 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.042963 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.041505 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.041505 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.041719 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.041732 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042004 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.041851 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041266 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.043148 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.043148 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.042987 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.041697 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041261 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.041492 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.037917 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040812 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.041086 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.041021 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.041018 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.04378 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041301 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.041017 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.041323 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.041011 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.040979 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.04079 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.041643 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.041643 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.04102 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.041118 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.041118 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.045536 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041266 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041261 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.041007 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.041005 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040757 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.042987 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.04097 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.04097 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.043842 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.041024 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.070718 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.053728 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.053728 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.081947 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.076694 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.077047 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.077344 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.076673 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.076673 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.07764 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.07753 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.073399 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.082224 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.07692 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.033541 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.033541 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.077539 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.077585 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.075501 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079973 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.072151 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.074526 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.072936 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.072772 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.22958 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.075703 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.073819 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.077807 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.073757 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.073452 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.071959 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.081914 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.081914 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.073083 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.07486 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.07486 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.047819 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.075524 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.075501 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.071897 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.073474 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.064752 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.077539 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.07196 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.07196 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05507 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.073393 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.035359 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.032938 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.04664 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.044849 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.044849 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.050162 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.044309 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04086 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.053918 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.053918 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.042054 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.042054 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.044241 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.044333 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.045109 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.047998 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.040339 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.058792 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.058792 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059615 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.044022 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.039552 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.044138 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.035279 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.034631 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.037685 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.035483 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.035283 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072499 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.039962 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.036585 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.041532 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.036485 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.036129 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.034397 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.046475 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.046475 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.035665 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.038103 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.038103 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.039596 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.039552 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.034157 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.036154 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059615 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.033975 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.033975 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.03605 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059794 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040747 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.038902 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.038902 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.041553 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053373 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053373 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.042784 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.041868 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.0411 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.047321 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.047321 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.041453 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.041453 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.041762 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.041788 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042402 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.041837 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041062 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.047043 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.047043 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.044102 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.041727 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041107 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.041339 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.059884 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040534 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.040862 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040759 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.040755 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.046765 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041162 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.040765 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.041139 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.040757 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.04072 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.040509 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.041518 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.041518 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.04076 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.040901 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.040901 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.040618 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041113 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041107 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.04073 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.040748 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040374 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.044102 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.040673 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.040673 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.043238 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.040768 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.072776 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0772 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.070856 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.070856 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.08041 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.080243 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.080243 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.085851 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.0823 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.07807 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.090044 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.090044 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080017 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080017 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081726 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081828 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.084392 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.082181 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077872 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.089474 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.089474 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.090936 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.081547 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.07808 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079235 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.072685 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.074662 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.076707 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.076573 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.076592 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.089446 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.078391 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.07626 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078165 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.076226 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.075984 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.074498 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080195 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080195 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.076518 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.076933 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.076933 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15384 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.078113 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.07808 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.076754 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.076245 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.076348 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.090936 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.076407 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.076407 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.11974 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.076469 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.030892 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.099075 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.054507 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.041201 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.041201 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.11542 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.13706 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.043869 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.059455 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.059455 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.09412 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.09412 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.12112 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.12135 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.16243 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.095158 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.043341 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.056531 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.056531 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.078836 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.11867 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.063219 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.04689 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.030786 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.042806 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.053277 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.056175 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.036507 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.068034 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.038194 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.043907 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.0375 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.036106 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049565 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049565 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050831 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.044368 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.044368 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.063728 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.063219 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.063163 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.041165 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29768 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.078836 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.042425 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.042425 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.042143 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.046512 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525824 'TUCO_TR1 1' 13 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.070718 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.053728 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.053728 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.081947 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.076694 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.077047 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.077344 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.076673 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.076673 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.07764 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.07753 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.073399 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.082224 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.07692 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.033541 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.033541 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.077539 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.077585 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.075501 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079973 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.072151 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.074526 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.072936 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.072772 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.22958 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.075703 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.073819 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.077807 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.073757 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.073452 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.071959 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.081914 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.081914 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.073083 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.07486 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.07486 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.047819 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.075524 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.075501 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.071897 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.073474 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.064752 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.077539 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.07196 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.07196 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05507 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.073393 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059794 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040747 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.038902 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.038902 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.041553 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053373 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053373 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.042784 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.041868 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.0411 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.047321 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.047321 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.041453 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.041453 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.041762 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.041788 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042402 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.041837 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041062 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.047043 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.047043 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.044102 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.041727 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041107 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.041339 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.059884 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040534 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.040862 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040759 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.040755 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.046765 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041162 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.040765 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.041139 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.040757 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.04072 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.040509 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.041518 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.041518 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.04076 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.040901 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.040901 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.040618 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041113 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041107 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.04073 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.040748 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040374 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.044102 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.040673 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.040673 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.043238 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.040768 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.043973 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.059356 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.064764 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.064764 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.056896 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047884 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047884 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056769 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.057822 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057531 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.052886 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.052886 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.057739 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.057739 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057714 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057697 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.057676 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.057145 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.057593 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052641 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052641 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.055134 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057721 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057764 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057103 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.043925 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057793 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057795 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058395 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058459 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.051603 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.057759 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057946 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057368 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057963 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057957 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057787 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.056866 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.056866 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058319 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057774 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057774 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065193 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057763 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057764 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058854 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058062 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.061198 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.055134 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058795 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058795 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062002 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058189 |  | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058844 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.58759 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.58759 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.057828 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.070151 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.079145 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.079145 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.065997 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.067227 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.068455 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.066714 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.051916 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.051916 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.067703 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.067703 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.068099 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.06809 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.068675 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.067083 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.066792 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.050877 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.050877 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.065136 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.068066 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.067246 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.066126 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.066486 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.066955 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.068098 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.068229 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.047738 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.067316 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.067139 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.066418 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.067164 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.067099 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.066439 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.065865 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.065865 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.067936 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.066964 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.066964 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.17852 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.067253 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.067246 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.069047 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.067366 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.073565 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.065136 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.068834 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.068834 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.11652 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.067667 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055683 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.030687 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.046035 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.046035 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.032127 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.031093 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.030233 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.037914 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.037914 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.030636 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.030636 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.03097 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.031 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.031728 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.031007 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.030194 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.037486 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.037486 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.033603 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.030932 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.030263 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.03047 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055828 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.030001 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.036906 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.030322 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.030272 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.030648 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.030648 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.03004 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.03004 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.030269 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.030263 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.033603 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.032273 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.043973 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.059356 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.064764 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.064764 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.056896 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047884 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047884 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056769 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.057822 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057531 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.052886 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.052886 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.057739 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.057739 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057714 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057697 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.057676 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.057145 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.057593 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052641 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052641 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.055134 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057721 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057764 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057103 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.043925 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057793 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057795 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058395 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058459 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.051603 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.057759 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057946 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057368 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057963 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057957 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057787 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.056866 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.056866 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058319 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057774 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057774 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065193 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057763 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057764 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058854 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058062 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.061198 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.055134 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058795 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058795 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062002 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058189 |  | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.04447 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040067 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.033721 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.033721 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.043518 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.044857 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.044857 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.044051 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.042681 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.042112 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.045673 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.045673 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.042233 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.042233 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.042689 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.04271 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.042851 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.043615 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.041983 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.046624 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.046624 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.04625 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.042643 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.041712 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.042926 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.04448 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.040595 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.041313 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040758 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.040705 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.049401 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.041799 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.041055 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.042279 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.041032 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.040946 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.04054 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.043506 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.043506 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.040807 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.041414 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.041414 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.041722 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.041712 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.040407 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.040944 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.038149 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.04625 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.040385 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.040385 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.035151 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.040909 |  | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.088663 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.068454 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.038352 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.049735 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.11465 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.12217 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.12217 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070444 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.069796 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.032167 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.055925 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.11879 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.075197 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18252 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.11421 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.46312 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.23246 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.14771 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14421 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17208 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.19913 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.16355 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.14228 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.13903 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.39927 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.069978 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.069978 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.1514 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2154 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2154 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18137 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18252 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.11922 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.15534 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.035068 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.12062 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.12062 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.16124 |  | Single 528015 PHANTOM7 345 528223 CHINA_DRAW7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.033758 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.27274 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.080836 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.055159 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.055159 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.074196 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.078789 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.045981 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.041164 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.6432 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.07124 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.034966 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.038075 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.035293 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.034966 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.033019 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.6432 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055683 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.030687 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.046035 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.046035 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.032127 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.031093 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.030233 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.037914 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.037914 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.030636 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.030636 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.03097 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.031 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.031728 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.031007 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.030194 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.037486 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.037486 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.033603 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.030932 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.030263 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.03047 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055828 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.030001 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.036906 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.030322 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.030272 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.030648 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.030648 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.03004 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.03004 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.030269 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.030263 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.033603 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.032273 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18829 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.066761 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.042631 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.054686 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.098075 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.070411 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.070411 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.058686 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.058095 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058249 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.10088 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059886 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.083513 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.073728 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.067794 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.091078 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.1416 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14444 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.081594 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.10676 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.080346 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.10935 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.10416 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.064953 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067796 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067796 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.13549 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.091969 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.091969 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.083316 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.083513 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.1838 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.11484 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.2073 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.2073 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.12649 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.050897 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.068947 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.07299 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.07299 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.067327 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.059398 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.059398 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.072175 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.07074 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.066422 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.071695 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.071695 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.068543 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.068543 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070015 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.070082 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.072504 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.069312 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.06636 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.070419 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.070419 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.073968 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.069867 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066869 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.066673 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.050796 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.063913 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06571 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066666 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066798 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.067853 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.067136 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065585 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.066213 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065586 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.065363 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.06376 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067086 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067086 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066482 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.065869 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.065869 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.12211 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.066898 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066869 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.067648 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065781 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071516 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.073968 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.067231 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.067231 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.112 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.066205 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.070217 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.091305 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.095803 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.095803 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.093044 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.071055 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.071055 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.081279 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.088335 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.092224 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.058025 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.058025 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.09001 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.09001 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.089232 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.088952 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.081691 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.092117 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.092137 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.070851 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.070851 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.072977 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.089379 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.090795 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.092673 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.070234 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.090613 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.091225 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.091454 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.091449 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.098123 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.090681 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.091365 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.092134 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.091385 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.091263 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.090544 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.093157 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.093157 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.09144 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.091306 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.091306 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22642 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.090783 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.090795 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.091535 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.091354 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.091187 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.072977 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.09179 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.09179 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.091433 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.050897 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.068947 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.067327 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.059398 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.059398 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.072175 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.07074 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.066422 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.071695 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.071695 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.068543 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.068543 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.070015 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.070082 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.072504 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.069312 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.06636 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.070419 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.070419 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.073968 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.069867 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.066869 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.066673 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.050796 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.063913 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06571 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.066666 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066798 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.067853 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.067136 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065585 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.066213 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065586 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.065363 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.06376 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067086 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067086 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066482 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.065869 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.065869 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.12211 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.066898 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.066869 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.067648 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065781 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071516 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.073968 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.067231 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.067231 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.112 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.066205 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.041872 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.057255 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.062663 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.062663 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.054795 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.045783 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.045783 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054668 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.055721 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.05543 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.050785 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.050785 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.055638 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.055638 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.055613 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.055596 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055575 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.055044 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.055492 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.05054 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.05054 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.053033 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.05562 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.055663 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.055002 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.041823 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.055692 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.055694 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.056294 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.056358 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.049502 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.055658 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.055845 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.055267 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.055862 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.055856 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.055686 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.054765 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.054765 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.056218 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.055673 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.055673 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.063092 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.055662 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.055663 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.056753 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.055961 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.059097 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.053033 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.056693 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.056693 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.059901 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.056088 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.078097 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16328 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.093665 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.093665 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.081904 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.064867 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.038917 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.10852 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.10852 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.05624 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.056319 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.060829 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.11228 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.11544 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.11544 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.11062 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052829 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1072 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.077952 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.1399 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.037716 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.16948 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.16948 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.11062 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.077053 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.031445 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.038188 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.037458 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.037458 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.038593 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.037736 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.037736 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.038984 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.038684 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.038343 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.038782 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.038782 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.038491 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.038491 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.038642 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.03865 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.038824 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.038731 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.038321 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.038956 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.038956 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.039429 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.038627 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.038318 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.038472 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.031311 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.037993 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.038193 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.038163 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.038162 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.039484 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.038346 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.038148 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.038356 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.038144 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.03812 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.037977 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.038577 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.038577 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.03816 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.038216 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.038216 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043055 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.038321 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.038318 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.038165 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.038142 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.038046 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.039429 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.038137 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.038137 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.041543 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.03816 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.039222 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.039222 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.039171 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.069246 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.069246 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.036859 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.054358 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.054358 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.05498 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.05498 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.35778 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.047715 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.041793 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.041793 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.050037 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10573 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10573 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054854 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05148 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04866 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074302 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074302 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.05 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.05 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.051067 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.051169 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.053616 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051096 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.048544 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073274 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073274 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059655 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.050945 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.048805 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.049375 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.04694 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.047973 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.047667 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.047656 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072301 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.048996 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.047655 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.04878 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.047628 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.047516 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.046862 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049909 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049909 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.047663 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.048092 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.048092 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04183 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.048826 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.048805 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.047602 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.047611 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.04663 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059655 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.047394 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.047394 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.054693 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.04768 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.055907 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.092126 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.088761 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.088761 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.094367 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.070673 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.070673 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.092554 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.092838 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.093681 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.084862 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.084862 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.093137 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.093137 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.09305 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.093022 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.091979 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.093932 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.093613 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.086472 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.086472 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.092391 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.093065 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.093223 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.094121 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.055713 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.093074 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.093249 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.092846 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.092799 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.090112 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.093213 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.093153 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.093787 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.093143 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.093117 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.09306 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.094419 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.094419 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.092898 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.093287 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.093287 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.081467 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.093222 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.093223 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.092525 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.093064 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.090759 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.092391 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.092609 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.092609 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.083581 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.092992 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.049332 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.11525 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17276 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.060474 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.060474 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.09163 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.098585 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18896 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.07306 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.07306 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.14526 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.14526 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.11429 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.11354 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.073491 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.13029 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18999 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.076324 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.076324 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.08414 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.11724 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18069 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18631 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.049226 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.24818 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.20545 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17677 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.1731 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.083934 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17503 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.2063 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.19566 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20603 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.21155 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.25193 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17792 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17792 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18179 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.20179 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.20179 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18009 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18069 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14943 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.20066 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.037384 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.08414 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.15881 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.15881 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.052623 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18946 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.065187 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.060563 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.060563 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.068633 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.063394 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.065074 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.067953 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.045535 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.045535 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.06566 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.065573 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.062713 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.067285 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.067875 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.048667 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.048667 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061467 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.065743 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.067042 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.068482 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.067707 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.067484 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.06675 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.066653 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.055291 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.066933 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.067426 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.068129 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.067417 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.067432 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.067725 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.068797 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.068797 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.066865 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.067496 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.067496 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.032385 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.067031 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.067042 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.066084 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.067259 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.062794 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061467 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.066345 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.066345 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.038814 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.067059 |  | Single 515378 WWRDEHV9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.035444 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.033017 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.046753 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.044957 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.044957 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.050283 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.044415 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.040958 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.054048 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.054048 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.042155 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.042155 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.044348 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.04444 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.045217 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.048114 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.040436 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.058933 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.058933 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.059758 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.044128 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.039647 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.044245 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.035364 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.034714 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.037776 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.035569 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.035368 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072674 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.040059 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.036673 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.041632 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.036573 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.036216 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.03448 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.046587 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.046587 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.035751 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.038195 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.038195 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.039692 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.039647 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.034239 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.036241 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.059758 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.034057 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.034057 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.036137 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.049332 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.11525 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17276 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.060474 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.060474 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.09163 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.098585 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18896 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.07306 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.07306 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.14526 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.14526 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.11429 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.11354 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.073491 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.13029 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18999 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.076324 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.076324 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.08414 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.11724 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18069 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18631 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.049226 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.24818 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.20545 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17677 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.1731 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.083934 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17503 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.2063 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.19566 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20603 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.21155 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.25193 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17792 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17792 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18179 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.20179 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.20179 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18009 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18069 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14943 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.20066 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.037384 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.08414 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.15881 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.15881 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.052623 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18946 |  | Single 526001 CRWFSHDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059566 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.05714 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.054729 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.054729 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058248 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.071644 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.071644 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.059774 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.05863 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057614 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.063948 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.063948 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.058076 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.058076 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.058494 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.058526 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.059268 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058635 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05756 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.064209 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.064209 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061435 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.058448 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057605 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057947 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.05922 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.056802 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057271 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.057141 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.057136 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.065323 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05768 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.05714 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057664 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057129 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057075 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.056766 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058201 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058201 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.05714 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057326 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057326 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.059605 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057613 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057605 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.05711 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.057118 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056651 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061435 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.057034 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.057034 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.061344 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.057149 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.043973 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.059356 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.064764 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.064764 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.056896 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047884 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047884 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056769 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.057822 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.057531 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.052886 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.052886 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.057739 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.057739 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057714 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057697 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.057676 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.057145 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.057593 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052641 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052641 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.055134 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057721 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.057764 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057103 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.043925 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057793 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057795 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058395 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058459 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.051603 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.057759 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057946 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.057368 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057963 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.057957 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057787 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.056866 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.056866 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058319 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.057774 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.057774 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.065193 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.057763 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.057764 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058854 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058062 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.061198 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.055134 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058795 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058795 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062002 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058189 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12103 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.055428 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.048718 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.048718 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058141 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.11987 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.11987 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.063275 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.059621 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.056567 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.082181 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.082181 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.058008 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.058008 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059183 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059291 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.061873 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.059294 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.056434 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082421 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082421 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.068506 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059049 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.056692 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.057388 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12109 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.05461 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.055772 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.055413 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.055399 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.08464 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.056902 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.055416 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.056705 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.055386 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.055258 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.054522 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058001 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058001 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.055412 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.055908 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.055908 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.048814 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.056715 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.056692 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.055326 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.055362 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.054149 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.068506 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.055101 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.055101 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062713 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.055436 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.097024 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.065492 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.036091 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.047382 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.13293 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080306 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080306 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.056753 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.056233 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.031053 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053039 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.13905 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.05898 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.10689 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.082694 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.045752 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.12261 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.14974 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14688 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.10296 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.15938 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1002 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20888 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20145 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.035704 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067007 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067007 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.15546 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.12393 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.12393 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.10648 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.10689 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.12845 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.1814 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.037079 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.14393 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.14393 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.15972 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.072776 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0772 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.07299 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.08041 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.080243 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.080243 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.085851 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.0823 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.07807 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.090044 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.090044 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080017 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080017 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081726 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081828 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.084392 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.082181 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077872 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.089474 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.089474 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.090936 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.081547 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.07808 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079235 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.072685 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.074662 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.076707 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.076573 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.076592 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.089446 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.078391 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.07626 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078165 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.076226 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.075984 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.074498 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080195 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080195 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.076518 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.076933 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.076933 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15384 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.078113 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.07808 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.076754 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.076245 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.076348 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.090936 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.076407 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.076407 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.11974 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.076469 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.093369 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.057189 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.050312 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.050312 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059788 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.1191 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.1191 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.064614 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.061218 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.058219 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.082975 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.082975 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059631 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059631 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.060793 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.060893 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.063295 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.060942 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.058087 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.091524 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.091524 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.069482 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.060663 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.058323 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059033 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.092398 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.05622 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057412 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.0571 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.057092 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.086286 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.058536 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057058 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.058348 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057063 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.056921 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.056127 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.059647 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.059647 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.057095 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05755 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05755 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.050206 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.058345 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.058323 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.057052 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.057029 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056047 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.069482 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.056825 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.056825 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.064553 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.057107 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.06104 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.058568 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05601 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05601 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059649 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.072713 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.072713 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061181 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.060054 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.059008 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.065322 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.065322 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059485 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059485 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059914 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059946 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.060687 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.060053 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.058953 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.067227 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.067227 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.062817 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059867 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.059 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059343 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.060696 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.058173 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.058659 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058541 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058538 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.066777 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05908 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.058524 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.059056 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.058528 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.058468 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.058134 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.0596 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.0596 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058539 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.058715 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.058715 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.061475 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.059008 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.059 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058523 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058512 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.058117 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.062817 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058443 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058443 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062905 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058544 |  | Single 516106 BOBCAT7 345 539841 G-2011-008-1 345 YY | TDF Impact | Add line 516106 BOBCAT 7 345 539841 G-2011-008-1 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.085627 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.031806 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.031806 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.090914 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.090915 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.15207 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.069335 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.12541 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.12541 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.15498 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.15204 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.073701 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.19894 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.068552 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.15318 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.090345 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.074101 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048399 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.067392 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.068938 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.069833 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.095901 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.061224 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.069998 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.061018 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.059288 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.047039 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.077779 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.077779 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.067755 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.069095 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.069095 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.090917 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.090345 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.075564 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.06267 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.074805 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.067996 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.067996 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.065909 |  | Single 523961 POTTER_CO7 345 525549 TOLK7 345 1 | TDF Impact | Add line 523961 POTTER_CO 7 345 525549 TOLK 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14447 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14447 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14447 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17454 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17454 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17454 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.082882 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.082882 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.082882 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.082882 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.082882 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.082882 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22116 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22116 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22116 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.19995 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.19995 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.19995 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.19995 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.19995 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.19995 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24347 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24347 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24347 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21824 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21824 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21824 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.19809 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.19809 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.19809 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.25877 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.25877 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.25877 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.25877 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.25877 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.25877 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20565 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20565 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20565 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20565 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20565 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20565 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21631 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21631 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21631 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21685 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21685 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21685 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22648 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22648 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22648 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.2277 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.2277 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.2277 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19602 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19602 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19602 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.25443 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.25443 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.25443 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.25443 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.25443 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.25443 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.28255 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.28255 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.28255 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21522 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21522 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21522 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19345 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19345 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19345 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21076 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21076 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21076 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14398 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14398 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14398 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.16933 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.16933 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.16933 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18452 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18452 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18452 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17871 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17871 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17871 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17827 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17827 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17827 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.29905 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.29905 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.29905 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19548 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19548 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19548 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18027 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18027 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18027 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20004 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20004 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20004 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18044 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18044 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18044 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.17844 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.17844 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.17844 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.16809 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.16809 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.16809 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22036 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22036 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22036 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22036 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22036 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22036 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.17895 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.17895 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.17895 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18642 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18642 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18642 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18642 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18642 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18642 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10026 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10026 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10026 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19366 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19366 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19366 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19345 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19345 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19345 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17609 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17609 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17609 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.17932 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.17932 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.17932 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15299 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15299 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15299 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.28255 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.28255 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.28255 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17471 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17471 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17471 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17471 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17471 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17471 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.21777 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.21777 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.21777 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.17974 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.17974 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.17974 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.1538 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.1538 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.1538 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28961 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28961 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28961 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.32524 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.32524 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.32524 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.32524 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.32524 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.32524 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.27324 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.27324 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.27324 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17722 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17722 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17722 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17722 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17722 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17722 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.25004 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.25004 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.25004 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.26652 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.26652 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.26652 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.28396 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.28396 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.28396 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20339 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20339 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20339 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20339 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20339 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20339 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.27611 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.27611 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.27611 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.27611 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.27611 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.27611 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26888 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26888 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26888 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26842 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26842 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26842 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25721 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25721 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25721 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.26647 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.26647 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.26647 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.28488 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.28488 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.28488 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19891 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19891 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19891 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19891 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19891 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19891 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22619 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22619 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22619 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26965 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26965 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26965 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.28432 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.28432 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.28432 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27845 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27845 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27845 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.15357 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.15357 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.15357 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29892 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29892 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29892 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.29013 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.29013 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.29013 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.29131 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.29131 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.29131 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.29128 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.29128 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.29128 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20421 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20421 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20421 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.28297 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.28297 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.28297 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.29226 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.29226 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.29226 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.28336 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.28336 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.28336 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.29217 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.29217 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.29217 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.29327 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.29327 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.29327 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29964 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29964 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29964 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.27406 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.27406 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.27406 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.27406 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.27406 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.27406 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.29144 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.29144 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.29144 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28913 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28913 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28913 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28913 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28913 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28913 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22064 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22064 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.22064 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.28418 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.28418 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.28418 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.28432 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.28432 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.28432 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.29099 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.29099 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.29099 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.29231 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.29231 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.29231 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29502 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29502 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29502 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22619 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22619 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22619 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.29242 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.29242 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.29242 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.29242 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.29242 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.29242 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18223 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18223 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18223 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.29153 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.29153 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.29153 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058905 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.096666 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.094079 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.094079 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.098354 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.074815 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.074815 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.09676 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.097084 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.097861 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.088687 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.088687 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.09737 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.09737 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.097262 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.097237 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.096349 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.09795 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.09781 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.086711 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.086711 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.096524 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.097279 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.097481 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.098183 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058706 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.097427 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.097531 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.097225 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.097185 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.092913 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.097466 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.097471 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.097936 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.097474 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.097452 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.097418 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.098403 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.098403 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.097262 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.097558 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.097558 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.084369 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.09748 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.097481 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.096976 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.097401 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.095637 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.096524 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.097059 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.097059 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.087218 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.097336 |  | P12:345:WERE:VIOL-WICH-345:EHV: | TDF Impact | Add line 532796 WICHITA7 345 532798 VIOLA 7 345 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.22614 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.22614 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.22614 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24476 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24476 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24476 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24476 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24476 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24476 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.2176 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.2176 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.2176 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16532 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16532 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16532 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16532 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16532 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16532 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20681 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20681 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20681 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21483 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21483 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21483 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.22285 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.22285 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.22285 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.18257 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.18257 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.18257 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.18257 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.18257 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.18257 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.21928 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.21928 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.21928 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.21928 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.21928 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.21928 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21589 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21589 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21589 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21567 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21567 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21567 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.21047 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.21047 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.21047 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21455 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21455 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21455 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.2233 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.2233 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.2233 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17916 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19511 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19511 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19511 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21625 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21625 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21625 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.22312 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.22312 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.22312 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.22012 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.22012 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.22012 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14898 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14898 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14898 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.22997 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.22997 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.22997 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22585 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22585 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22585 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.2266 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.2266 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.2266 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22661 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22661 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22661 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18212 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18212 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18212 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.22249 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.22249 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.22249 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22689 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22689 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22689 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.22251 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.22251 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.22251 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22685 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22685 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22685 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22737 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22737 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22737 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.23031 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.23031 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.23031 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21797 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21797 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21797 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21797 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21797 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21797 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22664 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22664 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22664 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.22537 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.22537 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.22537 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.22537 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.22537 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.22537 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.20749 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.20749 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.20749 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.22306 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.22306 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.22306 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.22312 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.22312 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.22312 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22661 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22661 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22661 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22696 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22696 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22696 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.22929 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.22929 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.22929 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19511 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19511 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19511 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22725 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22725 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22725 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22725 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22725 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22725 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18291 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18291 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18291 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22664 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22664 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22664 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.24855 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.24855 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.35863 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.34137 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.3537 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.11623 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.033112 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.13684 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.034683 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.034683 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.11834 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.11623 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.07494 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.077308 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06893 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06893 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.081077 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.083017 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.083017 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.08727 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.083153 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.078411 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.092734 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.092734 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080598 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080598 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.082513 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.082631 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.085559 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.083039 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.078186 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.089999 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.089999 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.093168 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.082311 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.078423 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079754 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.074844 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.074614 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.07689 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.076685 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.076707 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.09175 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.078778 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.076355 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078543 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.076379 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.076094 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.074428 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080839 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080839 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.076638 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.077145 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.077145 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.16375 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.07846 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.078423 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.076851 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.076365 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.076212 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.093168 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.076456 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.076456 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.1223 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.076591 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.031216 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17454 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.077248 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.041556 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.041556 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.11862 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.14448 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.08221 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.057548 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.057548 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.11411 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.11411 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13236 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13225 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.15319 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.10935 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.083032 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052149 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052149 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.078012 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.13078 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.092995 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.073799 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.031115 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050813 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.07858 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.11205 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.11638 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.041716 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.096411 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.081189 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.074306 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.082153 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.078495 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048193 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.073345 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.073345 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.10752 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.080455 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.080455 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.09335 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.092995 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14106 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.088524 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.26996 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.078012 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.13281 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.13281 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.042697 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.099166 |  | Single 525832 TUCO_INT7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.040759 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.071086 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.071086 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.033178 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.03363 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.033883 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.038064 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.035695 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.038072 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.038297 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.033467 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.036792 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.036805 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.037094 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.038237 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.037882 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.035355 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.035355 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.61785 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.033839 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.033883 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.039533 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.037218 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048444 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.039721 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.039721 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.037461 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058154 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0318 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.032574 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047761 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047761 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.033966 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.032978 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.032109 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.03977 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.03977 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.032516 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.032516 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.032855 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.032884 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.033581 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.032904 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.03207 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041283 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041283 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.035378 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.032817 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.032134 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.032351 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058304 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.031515 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.031868 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.031776 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.031773 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.038966 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.032196 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.031764 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.032147 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.031766 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.031723 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.031488 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.032534 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.032534 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.031774 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.031909 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.031909 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.030525 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.032141 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.032134 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.031761 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.031755 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.031462 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.035378 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.031695 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.031695 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.034272 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.031778 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.064094 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.069361 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.069361 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.06179 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.06412 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.064101 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.061784 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.052074 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.052074 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.063014 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.063014 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.063704 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.063724 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06482 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.063035 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061798 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.043081 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.043081 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.063835 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.063637 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.062225 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.061624 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.060904 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.061696 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.062484 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.062594 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.047635 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.062352 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.061704 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.061608 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.061723 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.061626 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.060833 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.061638 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.061638 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.06237 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.061753 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.061753 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.18657 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.062238 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.062225 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.063209 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.061886 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.066347 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.063835 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.062945 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.062945 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.11536 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.06216 |  | P12:345:OKGE:BKRBKR4890:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.063472 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.075604 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.075604 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.057968 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.053067 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.057347 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.060807 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.046024 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.046024 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059332 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059332 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057761 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057652 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055315 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.056751 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061057 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.044734 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.044734 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.04908 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.05793 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.061114 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.05927 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.064312 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.062389 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.063103 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.06315 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.045433 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.060821 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.062958 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.060557 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.062944 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.063187 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.064466 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058116 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058116 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.063081 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.062153 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.062153 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.0708 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.061083 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.061114 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.063388 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.063064 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.06606 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.04908 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.063633 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.063633 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.052262 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.062997 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.13345 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18566 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.1761 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.1761 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.19104 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.15743 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.15743 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.18937 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.18859 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18908 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.17871 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.17871 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.18883 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.18881 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18775 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.19059 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18889 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17632 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17632 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19106 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.1888 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18819 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19026 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.13317 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.18705 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18788 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18699 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18689 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18797 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.18825 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18757 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.18933 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18758 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18745 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18698 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.1911 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.1911 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18708 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18801 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18801 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15506 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.1882 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18819 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18636 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18738 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.18261 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19106 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.18645 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.18645 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.16635 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18726 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.036005 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.037633 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.049443 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047224 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047224 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054062 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.048246 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.04414 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.056609 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.056609 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.045716 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.045716 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.047997 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.048103 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.049572 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051093 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.043667 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.058208 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.058208 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.063427 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.047766 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.043105 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.047094 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.035918 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.038149 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.041195 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.039405 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.039246 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072205 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.043539 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.040175 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.044698 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.040196 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.039801 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.037908 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.049242 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.049242 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.039521 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.041597 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.041597 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.043151 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.043105 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.038422 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.039863 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.031314 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.063427 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.038192 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.038192 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.039811 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.036091 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.037724 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.049562 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047338 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047338 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.054192 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.048362 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.044246 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.056746 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.056746 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.045827 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.045827 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.048113 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.048219 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.049692 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.051216 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.043772 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.058349 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.058349 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.063579 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.047881 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.043209 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.047208 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.036005 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.038241 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.041295 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.0395 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.039341 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.072379 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.043644 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.040272 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.044806 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.040293 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.039896 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.038 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.04936 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.04936 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.039617 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.041697 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.041697 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.043255 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.043209 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.038515 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.039959 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.031389 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.063579 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.038284 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.038284 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.039907 |  | Single 516059 BECKHAM7 345 523961 POTTER_CO7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.072109 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.054694 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.054694 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.082241 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.080225 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.079045 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.07776 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.030813 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.030813 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.077928 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.077928 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.079303 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.079256 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.076986 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.083088 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077354 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.083217 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.079195 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.076305 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.080263 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.072492 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.075052 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.073688 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.073554 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.22867 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.076581 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.074315 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078171 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.074352 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.073997 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.072281 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.082138 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.082138 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.073784 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.075393 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.075393 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.0472 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.076335 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.076305 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.072897 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.074058 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.066966 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.083217 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.072851 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.072851 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.058716 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.074023 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058154 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0318 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.032574 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047761 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047761 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.033966 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.032978 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.032109 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.03977 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.03977 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.032516 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.032516 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.032855 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.032884 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.033581 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.032904 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.03207 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041283 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041283 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.035378 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.032817 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.032134 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.032351 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058304 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.031515 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.031868 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.031776 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.031773 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.038966 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.032196 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.031764 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.032147 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.031766 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.031723 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.031488 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.032534 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.032534 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.031774 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.031909 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.031909 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.030525 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.032141 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.032134 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.031761 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.031755 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.031462 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.035378 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.031695 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.031695 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.034272 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.031778 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.13345 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18566 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.1761 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.1761 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.19104 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.15743 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.15743 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.18937 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.18859 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18908 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.17871 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.17871 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18854 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18854 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.18883 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.18881 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18775 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.19059 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18889 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17632 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17632 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19106 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.1888 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18819 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19026 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.13317 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.18705 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18788 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18699 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18689 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.18797 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.18825 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18757 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.18933 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18758 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18745 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18698 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.1911 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.1911 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18708 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18801 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18801 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15506 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.1882 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18819 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18636 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18738 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.18261 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19106 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.18645 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.18645 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.16635 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18726 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.045218 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.055015 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05451 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05451 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.055385 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053213 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053213 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061164 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.058515 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.053746 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.064052 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.064052 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.056046 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.056046 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057775 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057869 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06071 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.05747 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.053617 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.060474 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.060474 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064728 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057596 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.054079 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.054442 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.045124 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050632 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.052712 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.053265 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.053372 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.060313 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.054399 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.052397 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.053674 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.05243 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.05217 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.050456 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.055131 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.055131 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.053139 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.052917 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.052917 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.11781 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.054112 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.054079 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.053985 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.052558 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056297 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064728 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.053527 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.053527 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.10426 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.052931 |  | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.041652 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.05381 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.057702 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.057702 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052169 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.045333 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.045333 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.052277 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052893 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.052547 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.049636 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.049636 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052765 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052765 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052799 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05279 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.05287 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052402 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.052585 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.04842 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.04842 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.051287 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052798 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.052724 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.052282 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.041607 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.052643 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.052705 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.053123 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.053173 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.048474 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05273 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.052792 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.052441 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.052799 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.052791 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.052635 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052141 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052141 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.053074 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.052697 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.052697 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.061668 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.052725 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.052724 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.053452 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.052879 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.055076 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.051287 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.053388 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.053388 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.059074 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.052979 |  | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.045218 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.055015 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05451 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05451 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.055385 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053213 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053213 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061164 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.058515 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.053746 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.064052 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.064052 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.056046 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.056046 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057775 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057869 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06071 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.05747 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.053617 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.060474 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.060474 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064728 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057596 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.054079 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.054442 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.045124 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050632 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.052712 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.053265 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.053372 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.060313 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.054399 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.052397 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.053674 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.05243 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.05217 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.050456 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.055131 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.055131 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.053139 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.052917 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.052917 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.11781 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.054112 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.054079 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.053985 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.052558 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056297 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064728 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.053527 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.053527 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.10426 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.052931 |  | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.059356 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.58794 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.58794 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058337 |  | Single 523267 PRINGLE6 230 523979 HARRNG_EST6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.07494 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.077308 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06893 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06893 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.081077 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.083017 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.083017 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.08727 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.083153 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.078411 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.092734 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.092734 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080598 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080598 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.082513 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.082631 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.085559 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.083039 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.078186 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.089999 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.089999 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.093168 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.082311 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.078423 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079754 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.074844 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.074614 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.07689 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.076685 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.076707 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.09175 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.078778 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.076355 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078543 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.076379 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.076094 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.074428 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080839 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080839 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.076638 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.077145 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.077145 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.16375 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.07846 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.078423 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.076851 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.076365 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.076212 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.093168 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.076456 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.076456 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.1223 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.076591 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.03289 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.066368 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.084275 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.084275 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059063 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.037817 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.037817 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055694 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.060273 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.061509 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.043313 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.043313 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.0611 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.0611 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.060296 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.060191 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.058587 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058904 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061734 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.042438 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.042438 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.048969 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.060396 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.061996 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.06002 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.032842 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.063386 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06265 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.064235 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.064401 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.043366 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.061848 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.063204 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.061065 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.063223 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.063309 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.063432 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.059082 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.059082 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.064083 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.062515 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.062515 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.05326 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.06198 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.061996 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.065326 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.063506 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071309 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.048969 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.0653 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.0653 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.03448 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.063768 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058154 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0318 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.032574 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047761 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047761 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.033966 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.032978 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.032109 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.03977 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.03977 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.032516 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.032516 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.032855 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.032884 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.033581 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.032904 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.03207 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041283 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041283 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.035378 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.032817 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.032134 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.032351 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058304 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.031515 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.031868 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.031776 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.031773 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.038966 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.032196 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.031764 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.032147 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.031766 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.031723 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.031488 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.032534 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.032534 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.031774 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.031909 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.031909 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.030525 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.032141 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.032134 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.031761 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.031755 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.031462 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.035378 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.031695 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.031695 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.034272 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.031778 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.078387 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.15998 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.096368 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.096368 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.082829 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.064059 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.034948 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.11172 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.11172 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.054971 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.055122 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06192 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.11007 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.11333 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.11333 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.11397 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.051478 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.10379 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.078232 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.13708 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.034324 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.16605 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.16605 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.11397 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.084176 |  | Single 527669 CROSSROADS9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.07494 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.077308 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06893 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06893 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.081077 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.083017 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.083017 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.08727 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.083153 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.078411 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.092734 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.092734 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080598 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080598 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.082513 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.082631 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.085559 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.083039 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.078186 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.089999 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.089999 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.093168 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.082311 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.078423 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.079754 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.074844 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.074614 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.07689 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.076685 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.076707 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.09175 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.078778 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.076355 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078543 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.076379 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.076094 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.074428 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.080839 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.080839 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.076638 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.077145 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.077145 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.16375 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.07846 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.078423 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.076851 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.076365 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.076212 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.093168 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.076456 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.076456 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.1223 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.076591 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.078275 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.042813 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.031702 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.031702 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.093002 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.11196 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.03313 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.045168 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.045168 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.075855 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.075855 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.098615 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.098782 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.13291 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.077085 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.032618 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.040126 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.040126 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061084 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.096556 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.049712 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.036278 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.032552 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.040694 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.043265 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.053861 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.033636 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.038646 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.038646 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.038971 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.033891 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.033891 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05014 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.049712 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.048419 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.030844 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.2481 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061084 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.030159 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.030159 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.033915 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.035372 |  | Single 525832 TUCO_INT7 345 525830 TUCO_INT6 230 525825 'TUCO_TR2 1' 13 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.031216 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17454 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.077248 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.041556 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.041556 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.11862 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.14448 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.08221 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.057548 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.057548 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.11411 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.11411 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13236 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13225 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.15319 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.10935 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.083032 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052149 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052149 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.078012 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.13078 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.092996 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.073799 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.031115 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050813 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.07858 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.11205 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.11638 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.041716 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.096411 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.081189 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.074306 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.082153 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.078495 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048193 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.073345 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.073345 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.10752 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.080455 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.080455 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.09335 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.092996 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14106 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.088524 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.26996 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.078012 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.13281 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.13281 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.042697 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.099166 |  | Single 525832 TUCO_INT7 345 526000 CRWFSHDRW7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.057189 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.050312 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.050312 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059788 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.1191 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.1191 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.064614 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.061218 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.058219 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.082975 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.082975 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059631 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059631 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.060793 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.060893 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.063295 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.060942 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.058087 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.091524 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.091524 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.069482 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.060663 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.058323 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059033 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.05622 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.057412 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.0571 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.057092 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.086286 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.058536 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.057058 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.058348 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.057063 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.056921 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.056127 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.059647 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.059647 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.057095 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05755 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05755 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.050206 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.058345 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.058323 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.057052 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.057029 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056047 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.069482 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.056825 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.056825 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.064553 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.057107 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.50967 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.50967 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.038923 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.031111 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.035842 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.035842 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.030194 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.037332 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19737 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19737 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.049934 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.049934 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.041802 |  | Single 523095 HITCHLAND6 230 778320 G24-045-TAP 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.039837 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.042163 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.040734 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.040734 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.042836 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.044954 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.044954 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.043527 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.042983 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.042444 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.044411 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.044411 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.04268 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.04268 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.042916 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.04293 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.043249 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.043045 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.04241 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.044679 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.044679 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.044335 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.042891 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.042411 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.04265 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.039716 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.041923 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.042219 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.042153 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.04215 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.045174 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.042455 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.042143 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.042471 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.042146 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.042108 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.041899 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.042811 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.042811 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.042151 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.042254 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.042254 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.04717 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.042416 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.042411 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.042142 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.042135 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.041894 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.044335 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.0421 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.0421 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.044956 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.042155 |  | P42:345:OKGE:SB_DGSE7385:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.096221 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.072899 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.040705 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053187 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.12211 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.11991 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.11991 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.072254 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.071592 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.03485 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.059608 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.12653 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.076652 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.17325 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.12111 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.19961 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.16027 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.15547 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.16587 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.21586 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.17309 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.15064 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.14492 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.074515 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.074515 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.16288 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2096 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2096 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.17254 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.17325 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.12891 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.16582 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040081 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.12936 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.12936 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.17382 |  | P42:345:SPS:KIOWA-J20-4R45:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.035842 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.27695 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.083536 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.057069 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.057069 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.076553 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081206 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.050408 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.042631 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.64956 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.073535 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.036324 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.039575 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.036657 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.036324 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.036034 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.64956 |  | Single 523959 POTTER_CO6 230 524267 BUSHLAND6 230 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.17439 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.031216 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.1439 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.1439 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.040057 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.034 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.079047 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.079047 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.031227 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.031227 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.033224 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.033407 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.037871 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.033252 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.092495 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.092495 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.048653 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.032996 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.17438 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.07699 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.030969 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.030969 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.048653 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.038964 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.069066 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.071369 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.066505 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.068308 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.0711 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.047837 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.047837 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.06955 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.06955 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.068832 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.068749 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.066171 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.070063 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.071061 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.043413 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.043413 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064371 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.068919 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.070345 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.071378 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.071233 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.070848 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.070313 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.07023 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.055569 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.070221 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.070873 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.071211 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.070874 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.070904 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.071263 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.071528 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.071528 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.070396 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.070833 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.070833 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.031373 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.070333 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.070345 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.069789 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.070735 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.067365 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064371 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.070055 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.070055 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.040669 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.070552 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.06104 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.058568 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05601 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05601 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059649 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.072713 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.072713 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061181 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.060054 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.059008 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.065322 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.065322 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059485 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059485 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059914 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059946 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.060687 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.060053 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.058953 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.067227 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.067227 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.062817 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059867 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.059 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059343 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.060696 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.058173 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.058659 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058541 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058538 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.066777 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05908 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.058524 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.059056 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.058528 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.058468 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.058134 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.0596 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.0596 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058539 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.058715 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.058715 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.061475 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.059008 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.059 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058523 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058512 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.058117 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.062817 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058443 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058443 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062905 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058544 |  | Single 539840 GEN-2011-008 345 539841 G-2011-008-1 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.063479 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.080478 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.080478 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.057968 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061164 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.058515 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.061113 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.064052 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.064052 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059332 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059332 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057775 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057869 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06071 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.05747 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061579 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.060474 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.060474 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064728 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.05793 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.061198 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.05927 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.068951 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.064283 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.064707 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.064666 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.060313 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.060821 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.065368 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.060844 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.065316 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.065904 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.069333 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058116 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058116 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.064801 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.06376 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.06376 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.11781 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.061124 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.061198 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.064383 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.065352 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.06606 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064728 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.065169 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.065169 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.10426 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.064894 |  | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.049298 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.11678 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17228 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.061781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.061781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.093191 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.10002 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18882 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074327 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074327 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.14552 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.14552 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.11529 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.11457 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.075722 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.13069 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18988 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073802 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073802 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.085792 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.11817 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18023 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18559 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.049188 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.24662 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.20436 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17639 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17242 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.082944 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17458 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.20609 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1948 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20502 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.21051 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.25039 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17733 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17733 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18074 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2007 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2007 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.17964 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18023 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14959 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.19957 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.041197 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.085792 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.15971 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.15971 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.056498 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18844 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.072109 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.054694 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.054694 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.082241 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.080225 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.079045 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.07776 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.030813 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.030813 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.077928 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.077928 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.079303 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.079256 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.076986 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.083088 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077354 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.083217 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.079195 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.076305 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.080263 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.072492 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.075052 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.073688 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.073554 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.22867 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.076581 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.074315 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.078171 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.074352 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.073997 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.072281 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.082138 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.082138 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.073784 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.075393 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.075393 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.0472 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.076335 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.076305 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.072897 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.074058 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.066966 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.083217 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.072851 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.072851 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.058716 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.074023 |  | Single 523097 HITCHLAND7 345 784950 G24-266_TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.09782 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.068531 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.038953 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.050843 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.13457 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.12285 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.12285 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.071384 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.070731 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.03322 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.056559 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.14075 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.076117 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18313 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.11416 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.46219 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.23262 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.15073 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14622 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17251 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.19826 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.16343 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20753 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20027 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.39769 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.069987 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.069987 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.15301 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.21565 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.21565 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18199 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18313 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.12712 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.17946 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.039677 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.14571 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.14571 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.16312 |  | P12:345:SPS:J27_J28::1_RDRND_PHTM_CHINA:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.049298 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.11678 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17228 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.061781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.061781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.093191 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.10002 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18882 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074327 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074327 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.14552 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.14552 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.11529 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.11457 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.075722 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.13069 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.18988 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.073802 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.073802 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.085792 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.11817 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18023 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18559 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.049188 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.24662 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.20436 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17639 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17242 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.082944 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17458 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.20609 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1948 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20502 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.21051 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.25039 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17733 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17733 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18074 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2007 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2007 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.17964 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18023 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14959 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.19957 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.041197 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.085792 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.15971 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.15971 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.056498 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18844 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.031653 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.038764 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.037963 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.037963 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.039158 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.038173 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.038173 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.039597 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.039273 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.038907 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.039378 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.039378 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.039069 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.039069 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.039227 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.039235 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.039437 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.039305 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.038885 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.039224 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.039224 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.040072 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.03921 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.038888 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.039036 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.031517 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.038558 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.03876 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.038732 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.038732 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.039961 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.038918 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.038712 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.038921 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.038714 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.038689 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.038541 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.03914 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.03914 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.038729 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.038783 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.038783 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044382 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.038892 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.038888 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.038737 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.03871 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.038632 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.040072 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.038707 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.038707 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.042375 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.038728 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.181 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.062565 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.037535 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.048534 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.093284 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.065339 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.065339 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052952 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052372 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053164 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.096027 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.054208 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.079244 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.069702 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.064468 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.087264 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.13671 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.13987 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.077166 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.10195 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.076389 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.10521 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.1001 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.061621 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.063708 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.063708 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.13136 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.088139 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.088139 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.079035 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.079244 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17815 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.11082 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.20087 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.20087 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.12238 |  | Single 525832 TUCO_INT7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.045218 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.055015 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05451 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05451 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.055385 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053213 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053213 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061164 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.058515 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.053746 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.064052 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.064052 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.056046 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.056046 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057775 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057869 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06071 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.05747 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.053617 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.060474 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.060474 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064728 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057596 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.054079 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.054442 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.045124 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050632 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.052712 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.053265 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.053372 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.060313 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.054399 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.052397 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.053674 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.05243 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.05217 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.050456 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.055131 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.055131 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.053139 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.052917 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.052917 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.11781 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.054112 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.054079 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.053985 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.052558 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056297 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064728 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.053527 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.053527 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.10426 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.052931 |  | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.09782 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.066368 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.036702 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.048456 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.13457 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.080508 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.080508 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057571 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057045 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.032123 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053998 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.14075 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059745 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.10647 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.083206 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.045265 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.12177 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.14734 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.14465 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.10257 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.16031 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.10031 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20753 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20027 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.034884 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.067872 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.067872 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.15294 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.123 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.123 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.10608 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.10647 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.12712 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.17946 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.039677 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.14571 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.14571 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.15717 |  | Single 528015 PHANTOM7 345 528027 RDRUNNER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058905 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.096666 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.094079 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.094079 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.098354 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.074815 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.074815 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.09676 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.097084 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.097861 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.088687 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.088687 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.09737 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.09737 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.097262 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.097237 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.096349 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.09795 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.09781 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.086711 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.086711 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.096524 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.097279 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.097481 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.098183 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058706 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.097427 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.097531 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.097225 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.097185 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.092913 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.097466 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.097471 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.097936 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.097474 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.097452 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.097418 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.098403 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.098403 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.097262 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.097558 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.097558 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.084369 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.09748 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.097481 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.096976 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.097401 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.095637 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.096524 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.097059 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.097059 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.087218 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.097336 |  | P23:345:WERE:WICH-345-116:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.12203 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.049276 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.043213 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.043213 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.051509 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10503 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10503 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055987 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.052878 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.050136 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074915 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074915 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.051434 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.051434 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052483 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052576 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.054826 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.052559 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.05002 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.081103 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.081103 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.060415 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.052364 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.050255 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.050845 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1221 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.048379 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.049436 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.04917 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.049164 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.073793 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.050446 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.049122 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.050247 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.049125 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048297 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.051381 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.051381 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.049163 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.049557 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.049557 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.043071 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.050275 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.050255 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.049137 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.049098 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048305 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.060415 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.048929 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.048929 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.05631 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.049171 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.181 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.062565 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.037535 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.048534 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.093284 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.065339 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.065339 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.052952 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.052372 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053164 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.096027 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.054208 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.079244 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.069702 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.064468 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.087264 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.13671 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.13987 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.077166 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.10195 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.076389 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.10521 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.1001 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.061621 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.063708 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.063708 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.13136 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.088139 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.088139 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.079035 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.079244 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17815 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.11082 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.20087 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.20087 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.12238 |  | Single 526936 YOAKUM7 345 764945 G20-067-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.03289 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.066368 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.084275 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.084275 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059063 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.037817 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.037817 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055694 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.060273 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.061509 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.043313 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.043313 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.0611 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.0611 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.060296 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.060191 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.058587 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058904 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061734 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.042438 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.042438 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.048969 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.060396 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.061996 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.06002 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.032842 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.063386 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.06265 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.064235 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.064401 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.043366 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.061848 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.063204 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.061065 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.063223 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.063309 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.063432 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.059082 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.059082 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.064083 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.062515 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.062515 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.05326 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.06198 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.061996 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.065326 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.063506 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.071309 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.048969 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.0653 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.0653 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.03448 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.063768 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.069066 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06632 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.071369 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.066505 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.068308 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.0711 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.047837 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.047837 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.06955 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.06955 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.068832 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.068749 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.066171 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.070063 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.071061 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.043413 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.043413 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064371 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.068919 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.070345 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.071378 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.071233 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.070848 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.070313 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.07023 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.055569 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.070221 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.070873 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.071211 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.070874 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.070904 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.071263 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.071528 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.071528 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.070396 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.070833 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.070833 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.031373 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.070333 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.070345 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.069789 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.070735 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.067365 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064371 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.070055 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.070055 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.040669 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.070552 |  | Single 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.057049 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.032951 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.03108 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.03108 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.033674 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047253 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047253 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.034936 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.034034 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.033244 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.040173 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.040173 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.033613 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.033613 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.033923 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.033949 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.03458 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.033973 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.033207 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041504 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041504 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.036227 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.033888 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.033263 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.033468 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.057196 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.032694 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.033019 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.032932 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.03293 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.039426 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.03332 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.032923 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.033279 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.032925 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.032886 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.032668 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.033638 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.033638 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.032931 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.033057 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.033057 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.031818 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.033269 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.033263 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.032917 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.032914 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.032634 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.036227 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.032857 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.032857 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.035202 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.032935 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.057049 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.032951 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.03108 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.03108 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.033674 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047253 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047253 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.034936 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.034034 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.033244 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.040173 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.040173 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.033613 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.033613 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.033923 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.033949 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.03458 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.033973 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.033207 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041504 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041504 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.036227 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.033888 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.033263 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.033468 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.057196 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.032694 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.033019 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.032932 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.03293 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.039426 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.03332 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.032923 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.033279 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.032925 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.032886 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.032668 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.033638 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.033638 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.032931 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.033057 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.033057 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.031818 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.033269 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.033263 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.032917 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.032914 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.032634 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.036227 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.032857 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.032857 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.035202 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.032935 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.072634 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.088673 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.090089 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.090089 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.091341 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.07507 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.07507 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.083117 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.087751 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.089999 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.062717 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.062717 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.088599 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.088599 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.088362 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.088159 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.082854 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.090941 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.08987 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.075312 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.075312 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.078375 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.088439 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.088789 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.090725 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.072647 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.087851 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.088818 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.088844 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.088833 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.098635 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.088769 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.088789 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.089984 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.088836 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.088669 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.087756 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.09139 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.09139 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.088839 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.088941 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.088941 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.24109 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.088787 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.088789 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.088859 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.08877 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.087975 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.078375 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.089004 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.089004 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.088847 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.058154 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0318 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.032574 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.047761 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.047761 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.033966 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.032978 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.032109 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.03977 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.03977 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.032516 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.032516 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.032855 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.032884 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.033581 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.032904 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.03207 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041283 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041283 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.035378 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.032817 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.032134 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.032351 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.058304 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.031515 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.031868 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.031776 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.031773 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.038966 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.032196 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.031764 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.032147 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.031766 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.031723 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.031488 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.032534 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.032534 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.031774 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.031909 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.031909 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.030525 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.032141 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.032134 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.031761 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.031755 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.031462 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.035378 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.031695 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.031695 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.034272 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.031778 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.06104 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.058568 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05601 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05601 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.059649 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.072713 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.072713 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061181 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.060054 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.059008 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.065322 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.065322 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.059485 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.059485 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059914 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059946 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.060687 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.060053 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.058953 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.067227 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.067227 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.062817 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059867 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.059 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059343 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.060696 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.058173 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.058659 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.058541 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058538 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.066777 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.05908 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.058524 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.059056 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.058528 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.058468 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.058134 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.0596 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.0596 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058539 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.058715 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.058715 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.061475 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.059008 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.059 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058523 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058512 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.058117 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.062817 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.058443 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.058443 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.062905 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058544 |  | Single 539800 CLARKCOUNTY7 345 539840 GEN-2011-008 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.045218 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.055015 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.05451 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.05451 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.055385 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.053213 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.053213 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.061164 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.058515 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.053746 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.064052 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.064052 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.056046 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.056046 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.057775 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.057869 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.06071 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.05747 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.053617 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.060474 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.060474 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.064728 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.057596 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.054079 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.054442 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.045124 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050632 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.052712 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.053265 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.053372 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.060313 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.054399 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.052397 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.053674 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.05243 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.05217 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.050456 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.055131 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.055131 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.053139 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.052917 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.052917 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.11781 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.054112 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.054079 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.053985 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.052558 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.056297 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.064728 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.053527 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.053527 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.10426 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.052931 |  | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.031216 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17454 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.87478 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.87478 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.077248 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.041556 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.041556 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.11862 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.14448 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.08221 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.057548 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.057548 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.11411 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.11411 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13236 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13225 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.15319 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.10935 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.083032 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.052149 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.052149 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.078012 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.13078 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.092995 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.073799 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.031115 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.050813 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.07858 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.11205 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.11638 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.041716 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.096411 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.081189 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.074306 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.082153 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.078495 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.048193 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.073345 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.073345 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.10752 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.080455 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.080455 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.09335 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.092995 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.14106 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.088524 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.26996 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.078012 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.13281 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.13281 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.042697 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.099166 |  | Single 526000 CRWFSHDRW7 345 778200 G24-041-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.58794 |  | MULTIGEN523979 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.58794 |  | MULTIGEN523979 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.041182 |  | MULTIGEN523979 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.1971 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.12796 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.12796 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.33433 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.11124 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.314 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18916 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18916 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13739 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13415 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.030176 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18686 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.31045 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.14287 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.24731 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.33602 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29253 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.28288 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.2606 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.25653 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.23835 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.28718 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.31789 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.28818 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.28742 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29287 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.35227 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.35227 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.26464 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28348 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28348 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.032215 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.2464 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.24731 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.23518 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.28032 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.13029 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.25301 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.25301 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.27226 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.094503 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.058287 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.051406 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.051406 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.060888 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.12023 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.12023 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.065716 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.062318 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.059319 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.084052 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.084052 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.060731 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.060731 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.061893 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.061993 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.064396 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.062042 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.059186 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.092635 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.092635 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.070585 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.061763 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.059424 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.060133 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.093536 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057318 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.058511 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.0582 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058192 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.087396 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.059634 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.058157 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.059447 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.058162 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.058019 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057225 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.060747 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.060747 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058194 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.058649 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.058649 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.051302 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.059446 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.059424 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058151 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058127 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.057139 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.070585 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.057923 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.057923 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.065666 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058206 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | Add line 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.032757 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.41011 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.41011 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13914 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13795 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.16343 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.6722 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14657 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14657 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14657 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17665 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17665 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.17665 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.084986 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.084986 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.084986 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.084986 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.084986 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.084986 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22327 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22327 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.22327 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.20205 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.20205 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.20205 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.20205 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.20205 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.20205 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.22034 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.22034 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.22034 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.20021 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.20021 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.20021 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.26097 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.26097 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.26097 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.26097 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.26097 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.26097 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20776 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20776 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.20776 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20776 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20776 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.20776 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21842 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21842 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21842 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21896 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21896 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21896 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22858 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22858 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.22858 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.22981 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.22981 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.22981 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19815 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19815 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19815 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.25654 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.25654 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.25654 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.25654 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.25654 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.25654 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.28467 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.28467 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.28467 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21733 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21733 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21733 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21288 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21288 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21288 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14608 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14608 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14608 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.17145 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.17145 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.17145 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18664 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18664 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.18664 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18085 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18085 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18085 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18042 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18042 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18042 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.30116 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.30116 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.30116 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.1976 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.1976 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.1976 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18239 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18239 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18239 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20216 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20216 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.20216 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18256 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18256 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18256 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18056 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18056 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18056 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.17021 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.17021 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.17021 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22248 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22248 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.22248 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22248 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22248 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.22248 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.1811 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.1811 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.1811 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18854 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10236 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10236 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.10236 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.1958 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.1958 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.1958 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19559 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17823 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17823 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.17823 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18145 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18145 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18145 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15498 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15498 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.15498 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.28467 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.28467 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.28467 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17683 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17683 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.17683 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17683 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17683 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.17683 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.21991 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.21991 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.21991 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18187 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add line 515378 WWRDEHV9 765 523966 POTTER_CO 9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18187 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at WWRDEHV9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18187 |  | Single 515378 WWARD9 765 523966 POTTER_CO9 765 1 | TDF Impact | Add 560 MVAR switched shunt at POTTER_CO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.15173 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.15173 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.15173 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28759 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28759 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.28759 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.32322 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.32322 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.32322 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.32322 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.32322 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.32322 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.27121 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.27121 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.27121 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17516 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17516 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.17516 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17516 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17516 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.17516 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24801 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24801 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.24801 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.2645 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.2645 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.2645 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.28193 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.28193 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.28193 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20139 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20139 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.20139 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20139 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20139 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.20139 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.27408 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.27408 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.27408 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.27408 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.27408 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.27408 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26685 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26685 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.26685 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26639 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26639 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.26639 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25518 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25518 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.25518 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.26444 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.26444 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.26444 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.28285 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.28285 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.28285 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19687 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19687 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.19687 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19687 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19687 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.19687 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22416 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22416 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.22416 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26762 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26762 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.26762 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.28228 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.28228 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.28228 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27642 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27642 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.27642 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1515 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1515 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1515 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.2969 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.2969 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.2969 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.2881 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.2881 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.2881 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.28928 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.28928 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.28928 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.28925 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.28925 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.28925 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20217 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20217 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.20217 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.28095 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.28095 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.28095 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.29023 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.29023 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.29023 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.28133 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.28133 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.28133 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.29014 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.29014 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.29014 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.29125 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.29125 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.29125 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29761 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29761 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29761 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.27203 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.27203 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.27203 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.27203 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.27203 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.27203 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.28941 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.28941 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.28941 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2871 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2871 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.2871 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2871 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2871 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.2871 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.21862 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.21862 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.21862 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.28214 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.28214 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.28214 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.28228 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.28228 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.28228 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.28897 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.28897 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.28897 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.29028 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.29028 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.29028 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29301 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29301 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.29301 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22416 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22416 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.22416 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.29039 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.29039 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.29039 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.29039 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.29039 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.29039 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18019 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18019 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.18019 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.2895 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 526001 CRWFSHDRW9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.2895 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.2895 |  | Single 514812 MINCO9 765 526001 CRDRW9 765 1 | TDF Impact | Add 720 MVAR switched shunt at CRWFSHDRW9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | Single 523823 CARPENTER7 345 772280 G23-015-TAP 345 1 | TDF Impact | Add line 523823 CARPENTER 7 345 772280 G23-015-TAP 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14493 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14493 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.14493 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.22196 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.22196 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.22196 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24059 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24059 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24059 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24059 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24059 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24059 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.21342 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.21342 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.21342 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16111 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16111 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.16111 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16111 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16111 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.16111 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20262 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20262 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.20262 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21065 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21065 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.21065 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.21867 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.21867 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.21867 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.1784 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.1784 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.1784 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.1784 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.1784 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.1784 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.2151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.2151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.2151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.2151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.2151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.2151 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21171 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21171 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.21171 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21149 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21149 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.21149 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.20629 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.20629 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.20629 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21037 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21037 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.21037 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.21912 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.21912 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.21912 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17496 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17496 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17496 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17496 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17496 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17496 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19093 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19093 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19093 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21208 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21208 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.21208 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.21894 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.21894 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.21894 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21594 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21594 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.21594 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14475 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14475 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.14475 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.2258 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.2258 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.2258 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22167 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22167 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.22167 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.22242 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.22242 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.22242 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22243 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22243 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.22243 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.17792 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.17792 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.17792 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.21831 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.21831 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.21831 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22271 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22271 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.22271 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.21833 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.21833 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.21833 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22267 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22267 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.22267 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22319 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22319 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.22319 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.22613 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.22613 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.22613 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21379 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21379 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.21379 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21379 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21379 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.21379 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22246 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22246 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.22246 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.22119 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.22119 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.22119 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.22119 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.22119 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.22119 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.20332 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.20332 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.20332 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.21887 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.21887 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.21887 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.21894 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.21894 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.21894 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22243 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22243 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.22243 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22278 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22278 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.22278 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.22513 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.22513 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.22513 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19093 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19093 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19093 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22307 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22307 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.22307 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22307 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22307 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.22307 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.17872 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.17872 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.17872 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22246 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add line 514812 MINCO 9 765 515049 SEMINOLE9 765 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22246 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 1040 MVAR switched shunt at SEMINOLE9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.22246 |  | Single 514812 MINCO9 765 515049 SEMINOLE9 765 1 | TDF Impact | Add 960 MVAR switched shunt at MINCO 9 765 kV
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.13578 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18799 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.17843 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.17843 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.19337 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.15977 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.15977 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.1917 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.19091 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.19141 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.18107 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.18107 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.19086 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.19086 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.19115 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.19114 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.19007 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.19292 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19122 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17865 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17865 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19338 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19113 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19052 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19259 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1355 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.18938 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.19021 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18932 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18922 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.1903 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19058 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18989 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.19165 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.1899 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18978 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18931 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.19342 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.19342 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18941 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19034 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19034 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15738 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19053 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19052 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18869 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18971 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.18491 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19338 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.18878 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.18878 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.16868 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18959 |  | Single 532828 VIOLA9 765 532798 VIOLA7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.049723 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.11726 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17275 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.06221 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.06221 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.093597 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.10041 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18933 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074776 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074776 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.14598 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.14598 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.11572 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.115 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.07612 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.13113 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19039 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.074233 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.074233 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.086218 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.1186 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18067 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18607 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.049612 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.24711 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.20486 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17703 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17311 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.08338 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17507 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.20661 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1953 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20554 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.21103 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.25088 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18138 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.20121 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.20121 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18008 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18067 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.15024 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.20013 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040925 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.086218 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.16027 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.16027 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.056943 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18904 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 2 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.073877 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.076265 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06789 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06789 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.080033 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.081961 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.081961 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.086225 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.082109 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.077368 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.091692 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.091692 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.079554 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.079554 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081469 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081587 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.084514 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.081995 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077143 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.088948 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.088948 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.09212 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.081267 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.077382 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.07871 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.073781 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.073571 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.075848 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.075642 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.075664 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.090701 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.077734 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.075312 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.0775 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.075336 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.075051 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.073386 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.079795 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.079795 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.075595 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.076102 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.076102 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.16271 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.077419 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.077382 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.075808 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.075322 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.075169 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.09212 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.075413 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.075413 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.12115 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.075548 |  | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.072848 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.0889 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.090317 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.090317 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.091568 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.075291 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.075291 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.083348 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.087979 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.090226 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.062957 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.062957 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.088827 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.088827 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.08859 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.088387 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.083081 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.091169 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.090097 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.07554 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.07554 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.078608 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.088667 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.089017 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.090953 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.072861 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.088078 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.089046 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.089072 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.089061 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.098857 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.088996 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.089017 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.090212 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.089063 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.088896 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.087984 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.091617 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.091617 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.089067 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.089168 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.089168 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.24131 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.089015 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.089017 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.089088 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.088998 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.088199 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.078608 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.089231 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.089231 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.089075 |  | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.049723 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.11726 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17275 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.06221 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.06221 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.093597 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.10041 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.18933 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.074776 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.074776 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.14598 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.14598 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.11572 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.115 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.07612 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.13113 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19039 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.074233 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.074233 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.086218 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.1186 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.18067 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.18607 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.049612 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.24711 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.20486 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.17703 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.17311 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.08338 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.17507 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.20661 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.1953 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20554 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.21103 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.25088 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17781 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18138 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.20121 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.20121 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.18008 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.18067 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.15024 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.20013 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.040925 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.086218 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.16027 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.16027 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.056943 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18904 |  | Single 526001 CRDRW9 765 528014 PHANTOM9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.17473 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.031545 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.14423 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.14423 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.040384 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.034328 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.079298 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.079298 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.031555 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.031555 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.033552 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.033735 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.038199 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.033581 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.092821 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.092821 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.04898 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.033325 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.030321 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.17472 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.077318 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.031298 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.031298 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.04898 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.039322 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.050209 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.044142 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.044142 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.052443 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.10599 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.10599 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.056923 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.053812 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.051069 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.075822 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.075822 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.052368 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.052368 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.053417 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.05351 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.055761 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.053494 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.050954 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.082047 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.082047 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.061352 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.053299 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.05119 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.051779 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.049312 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.050369 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.050103 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.050098 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.074736 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.051379 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.050055 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.051181 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.050058 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.049933 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.049229 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.052316 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.052316 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.050096 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.05049 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.05049 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.044001 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.05121 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.05119 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.050071 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.050031 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.049233 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.061352 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.049862 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.049862 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.057257 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.050104 |  | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.19768 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.12848 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.12848 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.3349 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.11173 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.31461 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.18972 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.18972 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.13791 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.13467 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.030662 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.1874 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.31106 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.1434 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.24783 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.3366 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.29312 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.28349 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.26135 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.25733 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.23894 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.2878 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.31849 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.28881 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.28804 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.29345 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.35284 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.35284 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.26538 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.28409 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.28409 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.03274 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.24692 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.24783 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.23593 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.28098 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.13011 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.25366 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.25366 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.27296 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.073877 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.076265 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06789 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06789 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.080033 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.081961 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.081961 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.086225 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.082109 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.077368 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.091692 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.091692 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.079554 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.079554 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081469 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081587 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.084514 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.081995 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077143 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.088948 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.088948 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.09212 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.081267 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.077382 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.07871 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.073781 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.073571 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.075848 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.075642 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.075664 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.090701 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.077734 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.075312 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.0775 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.075336 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.075051 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.073386 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.079795 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.079795 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.075595 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.076102 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.076102 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.16271 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.077419 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.077382 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.075808 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.075322 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.075169 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.09212 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.075413 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.075413 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.12115 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.075548 |  | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.04102 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.071351 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.071351 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.033438 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.03389 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.03414 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.038325 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.035953 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.038322 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.038543 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.033728 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.03705 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.037064 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.037352 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.038498 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.038133 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.035614 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.035614 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.61804 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.034096 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.03414 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.039783 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.037474 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.048759 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.039977 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.039977 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.037714 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.073877 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.076265 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.06789 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.06789 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.080033 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.081961 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.081961 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.086225 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.082109 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.077368 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.091692 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.091692 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.079554 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.079554 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.081469 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.081587 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.084514 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.081995 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.077143 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.088948 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.088948 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.09212 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.081267 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.077382 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.07871 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.073781 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.073571 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.075848 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.075642 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.075664 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.090701 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.077734 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.075312 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.0775 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.075336 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.075051 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.073386 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.079795 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.079795 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.075595 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.076102 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.076102 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.16271 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.077419 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.077382 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.075808 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.075322 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.075169 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.09212 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.075413 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.075413 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.12115 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.075548 |  | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.123 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.058287 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.051406 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.051406 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.060888 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.12023 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.12023 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.065716 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.062318 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.059319 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.084052 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.084052 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.060731 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.060731 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.061893 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.061993 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.064396 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.062042 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.059186 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.092635 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.092635 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.070585 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.061763 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.059424 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.060133 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.12307 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.057318 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.058511 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.0582 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.058192 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.087396 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.059634 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.058157 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.059447 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.058162 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.058019 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.057225 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.060747 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.060747 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.058194 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.058649 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.058649 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.051302 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.059446 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.059424 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.058151 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.058127 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.057139 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.070585 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.057923 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.057923 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.065666 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.058206 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.13578 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.18799 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.17843 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.17843 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.19337 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.15977 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.15977 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.1917 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.19091 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.19141 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.18107 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.18107 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.19086 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.19086 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.19115 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.19114 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.19007 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.19292 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.19122 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.17865 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.17865 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.19338 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19113 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.19052 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19259 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.1355 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.18938 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.19021 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18932 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18922 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.1903 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.19058 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.18989 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.19165 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.1899 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18978 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18931 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.19342 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.19342 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.18941 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19034 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19034 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.15738 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.19053 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.19052 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18869 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.18971 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.18491 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.19338 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.18878 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.18878 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.16868 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.18959 |  | Single 515378 WWARD9 765 532828 VIOLA9 765 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.032369 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.065853 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.083764 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.083764 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058548 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.037299 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.037299 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055181 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.059762 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.060992 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.042806 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.042806 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.060586 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.060586 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059783 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059678 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.058075 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058391 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061217 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041923 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041923 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.048456 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059883 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.061479 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059504 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.032321 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.062871 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.062133 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.063712 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.063876 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.04285 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.061332 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.062686 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.060549 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.062706 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.062792 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.062917 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058567 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058567 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.06356 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.061999 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.061999 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.052748 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.061464 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.061479 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.064803 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.062988 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.070832 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.048456 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.064782 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.064782 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.033954 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.063247 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.032369 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.065853 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.083764 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.083764 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.058548 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-045 |  | Non-Converged |  |  | 0.037299 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-046 |  | Non-Converged |  |  | 0.037299 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-050 |  | Non-Converged |  |  | 0.055181 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-063 |  | Non-Converged |  |  | 0.059762 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-073 |  | Non-Converged |  |  | 0.060992 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-077 |  | Non-Converged |  |  | 0.042806 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-078 |  | Non-Converged |  |  | 0.042806 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-079 |  | Non-Converged |  |  | 0.060586 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-080 |  | Non-Converged |  |  | 0.060586 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-089 |  | Non-Converged |  |  | 0.059783 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-092 |  | Non-Converged |  |  | 0.059678 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.058075 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.058391 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-124 |  | Non-Converged |  |  | 0.061217 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.041923 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.041923 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-153 |  | Non-Converged |  |  | 0.048456 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.059883 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-186 |  | Non-Converged |  |  | 0.061479 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.059504 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-244 |  | Non-Converged |  |  | 0.032321 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-246 |  | Non-Converged |  |  | 0.062871 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-251 |  | Non-Converged |  |  | 0.062133 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.063712 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.063876 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-266 |  | Non-Converged |  |  | 0.04285 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-271 |  | Non-Converged |  |  | 0.061332 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-273 |  | Non-Converged |  |  | 0.062686 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-278 |  | Non-Converged |  |  | 0.060549 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.062706 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.062792 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.062917 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.058567 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.058567 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-306 |  | Non-Converged |  |  | 0.06356 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.061999 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.061999 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.052748 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-324 |  | Non-Converged |  |  | 0.061464 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-325 |  | Non-Converged |  |  | 0.061479 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.064803 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-351 |  | Non-Converged |  |  | 0.062988 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-355 |  | Non-Converged |  |  | 0.070832 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-364 |  | Non-Converged |  |  | 0.048456 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-365 |  | Non-Converged |  |  | 0.064782 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-366 |  | Non-Converged |  |  | 0.064782 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-368 |  | Non-Converged |  |  | 0.033954 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-371 |  | Non-Converged |  |  | 0.063247 |  | Single 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.37048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.37048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.37048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.37048 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.20126 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.075563 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-228 |  | Non-Converged |  |  | 0.87134 |  | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | TDF Impact | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-007 |  | Non-Converged |  |  | 0.053642 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.08055 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.15774 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-067 |  | Non-Converged |  |  | 0.030705 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-072 |  | Non-Converged |  |  | 0.047746 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-085 |  | Non-Converged |  |  | 0.065215 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.29276 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.37048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.37048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.37048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.37048 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-189 |  | Non-Converged |  |  | 0.052237 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.11983 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.11983 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-205 |  | Non-Converged |  |  | 0.037528 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.20126 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-215 |  | Non-Converged |  |  | 0.032823 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-288 |  | Non-Converged |  |  | 0.034987 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.10784 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.37269 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.37269 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.37269 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.090491 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.30162 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.37269 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.37269 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.37269 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.12987 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.12987 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.1959 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.071397 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-228 |  | Non-Converged |  |  | 0.87141 |  | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | TDF Impact | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-007 |  | Non-Converged |  |  | 0.045449 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.07137 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.14779 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-072 |  | Non-Converged |  |  | 0.040595 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-085 |  | Non-Converged |  |  | 0.056876 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.28254 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-189 |  | Non-Converged |  |  | 0.043671 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.1108 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.1108 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.1959 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.098482 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-007 |  | Non-Converged |  |  | 0.045449 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.07137 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.29067 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-072 |  | Non-Converged |  |  | 0.040595 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-085 |  | Non-Converged |  |  | 0.056876 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.36119 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.3296 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.3296 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.3296 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.3296 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-189 |  | Non-Converged |  |  | 0.043671 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.1108 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.1108 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.20491 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.098482 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.031013 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.033704 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.033811 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.033811 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.033811 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.033811 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.030796 |  | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Add line 652424 BELFELD3 345 800121 MAURINE 2 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.19896 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.074438 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-228 |  | Non-Converged |  |  | 0.87132 |  | Single 532871 CIRCLE6 230 783810 G24-228-TAP 230 1 | TDF Impact | Add line 532871 CIRCLE 6 230 783810 G24-228-TAP 230 P2
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-007 |  | Non-Converged |  |  | 0.051847 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.077682 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.15422 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-067 |  | Non-Converged |  |  | 0.030428 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-072 |  | Non-Converged |  |  | 0.046923 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-085 |  | Non-Converged |  |  | 0.063254 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.28895 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-189 |  | Non-Converged |  |  | 0.050143 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.11725 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.11725 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-205 |  | Non-Converged |  |  | 0.035977 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.19896 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-215 |  | Non-Converged |  |  | 0.032579 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-288 |  | Non-Converged |  |  | 0.034781 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.10485 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | ASGI-2024-003 |  | Non-Converged |  |  | 0.64472 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-007 |  | Non-Converged |  |  | 0.030204 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.041724 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.15345 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-032 |  | Non-Converged |  |  | 0.64472 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-085 |  | Non-Converged |  |  | 0.036322 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.14852 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.13953 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.13953 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.13953 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.13953 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.062956 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.062956 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.10747 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-218 |  | Non-Converged |  |  | 0.36075 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.057526 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-007 |  | Non-Converged |  |  | 0.052497 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-016 |  | Non-Converged |  |  | 0.077682 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.15422 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-067 |  | Non-Converged |  |  | 0.030428 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-072 |  | Non-Converged |  |  | 0.046923 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-085 |  | Non-Converged |  |  | 0.063254 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.28895 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.26695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.26695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.26695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.26695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-189 |  | Non-Converged |  |  | 0.16852 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-193 |  | Non-Converged |  |  | 0.28595 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-194 |  | Non-Converged |  |  | 0.28595 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-205 |  | Non-Converged |  |  | 0.053129 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.18379 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-215 |  | Non-Converged |  |  | 0.032579 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-288 |  | Non-Converged |  |  | 0.034781 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-322 |  | Non-Converged |  |  | 0.10485 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-030 |  | Non-Converged |  |  | 0.034625 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-102 |  | Non-Converged |  |  | 0.037648 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-136 |  | Non-Converged |  |  | 0.037682 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-137 |  | Non-Converged |  |  | 0.037682 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-138 |  | Non-Converged |  |  | 0.037682 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-144 |  | Non-Converged |  |  | 0.037682 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N1 | GEN-2024-210 |  | Non-Converged |  |  | 0.034122 |  | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | ASGI-2024-023 |  | Non-Converged |  |  | 0.037104 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-025 |  | Non-Converged |  |  | 0.04285 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-029 |  | Non-Converged |  |  | 0.049272 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-044 |  | Non-Converged |  |  | 0.041474 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-052 |  | Non-Converged |  |  | 0.046254 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-056 |  | Non-Converged |  |  | 0.043282 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-058 |  | Non-Converged |  |  | 0.03066 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-062 |  | Non-Converged |  |  | 0.049748 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-068 |  | Non-Converged |  |  | 0.04263 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-071 |  | Non-Converged |  |  | 0.041649 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-083 |  | Non-Converged |  |  | 0.045175 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-113 |  | Non-Converged |  |  | 0.03764 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-117 |  | Non-Converged |  |  | 0.032923 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-118 |  | Non-Converged |  |  | 0.038971 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-119 |  | Non-Converged |  |  | 0.05129 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-120 |  | Non-Converged |  |  | 0.049137 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-122 |  | Non-Converged |  |  | 0.041366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-123 |  | Non-Converged |  |  | 0.039286 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-134 |  | Non-Converged |  |  | 0.058176 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-135 |  | Non-Converged |  |  | 0.058176 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-154 |  | Non-Converged |  |  | 0.071215 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-157 |  | Non-Converged |  |  | 0.060482 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-158 |  | Non-Converged |  |  | 0.060124 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-161 |  | Non-Converged |  |  | 0.060469 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-164 |  | Non-Converged |  |  | 0.049264 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-165 |  | Non-Converged |  |  | 0.048015 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-171 |  | Non-Converged |  |  | 0.039949 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-177 |  | Non-Converged |  |  | 0.041463 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-178 |  | Non-Converged |  |  | 0.040991 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-180 |  | Non-Converged |  |  | 0.035974 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-184 |  | Non-Converged |  |  | 0.046681 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-187 |  | Non-Converged |  |  | 0.050585 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-204 |  | Non-Converged |  |  | 0.048282 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-219 |  | Non-Converged |  |  | 0.049389 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-220 |  | Non-Converged |  |  | 0.041623 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-226 |  | Non-Converged |  |  | 0.041741 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-227 |  | Non-Converged |  |  | 0.041741 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-229 |  | Non-Converged |  |  | 0.059595 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-230 |  | Non-Converged |  |  | 0.059595 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-232 |  | Non-Converged |  |  | 0.037087 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-235 |  | Non-Converged |  |  | 0.041196 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-236 |  | Non-Converged |  |  | 0.046224 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-239 |  | Non-Converged |  |  | 0.05157 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-241 |  | Non-Converged |  |  | 0.04285 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-242 |  | Non-Converged |  |  | 0.049545 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-243 |  | Non-Converged |  |  | 0.034432 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-245 |  | Non-Converged |  |  | 0.047864 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-250 |  | Non-Converged |  |  | 0.046491 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-252 |  | Non-Converged |  |  | 0.05157 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-254 |  | Non-Converged |  |  | 0.051476 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-255 |  | Non-Converged |  |  | 0.04947 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-267 |  | Non-Converged |  |  | 0.04782 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-268 |  | Non-Converged |  |  | 0.039756 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-291 |  | Non-Converged |  |  | 0.044161 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-294 |  | Non-Converged |  |  | 0.040823 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-296 |  | Non-Converged |  |  | 0.043407 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-297 |  | Non-Converged |  |  | 0.043407 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-298 |  | Non-Converged |  |  | 0.043407 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-305 |  | Non-Converged |  |  | 0.04143 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-308 |  | Non-Converged |  |  | 0.056798 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-312 |  | Non-Converged |  |  | 0.0328 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-316 |  | Non-Converged |  |  | 0.044934 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-318 |  | Non-Converged |  |  | 0.039172 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-332 |  | Non-Converged |  |  | 0.050545 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-333 |  | Non-Converged |  |  | 0.050126 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-337 |  | Non-Converged |  |  | 0.049855 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-338 |  | Non-Converged |  |  | 0.048471 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-344 |  | Non-Converged |  |  | 0.046411 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-345 |  | Non-Converged |  |  | 0.030486 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-346 |  | Non-Converged |  |  | 0.032301 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-360 |  | Non-Converged |  |  | 0.049042 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-361 |  | Non-Converged |  |  | 0.045047 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-362 |  | Non-Converged |  |  | 0.052771 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-367 |  | Non-Converged |  |  | 0.056025 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-369 |  | Non-Converged |  |  | 0.053927 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-373 |  | Non-Converged |  |  | 0.046254 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-376 |  | Non-Converged |  |  | 0.035809 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-029 |  | Non-Converged |  |  | 0.043819 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-052 |  | Non-Converged |  |  | 0.034486 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-056 |  | Non-Converged |  |  | 0.044453 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-058 |  | Non-Converged |  |  | 0.050775 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-062 |  | Non-Converged |  |  | 0.045965 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-083 |  | Non-Converged |  |  | 0.033986 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-117 |  | Non-Converged |  |  | 0.049933 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-118 |  | Non-Converged |  |  | 0.044996 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-119 |  | Non-Converged |  |  | 0.039877 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-120 |  | Non-Converged |  |  | 0.040587 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-134 |  | Non-Converged |  |  | 0.062257 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-135 |  | Non-Converged |  |  | 0.062257 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-154 |  | Non-Converged |  |  | 0.049873 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-157 |  | Non-Converged |  |  | 0.044803 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-158 |  | Non-Converged |  |  | 0.043931 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-161 |  | Non-Converged |  |  | 0.044687 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-164 |  | Non-Converged |  |  | 0.037118 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-165 |  | Non-Converged |  |  | 0.035721 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-171 |  | Non-Converged |  |  | 0.044586 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-180 |  | Non-Converged |  |  | 0.049055 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-184 |  | Non-Converged |  |  | 0.035644 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-187 |  | Non-Converged |  |  | 0.038754 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-204 |  | Non-Converged |  |  | 0.03595 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-219 |  | Non-Converged |  |  | 0.037321 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-229 |  | Non-Converged |  |  | 0.043513 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-230 |  | Non-Converged |  |  | 0.043513 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-235 |  | Non-Converged |  |  | 0.04565 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-236 |  | Non-Converged |  |  | 0.037149 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-239 |  | Non-Converged |  |  | 0.042725 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-240 |  | Non-Converged |  |  | 0.051745 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-242 |  | Non-Converged |  |  | 0.036888 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-245 |  | Non-Converged |  |  | 0.039455 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-250 |  | Non-Converged |  |  | 0.035893 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-252 |  | Non-Converged |  |  | 0.042725 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-254 |  | Non-Converged |  |  | 0.043894 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-255 |  | Non-Converged |  |  | 0.042541 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-267 |  | Non-Converged |  |  | 0.035453 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-268 |  | Non-Converged |  |  | 0.039443 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-291 |  | Non-Converged |  |  | 0.037239 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-294 |  | Non-Converged |  |  | 0.04512 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-296 |  | Non-Converged |  |  | 0.037678 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-297 |  | Non-Converged |  |  | 0.037678 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-298 |  | Non-Converged |  |  | 0.037678 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-308 |  | Non-Converged |  |  | 0.052859 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-316 |  | Non-Converged |  |  | 0.034257 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-318 |  | Non-Converged |  |  | 0.04504 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-332 |  | Non-Converged |  |  | 0.040788 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-333 |  | Non-Converged |  |  | 0.04121 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-337 |  | Non-Converged |  |  | 0.037155 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-338 |  | Non-Converged |  |  | 0.03596 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-344 |  | Non-Converged |  |  | 0.038918 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-345 |  | Non-Converged |  |  | 0.049875 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-346 |  | Non-Converged |  |  | 0.050415 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-360 |  | Non-Converged |  |  | 0.037829 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-361 |  | Non-Converged |  |  | 0.039733 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-362 |  | Non-Converged |  |  | 0.041935 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-367 |  | Non-Converged |  |  | 0.04171 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-369 |  | Non-Converged |  |  | 0.041604 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N1 | GEN-2024-373 |  | Non-Converged |  |  | 0.034486 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N1 | ASGI-2024-002 |  | Non-Converged |  |  | 0.033699 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-045 |  | Non-Converged |  |  | 0.0514 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-046 |  | Non-Converged |  |  | 0.0514 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-143 |  | Non-Converged |  |  | 0.63431 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-145 |  | Non-Converged |  |  | 0.63431 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-244 |  | Non-Converged |  |  | 0.03394 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | Add line 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-063 |  | Non-Converged |  |  | 0.030358 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-079 |  | Non-Converged |  |  | 0.40832 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-080 |  | Non-Converged |  |  | 0.40832 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-089 |  | Non-Converged |  |  | 0.13672 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-092 |  | Non-Converged |  |  | 0.13558 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-159 |  | Non-Converged |  |  | 0.16104 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-271 |  | Non-Converged |  |  | 0.67104 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-079 |  | Non-Converged |  |  | 0.25036 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-080 |  | Non-Converged |  |  | 0.25036 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-089 |  | Non-Converged |  |  | 0.36098 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-092 |  | Non-Converged |  |  | 0.34365 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-159 |  | Non-Converged |  |  | 0.356 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-186 |  | Non-Converged |  |  | 0.11783 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-251 |  | Non-Converged |  |  | 0.033989 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-271 |  | Non-Converged |  |  | 0.13811 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-310 |  | Non-Converged |  |  | 0.035567 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-311 |  | Non-Converged |  |  | 0.035567 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-324 |  | Non-Converged |  |  | 0.11996 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N1 | GEN-2024-325 |  | Non-Converged |  |  | 0.11783 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-079 |  | Non-Converged |  |  | 0.25047 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-080 |  | Non-Converged |  |  | 0.25047 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-089 |  | Non-Converged |  |  | 0.361 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-092 |  | Non-Converged |  |  | 0.3437 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-159 |  | Non-Converged |  |  | 0.35605 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-186 |  | Non-Converged |  |  | 0.1176 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-251 |  | Non-Converged |  |  | 0.03412 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-271 |  | Non-Converged |  |  | 0.13829 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-310 |  | Non-Converged |  |  | 0.035719 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-311 |  | Non-Converged |  |  | 0.035719 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-324 |  | Non-Converged |  |  | 0.11971 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N1 | GEN-2024-325 |  | Non-Converged |  |  | 0.1176 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.20122 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.075537 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-007 |  | Non-Converged |  |  | 0.053321 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.080167 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-030 |  | Non-Converged |  |  | 0.15717 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-067 |  | Non-Converged |  |  | 0.030548 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-072 |  | Non-Converged |  |  | 0.047527 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-085 |  | Non-Converged |  |  | 0.064875 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.29214 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-189 |  | Non-Converged |  |  | 0.051873 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.1194 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.1194 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-205 |  | Non-Converged |  |  | 0.037235 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.20122 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-215 |  | Non-Converged |  |  | 0.032669 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-288 |  | Non-Converged |  |  | 0.034838 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.10742 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.37269 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.37269 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.37269 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.090334 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.3013 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.37269 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.37269 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.37269 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.12968 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.12968 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.3654 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.1959 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.071393 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-007 |  | Non-Converged |  |  | 0.057999 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.071052 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-030 |  | Non-Converged |  |  | 0.14736 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-072 |  | Non-Converged |  |  | 0.040394 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-085 |  | Non-Converged |  |  | 0.062975 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.28205 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.26006 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.26006 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.26006 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.26006 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-189 |  | Non-Converged |  |  | 0.17438 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.29188 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.29188 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.17695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.098138 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-007 |  | Non-Converged |  |  | 0.045174 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.071052 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-030 |  | Non-Converged |  |  | 0.14736 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-072 |  | Non-Converged |  |  | 0.040394 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-085 |  | Non-Converged |  |  | 0.056588 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.28205 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.3654 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-189 |  | Non-Converged |  |  | 0.043372 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.11045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.11045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.1959 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.098138 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.03252 |  | P12:345.0:UMZ:# N-1 #:: LINE BELFELD3-CHARL_CK-BE3-1 :EHV: | TDF Impact | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.032591 |  | P12:345.0:UMZ:# N-1 #:: LINE BELFELD3-CHARL_CK-BE3-1 :EHV: | TDF Impact | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.032591 |  | P12:345.0:UMZ:# N-1 #:: LINE BELFELD3-CHARL_CK-BE3-1 :EHV: | TDF Impact | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.032591 |  | P12:345.0:UMZ:# N-1 #:: LINE BELFELD3-CHARL_CK-BE3-1 :EHV: | TDF Impact | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.032591 |  | P12:345.0:UMZ:# N-1 #:: LINE BELFELD3-CHARL_CK-BE3-1 :EHV: | TDF Impact | Add line 652424 BELFELD3 345 659183 CHARL_CK-BE3 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.36848 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.19896 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.074435 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-007 |  | Non-Converged |  |  | 0.051625 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.077414 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-030 |  | Non-Converged |  |  | 0.15384 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-067 |  | Non-Converged |  |  | 0.030326 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-072 |  | Non-Converged |  |  | 0.046775 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-085 |  | Non-Converged |  |  | 0.063017 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.28851 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.36848 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-189 |  | Non-Converged |  |  | 0.049895 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.11695 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.11695 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-205 |  | Non-Converged |  |  | 0.035774 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.19896 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-215 |  | Non-Converged |  |  | 0.032479 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-288 |  | Non-Converged |  |  | 0.034685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.10456 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | ASGI-2024-003 |  | Non-Converged |  |  | 0.64471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-007 |  | Non-Converged |  |  | 0.030089 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.041585 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-030 |  | Non-Converged |  |  | 0.15325 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-032 |  | Non-Converged |  |  | 0.64471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-085 |  | Non-Converged |  |  | 0.036199 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.14829 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.1393 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.1393 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.1393 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.1393 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.0628 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.0628 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.10725 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-218 |  | Non-Converged |  |  | 0.36074 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.057374 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-007 |  | Non-Converged |  |  | 0.052831 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-016 |  | Non-Converged |  |  | 0.077414 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-030 |  | Non-Converged |  |  | 0.15384 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-067 |  | Non-Converged |  |  | 0.030326 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-072 |  | Non-Converged |  |  | 0.046775 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-085 |  | Non-Converged |  |  | 0.063017 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-102 |  | Non-Converged |  |  | 0.28851 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-136 |  | Non-Converged |  |  | 0.26651 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-137 |  | Non-Converged |  |  | 0.26651 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-138 |  | Non-Converged |  |  | 0.26651 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-144 |  | Non-Converged |  |  | 0.26651 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-189 |  | Non-Converged |  |  | 0.16892 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-193 |  | Non-Converged |  |  | 0.28643 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-194 |  | Non-Converged |  |  | 0.28643 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-205 |  | Non-Converged |  |  | 0.053432 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-210 |  | Non-Converged |  |  | 0.18337 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-215 |  | Non-Converged |  |  | 0.032479 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-288 |  | Non-Converged |  |  | 0.034685 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N2 | GEN-2024-322 |  | Non-Converged |  |  | 0.10456 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | ASGI-2024-023 |  | Non-Converged |  |  | 0.037244 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-025 |  | Non-Converged |  |  | 0.04302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-029 |  | Non-Converged |  |  | 0.049484 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-044 |  | Non-Converged |  |  | 0.041635 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-052 |  | Non-Converged |  |  | 0.046441 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-056 |  | Non-Converged |  |  | 0.043483 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-058 |  | Non-Converged |  |  | 0.030826 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-062 |  | Non-Converged |  |  | 0.049963 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-068 |  | Non-Converged |  |  | 0.042798 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-071 |  | Non-Converged |  |  | 0.041812 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-083 |  | Non-Converged |  |  | 0.045356 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-113 |  | Non-Converged |  |  | 0.037798 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-117 |  | Non-Converged |  |  | 0.033093 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-118 |  | Non-Converged |  |  | 0.039149 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-119 |  | Non-Converged |  |  | 0.0515 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-120 |  | Non-Converged |  |  | 0.049344 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-122 |  | Non-Converged |  |  | 0.041527 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-123 |  | Non-Converged |  |  | 0.039436 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-134 |  | Non-Converged |  |  | 0.058504 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-135 |  | Non-Converged |  |  | 0.058504 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-154 |  | Non-Converged |  |  | 0.071483 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-157 |  | Non-Converged |  |  | 0.060719 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-158 |  | Non-Converged |  |  | 0.060358 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-161 |  | Non-Converged |  |  | 0.060705 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-164 |  | Non-Converged |  |  | 0.049466 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-165 |  | Non-Converged |  |  | 0.048211 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-171 |  | Non-Converged |  |  | 0.040132 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-177 |  | Non-Converged |  |  | 0.041625 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-178 |  | Non-Converged |  |  | 0.04115 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-180 |  | Non-Converged |  |  | 0.036141 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-184 |  | Non-Converged |  |  | 0.046873 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-187 |  | Non-Converged |  |  | 0.050792 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-204 |  | Non-Converged |  |  | 0.048479 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-219 |  | Non-Converged |  |  | 0.049592 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-220 |  | Non-Converged |  |  | 0.041786 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-226 |  | Non-Converged |  |  | 0.041905 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-227 |  | Non-Converged |  |  | 0.041905 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-229 |  | Non-Converged |  |  | 0.059831 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-230 |  | Non-Converged |  |  | 0.059831 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-232 |  | Non-Converged |  |  | 0.037225 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-235 |  | Non-Converged |  |  | 0.041389 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-236 |  | Non-Converged |  |  | 0.046417 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-239 |  | Non-Converged |  |  | 0.051785 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-241 |  | Non-Converged |  |  | 0.04302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-242 |  | Non-Converged |  |  | 0.049747 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-243 |  | Non-Converged |  |  | 0.034572 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-245 |  | Non-Converged |  |  | 0.048067 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-250 |  | Non-Converged |  |  | 0.046682 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-252 |  | Non-Converged |  |  | 0.051785 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-254 |  | Non-Converged |  |  | 0.051692 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-255 |  | Non-Converged |  |  | 0.049681 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-267 |  | Non-Converged |  |  | 0.048015 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-268 |  | Non-Converged |  |  | 0.039927 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-291 |  | Non-Converged |  |  | 0.044345 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-294 |  | Non-Converged |  |  | 0.041006 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-296 |  | Non-Converged |  |  | 0.04359 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-297 |  | Non-Converged |  |  | 0.04359 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-298 |  | Non-Converged |  |  | 0.04359 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-305 |  | Non-Converged |  |  | 0.041592 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-308 |  | Non-Converged |  |  | 0.057036 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-312 |  | Non-Converged |  |  | 0.032931 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-316 |  | Non-Converged |  |  | 0.045115 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-318 |  | Non-Converged |  |  | 0.039353 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-332 |  | Non-Converged |  |  | 0.050756 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-333 |  | Non-Converged |  |  | 0.050337 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-337 |  | Non-Converged |  |  | 0.050058 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-338 |  | Non-Converged |  |  | 0.048669 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-344 |  | Non-Converged |  |  | 0.04661 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-345 |  | Non-Converged |  |  | 0.030652 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-346 |  | Non-Converged |  |  | 0.03247 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-360 |  | Non-Converged |  |  | 0.049245 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-361 |  | Non-Converged |  |  | 0.045244 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-362 |  | Non-Converged |  |  | 0.052988 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-367 |  | Non-Converged |  |  | 0.056249 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-369 |  | Non-Converged |  |  | 0.054145 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-373 |  | Non-Converged |  |  | 0.046441 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N2 | GEN-2024-376 |  | Non-Converged |  |  | 0.03594 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-063 |  | Non-Converged |  |  | 0.030356 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-079 |  | Non-Converged |  |  | 0.40832 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-080 |  | Non-Converged |  |  | 0.40832 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-089 |  | Non-Converged |  |  | 0.13671 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-092 |  | Non-Converged |  |  | 0.13558 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-159 |  | Non-Converged |  |  | 0.16104 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-271 |  | Non-Converged |  |  | 0.67104 |  | Single 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 1 | TDF Impact | Add line 527483 CHAVES_CNTY6 230 785100 G24-271-TAP 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | ASGI-2024-002 |  | Non-Converged |  |  | 0.036479 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-045 |  | Non-Converged |  |  | 0.055668 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-046 |  | Non-Converged |  |  | 0.055668 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-143 |  | Non-Converged |  |  | 0.68733 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-145 |  | Non-Converged |  |  | 0.68733 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-244 |  | Non-Converged |  |  | 0.036741 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | Add line 523869 CHAN+TASCOS6 230 523959 POTTER_CO 6 230 P2
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-079 |  | Non-Converged |  |  | 0.25036 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-080 |  | Non-Converged |  |  | 0.25036 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-089 |  | Non-Converged |  |  | 0.36098 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-092 |  | Non-Converged |  |  | 0.34365 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-159 |  | Non-Converged |  |  | 0.356 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-186 |  | Non-Converged |  |  | 0.11783 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-251 |  | Non-Converged |  |  | 0.033989 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-271 |  | Non-Converged |  |  | 0.13811 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-310 |  | Non-Converged |  |  | 0.035567 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-311 |  | Non-Converged |  |  | 0.035567 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-324 |  | Non-Converged |  |  | 0.11996 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 26SP | N2 | GEN-2024-325 |  | Non-Converged |  |  | 0.11783 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-079 |  | Non-Converged |  |  | 0.25047 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-080 |  | Non-Converged |  |  | 0.25047 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-089 |  | Non-Converged |  |  | 0.361 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-092 |  | Non-Converged |  |  | 0.3437 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-159 |  | Non-Converged |  |  | 0.35605 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-186 |  | Non-Converged |  |  | 0.1176 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-251 |  | Non-Converged |  |  | 0.03412 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-271 |  | Non-Converged |  |  | 0.13829 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-310 |  | Non-Converged |  |  | 0.035719 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-311 |  | Non-Converged |  |  | 0.035719 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-324 |  | Non-Converged |  |  | 0.11971 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N2 | GEN-2024-325 |  | Non-Converged |  |  | 0.1176 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.20122 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.075538 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-007 |  | Non-Converged |  |  | 0.053312 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.080153 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-030 |  | Non-Converged |  |  | 0.15718 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-067 |  | Non-Converged |  |  | 0.030545 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-072 |  | Non-Converged |  |  | 0.047522 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-085 |  | Non-Converged |  |  | 0.064865 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.29213 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-189 |  | Non-Converged |  |  | 0.051866 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.11939 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.11939 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-205 |  | Non-Converged |  |  | 0.037225 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.20122 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-215 |  | Non-Converged |  |  | 0.032667 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-288 |  | Non-Converged |  |  | 0.034836 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.1074 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.37271 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.37271 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.37271 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.090354 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.30136 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.37271 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.37271 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.37271 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.12973 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29L | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.12973 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.19591 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.071401 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-007 |  | Non-Converged |  |  | 0.045156 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.071031 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-030 |  | Non-Converged |  |  | 0.14742 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-072 |  | Non-Converged |  |  | 0.04038 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-085 |  | Non-Converged |  |  | 0.056573 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.28207 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-189 |  | Non-Converged |  |  | 0.04337 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.11045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.11045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.19591 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.098125 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-007 |  | Non-Converged |  |  | 0.058121 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.071031 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-030 |  | Non-Converged |  |  | 0.14742 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-072 |  | Non-Converged |  |  | 0.04038 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-085 |  | Non-Converged |  |  | 0.063104 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.28207 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-189 |  | Non-Converged |  |  | 0.17453 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.29206 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.29206 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.17695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.098125 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.19897 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.074443 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-007 |  | Non-Converged |  |  | 0.051623 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.077409 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-030 |  | Non-Converged |  |  | 0.15391 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-067 |  | Non-Converged |  |  | 0.030325 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-072 |  | Non-Converged |  |  | 0.046776 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-085 |  | Non-Converged |  |  | 0.063019 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.28855 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-189 |  | Non-Converged |  |  | 0.049909 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.11697 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.11697 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-205 |  | Non-Converged |  |  | 0.035768 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.19897 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-215 |  | Non-Converged |  |  | 0.03248 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-288 |  | Non-Converged |  |  | 0.034687 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.10456 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-007 |  | Non-Converged |  |  | 0.052937 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.077409 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-030 |  | Non-Converged |  |  | 0.15391 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-067 |  | Non-Converged |  |  | 0.030325 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-072 |  | Non-Converged |  |  | 0.046776 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-085 |  | Non-Converged |  |  | 0.063019 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.28855 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-189 |  | Non-Converged |  |  | 0.16905 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.2866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.2866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-205 |  | Non-Converged |  |  | 0.053527 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.18339 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-215 |  | Non-Converged |  |  | 0.03248 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-288 |  | Non-Converged |  |  | 0.034687 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.10456 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | ASGI-2024-003 |  | Non-Converged |  |  | 0.64471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-007 |  | Non-Converged |  |  | 0.030088 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-016 |  | Non-Converged |  |  | 0.041582 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-030 |  | Non-Converged |  |  | 0.15329 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-032 |  | Non-Converged |  |  | 0.64471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-085 |  | Non-Converged |  |  | 0.0362 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-102 |  | Non-Converged |  |  | 0.14831 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-136 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-137 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-138 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-144 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-193 |  | Non-Converged |  |  | 0.06281 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-194 |  | Non-Converged |  |  | 0.06281 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-210 |  | Non-Converged |  |  | 0.10726 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-218 |  | Non-Converged |  |  | 0.36075 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N3 | GEN-2024-322 |  | Non-Converged |  |  | 0.057375 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | ASGI-2024-023 |  | Non-Converged |  |  | 0.037302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-025 |  | Non-Converged |  |  | 0.043088 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-029 |  | Non-Converged |  |  | 0.049556 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-044 |  | Non-Converged |  |  | 0.041702 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-052 |  | Non-Converged |  |  | 0.046516 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-056 |  | Non-Converged |  |  | 0.04355 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-058 |  | Non-Converged |  |  | 0.030879 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-062 |  | Non-Converged |  |  | 0.050035 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-068 |  | Non-Converged |  |  | 0.042866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-071 |  | Non-Converged |  |  | 0.041879 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-083 |  | Non-Converged |  |  | 0.045429 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-113 |  | Non-Converged |  |  | 0.037858 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-117 |  | Non-Converged |  |  | 0.033149 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-118 |  | Non-Converged |  |  | 0.039213 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-119 |  | Non-Converged |  |  | 0.051581 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-120 |  | Non-Converged |  |  | 0.049419 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-122 |  | Non-Converged |  |  | 0.041593 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-123 |  | Non-Converged |  |  | 0.039498 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-134 |  | Non-Converged |  |  | 0.058587 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-135 |  | Non-Converged |  |  | 0.058587 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-154 |  | Non-Converged |  |  | 0.071603 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-157 |  | Non-Converged |  |  | 0.060815 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-158 |  | Non-Converged |  |  | 0.060454 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-161 |  | Non-Converged |  |  | 0.060802 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-164 |  | Non-Converged |  |  | 0.049545 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-165 |  | Non-Converged |  |  | 0.048289 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-171 |  | Non-Converged |  |  | 0.040198 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-177 |  | Non-Converged |  |  | 0.041691 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-178 |  | Non-Converged |  |  | 0.041215 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-180 |  | Non-Converged |  |  | 0.036201 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-184 |  | Non-Converged |  |  | 0.046948 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-187 |  | Non-Converged |  |  | 0.050872 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-204 |  | Non-Converged |  |  | 0.048557 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-219 |  | Non-Converged |  |  | 0.049671 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-220 |  | Non-Converged |  |  | 0.041852 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-226 |  | Non-Converged |  |  | 0.041971 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-227 |  | Non-Converged |  |  | 0.041971 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-229 |  | Non-Converged |  |  | 0.059935 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-230 |  | Non-Converged |  |  | 0.059935 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-232 |  | Non-Converged |  |  | 0.037282 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-235 |  | Non-Converged |  |  | 0.041455 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-236 |  | Non-Converged |  |  | 0.046492 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-239 |  | Non-Converged |  |  | 0.051861 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-240 |  | Non-Converged |  |  | 0.030025 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-241 |  | Non-Converged |  |  | 0.043088 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-242 |  | Non-Converged |  |  | 0.049827 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-243 |  | Non-Converged |  |  | 0.034626 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-245 |  | Non-Converged |  |  | 0.048141 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-250 |  | Non-Converged |  |  | 0.046758 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-252 |  | Non-Converged |  |  | 0.051861 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-254 |  | Non-Converged |  |  | 0.051764 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-255 |  | Non-Converged |  |  | 0.049754 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-267 |  | Non-Converged |  |  | 0.048092 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-268 |  | Non-Converged |  |  | 0.039991 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-291 |  | Non-Converged |  |  | 0.044417 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-294 |  | Non-Converged |  |  | 0.041074 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-296 |  | Non-Converged |  |  | 0.04366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-297 |  | Non-Converged |  |  | 0.04366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-298 |  | Non-Converged |  |  | 0.04366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-305 |  | Non-Converged |  |  | 0.041658 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-308 |  | Non-Converged |  |  | 0.057095 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-312 |  | Non-Converged |  |  | 0.032981 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-316 |  | Non-Converged |  |  | 0.045187 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-318 |  | Non-Converged |  |  | 0.039417 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-332 |  | Non-Converged |  |  | 0.050833 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-333 |  | Non-Converged |  |  | 0.050412 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-337 |  | Non-Converged |  |  | 0.050139 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-338 |  | Non-Converged |  |  | 0.048748 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-344 |  | Non-Converged |  |  | 0.046681 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-345 |  | Non-Converged |  |  | 0.030705 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-346 |  | Non-Converged |  |  | 0.032526 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-360 |  | Non-Converged |  |  | 0.049323 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-361 |  | Non-Converged |  |  | 0.045315 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-362 |  | Non-Converged |  |  | 0.05307 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-367 |  | Non-Converged |  |  | 0.056342 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-369 |  | Non-Converged |  |  | 0.054231 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-373 |  | Non-Converged |  |  | 0.046516 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N3 | GEN-2024-376 |  | Non-Converged |  |  | 0.035995 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-079 |  | Non-Converged |  |  | 0.24929 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-080 |  | Non-Converged |  |  | 0.24929 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-089 |  | Non-Converged |  |  | 0.36061 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-092 |  | Non-Converged |  |  | 0.34331 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-159 |  | Non-Converged |  |  | 0.35558 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-186 |  | Non-Converged |  |  | 0.11841 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-251 |  | Non-Converged |  |  | 0.034366 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-271 |  | Non-Converged |  |  | 0.13635 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-310 |  | Non-Converged |  |  | 0.035976 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-311 |  | Non-Converged |  |  | 0.035976 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-324 |  | Non-Converged |  |  | 0.12054 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 05ALL | 0 | 29SP | N3 | GEN-2024-325 |  | Non-Converged |  |  | 0.11841 |  | P12:230:SPS:K18_K30-1::TOLK_RSVLT:HV: | TDF Impact | Add line 524909 ROOSEVELT 6 230 525531 TOLK 6 230 P3
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.37666 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.37666 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.37666 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.37666 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.20516 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.075833 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.37666 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.37666 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.37666 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.37666 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.20516 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.075833 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.37157 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.37157 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.37157 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.37157 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.19973 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.071554 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.37157 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.37157 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.37157 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.37157 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.19973 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.071554 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-016 |  | Non-Converged |  |  | 0.036843 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-030 |  | Non-Converged |  |  | 0.062922 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-085 |  | Non-Converged |  |  | 0.03643 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-102 |  | Non-Converged |  |  | 0.12774 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.11791 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.11791 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.11791 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.11791 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-193 |  | Non-Converged |  |  | 0.16849 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-194 |  | Non-Converged |  |  | 0.16849 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.080967 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.048912 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.37476 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.37476 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.37476 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.37476 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.2029 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.074697 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-016 |  | Non-Converged |  |  | 0.039835 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-030 |  | Non-Converged |  |  | 0.065972 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-085 |  | Non-Converged |  |  | 0.033785 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-102 |  | Non-Converged |  |  | 0.13079 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.12095 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.12095 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.12095 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.12095 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-189 |  | Non-Converged |  |  | 0.097518 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-193 |  | Non-Converged |  |  | 0.16535 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-194 |  | Non-Converged |  |  | 0.16535 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.083992 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.051935 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-016 |  | Non-Converged |  |  | 0.039835 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-030 |  | Non-Converged |  |  | 0.065972 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-085 |  | Non-Converged |  |  | 0.033785 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-102 |  | Non-Converged |  |  | 0.13079 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.37476 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.37476 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.37476 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.37476 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-189 |  | Non-Converged |  |  | 0.031419 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-193 |  | Non-Converged |  |  | 0.069484 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-194 |  | Non-Converged |  |  | 0.069484 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.2029 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.074697 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | ASGI-2024-003 |  | Non-Converged |  |  | 0.64486 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-007 |  | Non-Converged |  |  | 0.032137 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-016 |  | Non-Converged |  |  | 0.042692 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-030 |  | Non-Converged |  |  | 0.15268 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-032 |  | Non-Converged |  |  | 0.64486 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-085 |  | Non-Converged |  |  | 0.038452 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-102 |  | Non-Converged |  |  | 0.13481 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-136 |  | Non-Converged |  |  | 0.12698 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-137 |  | Non-Converged |  |  | 0.12698 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-138 |  | Non-Converged |  |  | 0.12698 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-144 |  | Non-Converged |  |  | 0.12698 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-189 |  | Non-Converged |  |  | 0.034053 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-193 |  | Non-Converged |  |  | 0.073742 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-194 |  | Non-Converged |  |  | 0.073742 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-210 |  | Non-Converged |  |  | 0.099546 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-218 |  | Non-Converged |  |  | 0.36083 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N4 | GEN-2024-322 |  | Non-Converged |  |  | 0.057008 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N4 | GEN-2024-154 |  | Non-Converged |  |  | 0.034872 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.37045 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.20122 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.075538 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-007 |  | Non-Converged |  |  | 0.053312 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-016 |  | Non-Converged |  |  | 0.080153 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-030 |  | Non-Converged |  |  | 0.15718 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-067 |  | Non-Converged |  |  | 0.030545 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-072 |  | Non-Converged |  |  | 0.047522 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-085 |  | Non-Converged |  |  | 0.064865 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-102 |  | Non-Converged |  |  | 0.29213 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.37045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-189 |  | Non-Converged |  |  | 0.051866 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-193 |  | Non-Converged |  |  | 0.11939 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-194 |  | Non-Converged |  |  | 0.11939 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-205 |  | Non-Converged |  |  | 0.037225 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.20122 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-215 |  | Non-Converged |  |  | 0.032667 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-288 |  | Non-Converged |  |  | 0.034836 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.1074 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.36541 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.19591 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.071401 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-007 |  | Non-Converged |  |  | 0.058121 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-016 |  | Non-Converged |  |  | 0.071031 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-030 |  | Non-Converged |  |  | 0.14742 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-072 |  | Non-Converged |  |  | 0.04038 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-085 |  | Non-Converged |  |  | 0.063104 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-102 |  | Non-Converged |  |  | 0.28207 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.26007 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-189 |  | Non-Converged |  |  | 0.17453 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-193 |  | Non-Converged |  |  | 0.29206 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-194 |  | Non-Converged |  |  | 0.29206 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.17695 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.098125 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-007 |  | Non-Converged |  |  | 0.045156 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-016 |  | Non-Converged |  |  | 0.071031 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-030 |  | Non-Converged |  |  | 0.14742 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-072 |  | Non-Converged |  |  | 0.04038 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-085 |  | Non-Converged |  |  | 0.056573 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-102 |  | Non-Converged |  |  | 0.28207 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.36541 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-189 |  | Non-Converged |  |  | 0.04337 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-193 |  | Non-Converged |  |  | 0.11045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-194 |  | Non-Converged |  |  | 0.11045 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.19591 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29SP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.098125 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.3685 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.19897 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.074443 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | Add line 531449 HOLCOMB7 345 531465 SETAB 7 345 P2
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-007 |  | Non-Converged |  |  | 0.052937 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-016 |  | Non-Converged |  |  | 0.077409 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-030 |  | Non-Converged |  |  | 0.15391 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-067 |  | Non-Converged |  |  | 0.030325 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-072 |  | Non-Converged |  |  | 0.046776 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-085 |  | Non-Converged |  |  | 0.063019 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-102 |  | Non-Converged |  |  | 0.28855 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.26654 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-189 |  | Non-Converged |  |  | 0.16905 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-193 |  | Non-Converged |  |  | 0.2866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-194 |  | Non-Converged |  |  | 0.2866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-205 |  | Non-Converged |  |  | 0.053527 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.18339 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-215 |  | Non-Converged |  |  | 0.03248 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-288 |  | Non-Converged |  |  | 0.034687 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.10456 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-007 |  | Non-Converged |  |  | 0.051623 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-016 |  | Non-Converged |  |  | 0.077409 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-030 |  | Non-Converged |  |  | 0.15391 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-067 |  | Non-Converged |  |  | 0.030325 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-072 |  | Non-Converged |  |  | 0.046776 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-085 |  | Non-Converged |  |  | 0.063019 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-102 |  | Non-Converged |  |  | 0.28855 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.3685 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-189 |  | Non-Converged |  |  | 0.049909 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-193 |  | Non-Converged |  |  | 0.11697 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-194 |  | Non-Converged |  |  | 0.11697 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-205 |  | Non-Converged |  |  | 0.035768 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.19897 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-215 |  | Non-Converged |  |  | 0.03248 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-288 |  | Non-Converged |  |  | 0.034687 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.10456 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | ASGI-2024-003 |  | Non-Converged |  |  | 0.64471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-007 |  | Non-Converged |  |  | 0.030088 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-016 |  | Non-Converged |  |  | 0.041582 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-030 |  | Non-Converged |  |  | 0.15329 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-032 |  | Non-Converged |  |  | 0.64471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-085 |  | Non-Converged |  |  | 0.0362 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-102 |  | Non-Converged |  |  | 0.14831 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-136 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-137 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-138 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-144 |  | Non-Converged |  |  | 0.13931 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-193 |  | Non-Converged |  |  | 0.06281 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-194 |  | Non-Converged |  |  | 0.06281 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-210 |  | Non-Converged |  |  | 0.10726 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-218 |  | Non-Converged |  |  | 0.36075 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 29WP | N5 | GEN-2024-322 |  | Non-Converged |  |  | 0.057375 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | ASGI-2024-023 |  | Non-Converged |  |  | 0.037302 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-025 |  | Non-Converged |  |  | 0.043088 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-029 |  | Non-Converged |  |  | 0.049556 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-044 |  | Non-Converged |  |  | 0.041702 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-052 |  | Non-Converged |  |  | 0.046516 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-056 |  | Non-Converged |  |  | 0.04355 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-058 |  | Non-Converged |  |  | 0.030879 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-062 |  | Non-Converged |  |  | 0.050035 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-068 |  | Non-Converged |  |  | 0.042866 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-071 |  | Non-Converged |  |  | 0.041879 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-083 |  | Non-Converged |  |  | 0.045429 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-113 |  | Non-Converged |  |  | 0.037858 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-117 |  | Non-Converged |  |  | 0.033149 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-118 |  | Non-Converged |  |  | 0.039213 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-119 |  | Non-Converged |  |  | 0.051581 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-120 |  | Non-Converged |  |  | 0.049419 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-122 |  | Non-Converged |  |  | 0.041593 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-123 |  | Non-Converged |  |  | 0.039498 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-134 |  | Non-Converged |  |  | 0.058587 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-135 |  | Non-Converged |  |  | 0.058587 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-154 |  | Non-Converged |  |  | 0.071603 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-157 |  | Non-Converged |  |  | 0.060815 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-158 |  | Non-Converged |  |  | 0.060454 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-161 |  | Non-Converged |  |  | 0.060802 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-164 |  | Non-Converged |  |  | 0.049545 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-165 |  | Non-Converged |  |  | 0.048289 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-171 |  | Non-Converged |  |  | 0.040198 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-177 |  | Non-Converged |  |  | 0.041691 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-178 |  | Non-Converged |  |  | 0.041215 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-180 |  | Non-Converged |  |  | 0.036201 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-184 |  | Non-Converged |  |  | 0.046948 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-187 |  | Non-Converged |  |  | 0.050872 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-204 |  | Non-Converged |  |  | 0.048557 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-219 |  | Non-Converged |  |  | 0.049671 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-220 |  | Non-Converged |  |  | 0.041852 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-226 |  | Non-Converged |  |  | 0.041971 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-227 |  | Non-Converged |  |  | 0.041971 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-229 |  | Non-Converged |  |  | 0.059935 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-230 |  | Non-Converged |  |  | 0.059935 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-232 |  | Non-Converged |  |  | 0.037282 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-235 |  | Non-Converged |  |  | 0.041455 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-236 |  | Non-Converged |  |  | 0.046492 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-239 |  | Non-Converged |  |  | 0.051861 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-240 |  | Non-Converged |  |  | 0.030025 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-241 |  | Non-Converged |  |  | 0.043088 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-242 |  | Non-Converged |  |  | 0.049827 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-243 |  | Non-Converged |  |  | 0.034626 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-245 |  | Non-Converged |  |  | 0.048141 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-250 |  | Non-Converged |  |  | 0.046758 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-252 |  | Non-Converged |  |  | 0.051861 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-254 |  | Non-Converged |  |  | 0.051764 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-255 |  | Non-Converged |  |  | 0.049754 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-267 |  | Non-Converged |  |  | 0.048092 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-268 |  | Non-Converged |  |  | 0.039991 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-291 |  | Non-Converged |  |  | 0.044417 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-294 |  | Non-Converged |  |  | 0.041074 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-296 |  | Non-Converged |  |  | 0.04366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-297 |  | Non-Converged |  |  | 0.04366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-298 |  | Non-Converged |  |  | 0.04366 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-305 |  | Non-Converged |  |  | 0.041658 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-308 |  | Non-Converged |  |  | 0.057095 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-312 |  | Non-Converged |  |  | 0.032981 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-316 |  | Non-Converged |  |  | 0.045187 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-318 |  | Non-Converged |  |  | 0.039417 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-332 |  | Non-Converged |  |  | 0.050833 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-333 |  | Non-Converged |  |  | 0.050412 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-337 |  | Non-Converged |  |  | 0.050139 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-338 |  | Non-Converged |  |  | 0.048748 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-344 |  | Non-Converged |  |  | 0.046681 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-345 |  | Non-Converged |  |  | 0.030705 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-346 |  | Non-Converged |  |  | 0.032526 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-360 |  | Non-Converged |  |  | 0.049323 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-361 |  | Non-Converged |  |  | 0.045315 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-362 |  | Non-Converged |  |  | 0.05307 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-367 |  | Non-Converged |  |  | 0.056342 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-369 |  | Non-Converged |  |  | 0.054231 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-373 |  | Non-Converged |  |  | 0.046516 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N5 | GEN-2024-376 |  | Non-Converged |  |  | 0.035995 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.86622 | 136.0367 | P12:138:GRDA:KINZEGR4-NORTHTP4:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21458 | 110.8702 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21569 | 110.8702 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.29959 | 136.1107 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.2146 | 117.4586 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.2157 | 117.4586 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.06449 | 115.8898 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.065555 | 115.8898 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.099631 | 115.8898 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.13839 | 125.5799 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.058597 | 143.8893 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.059646 | 143.8893 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.10238 | 143.8893 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.091696 | 113.5329 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.06449 | 115.2421 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.065555 | 115.2421 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.099631 | 115.2421 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.46769 | 105.0961 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.28593 | 101.2772 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.13839 | 127.4796 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.058597 | 145.7927 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.059646 | 145.7927 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.10238 | 145.7927 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.091696 | 115.43 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.46769 | 106.6696 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.28593 | 103.1914 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 113.4865 | P42:345:OKGE:SB_REUD7386:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 113.4866 | P42:345:OKGE:SB_REUD7389:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 110.3133 | Single 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 113.4867 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.213 | 109.586 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23179 | 109.586 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.4922 | 109.586 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079081 | 109.586 | 272864 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079825 | 109.586 | 272864 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.2133 | 117.7751 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23205 | 117.7751 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.49258 | 117.7751 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079238 | 117.7751 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079985 | 117.7751 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17069 | 119.2963 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.091797 | 119.2963 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.67044 | 119.2963 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.2235 | 121.7088 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.24043 | 121.7088 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.52897 | 121.7088 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.082674 | 121.7088 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.083457 | 121.7088 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.2133 | 109.8433 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23205 | 109.8433 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.49258 | 109.8433 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079238 | 109.8433 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079985 | 109.8433 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-247 | TO->FROM | 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | B | 191 | 0.84069 | 129.599 | P12:138:GRDA:4STILWTR-NORTHTP4:::HV: | TDF Impact | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.085614 | 101.6309 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.061941 | 101.6309 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.15152 | 101.6309 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.059396 | 100.1915 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.050198 | 100.1915 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.083693 | 100.1915 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.085614 | 101.6309 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.061941 | 101.6309 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.15152 | 101.6309 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 110.9692 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 110.9705 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.059396 | 111.1423 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.050198 | 111.1423 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.083693 | 111.1423 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.2644 | 104.3989 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.49921 | 104.3989 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26734 | 103.2834 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50323 | 103.2834 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26831 | 103.529 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50447 | 103.529 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26734 | 103.3397 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50323 | 103.3397 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.2644 | 102.2084 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.49921 | 102.2084 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26734 | 101.1194 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50323 | 101.1194 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26831 | 101.3593 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50447 | 101.3593 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26734 | 101.1745 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50323 | 101.1745 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.2644 | 104.6701 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.49921 | 104.6701 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26734 | 103.5604 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50323 | 103.5604 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26831 | 103.8053 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50447 | 103.8053 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26734 | 103.617 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50323 | 103.617 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49452 | 101.6056 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48832 | 101.6056 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.51136 | 104.793 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.50587 | 104.793 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79418 | 140.93 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79418 | 140.93 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79418 | 144.151 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79418 | 144.151 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79418 | 144.1206 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79418 | 144.1206 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48026 | 100.6364 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.47433 | 100.6364 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72459 | 135.1357 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72818 | 135.1357 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 1 | 196.2064 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72979 | 150.3931 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.73329 | 150.3931 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72459 | 139.4115 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72818 | 139.4115 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 200.5394 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72979 | 154.6901 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.73329 | 154.6901 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.083804 | 125.0711 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.08273 | 125.0711 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.056494 | 108.7462 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.055723 | 108.7462 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089573 | 112.0879 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088401 | 112.0879 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13328 | 147.319 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13155 | 147.319 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088853 | 108.1966 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088853 | 108.1966 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.073137 | 126.4157 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.07215 | 126.4157 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088853 | 109.3159 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088853 | 109.3159 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088853 | 109.3613 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088853 | 109.3613 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.058042 | 111.7233 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.057249 | 111.7233 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092027 | 115.1565 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090823 | 115.1565 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13693 | 151.3522 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13516 | 151.3522 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091287 | 111.1587 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091287 | 111.1587 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.074386 | 128.5589 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.073383 | 128.5589 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091287 | 112.3086 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091287 | 112.3086 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091287 | 112.3553 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091287 | 112.3553 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.5026 | 113.9119 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.49627 | 113.9119 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52608 | 126.8744 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52037 | 126.8744 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50217 | 119.5362 | GEN542951 5 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49585 | 119.5362 | GEN542951 5 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51111 | 120.221 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50489 | 120.221 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81986 | 164.2483 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81986 | 164.2483 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52579 | 126.9985 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51915 | 126.9985 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52494 | 126.5205 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51832 | 126.5205 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81986 | 167.5741 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81986 | 167.5741 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81986 | 167.5628 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81986 | 167.5628 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51278 | 119.4331 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.5069 | 119.4331 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49494 | 121.8846 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.48877 | 121.8846 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | A | 281 | 0.60225 | 142.4019 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.63077 | 146.1379 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60225 | 153.0023 | Single 548807 BLUVLY-161 161 783151 GEN-2024-206 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60225 | 153.4504 | GEN-2024-206_POI_548807_Generator_outage | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60183 | 135.2895 | GEN542951 5 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.61012 | 135.7495 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 196.4027 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 200.7938 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 200.8079 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.61489 | 136.6182 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.59448 | 138.478 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.093815 | 115.7018 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.092594 | 115.7018 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.62938 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32771 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32771 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.62938 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.62938 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32771 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32771 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.035854 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.035823 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.055293 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.047321 | 116.3384 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60996 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60996 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60996 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055864 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055808 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.081197 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.075606 | 130.9476 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62815 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62815 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62815 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.05683 | 126.8895 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.56993 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27493 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27493 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.56993 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.56993 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27493 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27493 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.06877 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.068732 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.076628 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.08009 | 138.1433 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060966 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.52136 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37111 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37111 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.52136 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.52136 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37111 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37111 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.061981 | 132.7829 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.63163 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32994 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32994 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.63163 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.63163 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32994 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32994 | 123.1768 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060673 | 123.1768 | P55:345:MEC:ORIENT | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052776 | 123.1768 | P55:345:MEC:ORIENT | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.070048 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57078 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44754 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44754 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57078 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57078 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44754 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44754 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.085735 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051714 | 151.5669 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67668 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36945 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36945 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67668 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67668 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36945 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36945 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.10138 | 124.2326 | P42:345:NPPD:BKR-CPR-3310:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.63234 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33059 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33059 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.63234 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.63234 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33059 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33059 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060933 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052968 | 123.1202 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60996 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60996 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60996 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31138 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055864 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055808 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.081197 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.075606 | 133.0044 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.070327 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54372 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42522 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42522 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54372 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54372 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42522 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42522 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.078166 | 146.6922 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | B | 201 | 0.21637 | 100.4946 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | B | 201 | 0.21637 | 100.4946 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1 | B | 203 | 0.16588 | 110.3779 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1 | B | 203 | 0.16588 | 110.3779 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655942 N.TWELVE-MW7 115 655959 EPPING -MW7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | B | 189 | 0.25872 | 192.0906 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | B | 189 | 0.25872 | 192.0906 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1 | B | 203 | 0.16588 | 111.1475 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1 | B | 203 | 0.16588 | 111.1475 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655945 WHEELS_T-MW7 115 655959 EPPING -MW7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | B | 435 | 0.39507 | 134.9735 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | B | 435 | 0.39507 | 134.9735 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 112.072 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 112.072 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.60493 | 124.2197 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.60493 | 124.2197 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 110.6391 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 110.6391 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60493 | 100.0222 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60493 | 100.0222 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60493 | 100.0222 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60493 | 100.0222 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 108.0382 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 108.039 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.56983 | 102.7909 | Single 515009 MCELROY4 138 515181 UNVRSTY4 138 1 | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.44974 | 101.3354 | P21:138:GRDA:KINZEGR-19TH ST:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.50693 | 108.5389 | Single 512731 NORTHTP4 138 512732 NORTHTP2 69 512739 'NORTAP1 ' 13 1 | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.86615 | 153.353 | P12:138:GRDA:KINZEGR4-NORTHTP4:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.7053 | 110.6341 | P12:138:OKGE-GRDA:BKRBKR1030:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.56983 | 104.0068 | Single 515008 KINZE4 138 515181 UNVRSTY4 138 1 | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.70528 | 110.6945 | P12:138:OKGE:BKRBKR0990:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.094909 | 108.7338 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.097429 | 108.7338 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21515 | 135.8722 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21625 | 135.8722 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.090286 | 109.2909 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.093011 | 109.2909 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.29964 | 155.015 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.094909 | 108.7338 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.097429 | 108.7338 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.084768 | 108.0401 | P12:161:KCPL:CARROLLTON-BRUNSWICK-SALISBUR:::HV: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.087254 | 108.0401 | P12:161:KCPL:CARROLLTON-BRUNSWICK-SALISBUR:::HV: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.084768 | 109.0746 | Single 543061 BRUNSWK5 161 543062 SALSBRY5 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.087254 | 109.0746 | Single 543061 BRUNSWK5 161 543062 SALSBRY5 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21478 | 129.1 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.2159 | 129.1 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.09489 | 108.7445 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.09741 | 108.7445 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.09489 | 108.7445 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.09741 | 108.7445 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.13179 | 110.0911 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.063821 | 137.8049 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.064893 | 137.8049 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.099466 | 137.8049 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 287 | 0.058167 | 107.7922 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 287 | 0.059226 | 107.7922 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 287 | 0.10246 | 107.7922 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.13179 | 109.5965 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.063821 | 137.2847 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.064893 | 137.2847 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.099466 | 137.2847 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | A | 137 | 0.033433 | 105.0443 | System Intact | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | A | 137 | 0.034021 | 105.0443 | System Intact | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.054093 | 106.4047 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.055028 | 106.4047 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.46796 | 111.3979 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.28405 | 110.9185 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.46796 | 112.9804 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.28405 | 113.0091 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.071853 | 101.396 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.063149 | 101.396 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.071853 | 101.2851 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.06315 | 101.2851 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.071853 | 107.0477 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.063149 | 107.0477 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.076671 | 102.4493 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.067568 | 102.4493 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.072816 | 102.8979 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.063713 | 102.8979 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.071853 | 106.9345 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.06315 | 106.9345 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 126.4054 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 126.4053 | P42:345:OKGE:SB_REUD7386:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 122.8396 | Single 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 126.4053 | P42:345:OKGE:SB_REUD7389:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.21764 | 110.0292 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20409 | 110.0292 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.40239 | 110.0292 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.064984 | 110.0292 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065547 | 110.0292 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.21622 | 109.9106 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20267 | 109.9106 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.40096 | 109.9106 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.06356 | 109.9106 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.064123 | 109.9106 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.21789 | 110.0285 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20434 | 110.0285 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.40263 | 110.0285 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065229 | 110.0285 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065793 | 110.0285 | Single 511568 TERRYRD7 345 515136 SUNNYSD7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20548 | 136.254 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22481 | 136.254 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.48357 | 136.254 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.075016 | 136.254 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.075751 | 136.254 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.21582 | 140.016 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23324 | 140.016 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.52003 | 140.016 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.078249 | 140.016 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079022 | 140.016 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20548 | 127.4669 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22481 | 127.4669 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.48357 | 127.4669 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.075016 | 127.4669 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.075751 | 127.4669 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.21764 | 110.0336 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20409 | 110.0336 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.40239 | 110.0336 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.064984 | 110.0336 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065547 | 110.0336 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.21764 | 110.0292 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20409 | 110.0292 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.40239 | 110.0292 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.064984 | 110.0292 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065547 | 110.0292 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20511 | 127.1087 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22448 | 127.1087 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.48308 | 127.1087 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.074826 | 127.1087 | 272864 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.075558 | 127.1087 | 272864 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.16395 | 135.6936 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.085692 | 135.6936 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.66226 | 135.6936 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | B | 191 | 0.07062 | 100.9272 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511425 TUTCONT4 138 514898 CIMARON4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.21147 | 100.1834 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.064585 | 100.1834 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.21147 | 100.0358 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.064585 | 100.0358 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-247 | TO->FROM | 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | B | 191 | 0.8408 | 145.5572 | P12:138:GRDA:4STILWTR-NORTHTP4:::HV: | TDF Impact | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.085505 | 109.5361 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.061452 | 109.5361 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.1514 | 109.5361 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.059666 | 115.4138 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.050269 | 115.4138 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.083929 | 115.4138 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.085505 | 109.5361 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.061452 | 109.5361 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.1514 | 109.5361 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Add 3-winding transformer 514808 JOHNCO 4 138 514809 JOHNCO 7 345 514810 JOHNCO11 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 122.9763 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 122.9793 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.059666 | 128.8052 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.050269 | 128.8052 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.083929 | 128.8052 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.059666 | 114.5605 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.050269 | 114.5605 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.083929 | 114.5605 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515121 MILLCKT4 138 515122 SXMLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.11921 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.067601 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.1325 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.25098 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.075244 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.11243 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.058986 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.058974 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 515235 PECANCK7 345 516374 KEEFTON7 345 1 | B | 1195 | 0.057916 | 105.7048 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515235 PECANCK7 345 516374 KEEFTON7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | TO->FROM | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | A | 76 | 0.034517 | 108.7425 | System Intact | TDF Impact | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | A | 76 | 0.034517 | 108.7425 | System Intact | TDF Impact | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.37517 | 111.1711 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.060125 | 111.1711 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.37517 | 111.1711 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.060125 | 111.1711 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26888 | 112.7318 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50474 | 112.7318 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26888 | 112.8029 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50474 | 112.8029 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26589 | 114.0845 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50069 | 114.0845 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26986 | 112.957 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50599 | 112.957 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26888 | 110.3264 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50474 | 110.3264 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26888 | 110.3956 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50474 | 110.3956 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26589 | 111.649 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50069 | 111.649 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26986 | 110.546 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50599 | 110.546 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | B | 287 | 0.054246 | 100.4042 | Single 515136 SUNNYSD7 345 560088 BISON7 345 1 | Cumulative Impact | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1 | B | 287 | 0.054246 | 100.4042 | Single 515136 SUNNYSD7 345 560088 BISON7 345 1 | Cumulative Impact | Rebuild line 521049 SCLMNJC4 138 784980 G24-267-TAP 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26888 | 112.8143 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50474 | 112.8143 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26888 | 112.8854 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50474 | 112.8854 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26589 | 114.1585 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50069 | 114.1585 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26986 | 113.0384 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50599 | 113.0384 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-132 | TO->FROM | 521157 HUGO 7 345 560088 BISON 7 345 1 | B | 1195 | 1 | 100.0687 | Single 515136 SUNNYSD7 345 560088 BISON7 345 1 | TDF Impact | Rebuild line 521157 HUGO 7 345 560088 BISON 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.076748 | 104.1544 | Single 640139 COOPER3 345 640009 COOPER1G 22 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37633 | 104.1544 | Single 640139 COOPER3 345 640009 COOPER1G 22 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.081967 | 103.5245 | P12:230:WERE:AUBN-JEC-230:HV: | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.41521 | 103.5245 | P12:230:WERE:AUBN-JEC-230:HV: | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.095291 | 102.636 | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37844 | 102.636 | Single 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.075339 | 102.8985 | GEN542962 2 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37492 | 102.8985 | GEN542962 2 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.076748 | 104.1544 | P11:022:NPPD:COOPER1G:1:983:: | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37633 | 104.1544 | P11:022:NPPD:COOPER1G:1:983:: | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.07982 | 102.5403 | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37381 | 102.5403 | Single 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.076748 | 104.423 | GEN640009 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37633 | 104.423 | GEN640009 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.07982 | 102.5239 | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37381 | 102.5239 | Single 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.07982 | 102.5273 | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.37381 | 102.5273 | Single 532768 EMPEC7 345 776400 G23-221-TAP 345 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.10623 | 117.2246 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | Cumulative Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | B | 830 | 0.39141 | 117.2246 | Single 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | Rebuild line 532765 HOYT 7 345 532766 JEC N 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 952 | 0.99622 | 101.3367 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 952 | 0.99622 | 101.5502 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 952 | 0.99622 | 101.5458 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 952 | 0.99622 | 101.3513 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49779 | 113.1198 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49181 | 113.1198 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48053 | 118.5411 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4746 | 118.5411 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.51165 | 121.2833 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.50615 | 121.2833 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 311 | 0.48862 | 114.3655 | System Intact | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 311 | 0.48252 | 114.3655 | System Intact | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49856 | 112.5464 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49233 | 112.5464 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49498 | 116.2934 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48878 | 116.2934 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79492 | 162.6919 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79492 | 162.6919 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49893 | 112.7755 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49269 | 112.7755 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79492 | 165.9291 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79492 | 165.9291 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79492 | 165.9585 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79492 | 165.9585 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48053 | 112.0925 | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4746 | 112.0925 | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.73143 | 171.7989 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.7349 | 171.7989 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 1 | 218.9093 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72513 | 155.836 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72872 | 155.836 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.73143 | 176.16 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.7349 | 176.16 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 223.315 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72513 | 160.1788 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72872 | 160.1788 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.083317 | 138.2277 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.082248 | 138.2277 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13247 | 160.3715 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13076 | 160.3715 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.054645 | 101.9501 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.053992 | 101.9501 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088768 | 121.3028 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087607 | 121.3028 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.056119 | 115.6013 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.055352 | 115.6013 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088128 | 116.6733 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088128 | 116.6733 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.072251 | 134.6244 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.071276 | 134.6244 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088128 | 117.8444 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088128 | 117.8444 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088128 | 117.798 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088128 | 117.798 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.1361 | 164.762 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13434 | 164.762 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.056142 | 104.7411 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.055471 | 104.7411 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | A | 112 | 0.053971 | 100.4612 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | A | 112 | 0.053243 | 100.4612 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.073495 | 136.9339 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.072503 | 136.9339 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.0912 | 124.6237 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090007 | 124.6237 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.057656 | 118.7661 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.056869 | 118.7661 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090542 | 119.8675 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090542 | 119.8675 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090542 | 121.0706 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090542 | 121.0706 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090542 | 121.023 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090542 | 121.023 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51178 | 134.9698 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50555 | 134.9698 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49564 | 140.1447 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.48946 | 140.1447 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.5135 | 134.2214 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50761 | 134.2214 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52682 | 143.9542 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.5211 | 143.9542 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.50327 | 128.821 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.49694 | 128.821 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52561 | 142.1648 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51898 | 142.1648 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82133 | 186.9415 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82133 | 186.9415 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52645 | 142.6687 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51981 | 142.6687 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82133 | 190.3049 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82133 | 190.3049 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82133 | 190.3166 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82133 | 190.3166 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49564 | 134.033 | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.48946 | 134.033 | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60988 | 148.4397 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.59426 | 155.0318 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60201 | 168.662 | Single 548807 BLUVLY-161 161 783151 GEN-2024-206 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.61467 | 149.2525 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.63056 | 161.7651 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60201 | 169.1248 | GEN-2024-206_POI_548807_Generator_outage | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | A | 281 | 0.60201 | 156.5103 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 219.2995 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 223.7808 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 223.766 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.59426 | 148.1463 | Single 541201 SIBLEY7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.094899 | 123.7024 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.093664 | 123.7024 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060472 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5238 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37334 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37334 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5238 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5238 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37334 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37334 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.062712 | 164.3658 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5707 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27585 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27585 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5707 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5707 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27585 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27585 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.067897 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.067859 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.07592 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.079368 | 173.8706 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62866 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32732 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32732 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62866 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62866 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32732 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32732 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056664 | 153.0684 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64307 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64307 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64307 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056286 | 149.3833 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67779 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37076 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37076 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67779 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67779 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37076 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37076 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.10158 | 152.5111 | P42:345:NPPD:BKR-CPR-3310:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61095 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61095 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61095 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.05568 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055625 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.080997 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.075474 | 163.2538 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61095 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61095 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61095 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31254 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.05568 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055625 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.080997 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.075474 | 165.5347 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.62981 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.3284 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.3284 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.62981 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.62981 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.3284 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.3284 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.035731 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.0357 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.055154 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.047249 | 140.5968 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64307 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64307 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64307 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33019 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056286 | 149.3833 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.069437 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5713 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44845 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44845 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5713 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.5713 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44845 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44845 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.085579 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051556 | 190.8152 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.069807 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54525 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.427 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.427 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54525 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54525 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.427 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.427 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.078481 | 184.2931 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28287 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.24234 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.24234 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28287 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28287 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.24234 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.24234 | 103.187 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.056133 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3304 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.28497 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.28497 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3304 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3304 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.28497 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.28497 | 100.6163 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.13739 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.13739 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.13739 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.13841 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.13841 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.13841 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.13739 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.13739 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.13739 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.06047 | 101.4235 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.13841 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.13841 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.13841 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.061958 | 101.9454 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.069291 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.051304 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.051304 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.069291 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.069291 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.051304 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.051304 | 102.2438 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45547 | 104.0861 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45547 | 104.0861 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45547 | 104.0861 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43068 | 102.5428 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43068 | 102.5428 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43068 | 102.5428 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4211 | 115.6339 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4211 | 115.6339 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4211 | 115.6339 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | B | 189 | 0.18224 | 154.4497 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | B | 189 | 0.18224 | 154.4497 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | B | 435 | 0.29489 | 120.368 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | B | 435 | 0.29489 | 120.368 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 124.1936 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 124.1936 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 122.8967 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 122.8967 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36758 | 103.7431 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36758 | 103.7431 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36758 | 103.7431 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36758 | 103.7431 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 119.6815 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 119.6839 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.70517 | 124.3343 | P12:138:OKGE-GRDA:BKRBKR1030:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.70515 | 124.3824 | P12:138:OKGE:BKRBKR0990:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.49291 | 106.3744 | P12:069:STILL:FERGUSN-NORTHTP:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.56995 | 112.0305 | Single 515009 MCELROY4 138 515181 UNVRSTY4 138 1 | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.56995 | 109.4054 | P12:138:OKGE:BKRBKR2030:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.45012 | 104.1072 | P12:138:GRDA:4RAMSEY-KINZEGR4:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.50716 | 113.3337 | Single 512731 NORTHTP4 138 512732 NORTHTP2 69 512739 'NORTAP1 ' 13 1 | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.86639 | 168.7371 | P12:138:GRDA:KINZEGR4-NORTHTP4:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.56995 | 113.0571 | Single 515008 KINZE4 138 515181 UNVRSTY4 138 1 | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 300141 4STILWTR 138 512731 NORTHTP4 138 1 | B | 191 | 0.45012 | 106.6749 | P21:138:GRDA:KINZEGR-19TH ST:::HV: | TDF Impact | Rebuild line 300141 4STILWTR 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 277 | 0.29944 | 105.6658 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 102.3428 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 102.3363 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | TO->FROM | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 101.1416 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.073837 | 102.6586 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.065134 | 102.6586 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.076647 | 104.1334 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.067545 | 104.1334 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.073837 | 100.807 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.065135 | 100.807 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.074866 | 104.21 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.065764 | 104.21 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.073837 | 102.5442 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509048 MURVAULTP 138 509049 MURVAUL4 138 P | B | 233 | 0.065135 | 102.5442 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509048 MURVAULTP 138 509049 MURVAUL4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.073837 | 109.1921 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.065134 | 109.1921 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.076647 | 110.6554 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.067545 | 110.6554 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.073837 | 107.333 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.065135 | 107.333 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.074866 | 110.7322 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.065764 | 110.7322 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.073837 | 109.0759 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 509049 MURVAUL4 138 712002 TENASK4 138 P | B | 233 | 0.065135 | 109.0759 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509049 MURVAUL4 138 712002 TENASK4 138 P
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 112.5476 | Single 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 115.8124 | P42:345:OKGE:SB_REUD7389:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 115.8124 | P42:345:OKGE:SB_REUD7386:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 115.8125 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20948 | 113.9931 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22886 | 113.9931 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.48753 | 113.9931 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.078988 | 113.9931 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079726 | 113.9931 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20909 | 113.7051 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22852 | 113.7051 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.48704 | 113.7051 | 272864 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.078785 | 113.7051 | 272864 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.07952 | 113.7051 | 272864 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.16906 | 129.1811 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.090833 | 129.1811 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.66733 | 129.1811 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20948 | 116.0669 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22886 | 116.0669 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.48753 | 116.0669 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.078988 | 116.0669 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.079726 | 116.0669 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.22016 | 124.9028 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23763 | 124.9028 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.52434 | 124.9028 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.082564 | 124.9028 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.08334 | 124.9028 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | Rebuild line 510907 PITTSB-7 345 515045 SEMINOL7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-247 | TO->FROM | 512710 KINZEGR4 138 512731 NORTHTP4 138 1 | B | 191 | 0.84045 | 161.3788 | P12:138:GRDA:4STILWTR-NORTHTP4:::HV: | TDF Impact | Rebuild line 512710 KINZEGR4 138 512731 NORTHTP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 112.7493 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 112.7465 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.060426 | 113.1788 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.05104 | 113.1788 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.084693 | 113.1788 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-128 | FROM->TO | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.37562 | 108.2719 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.060585 | 108.2719 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-128 | TO->FROM | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.37562 | 108.2719 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | TO->FROM | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.060585 | 108.2719 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26614 | 107.4188 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50094 | 107.4188 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.2691 | 107.5649 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50495 | 107.5649 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.2691 | 107.5007 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50495 | 107.5007 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.27008 | 107.8834 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | TO->FROM | 520560 HUGOITC4 138 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.5062 | 107.8834 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.26614 | 105.1418 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50094 | 105.1418 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.2691 | 105.2844 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50495 | 105.2844 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.2691 | 105.2217 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.50495 | 105.2217 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.27008 | 105.5951 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | B | 478 | 0.5062 | 105.5951 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Rebuild line 520560 HUGOITC4 138 520948 HUGO PP4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.26614 | 107.5294 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50094 | 107.5294 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.2691 | 107.6757 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50495 | 107.6757 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.2691 | 107.6114 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.50495 | 107.6114 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-132 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.27008 | 107.9917 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 521157 HUGO 7 345 3WXFMR 849:525:HUGO 345-138 XFMR 138 1 | B | 478 | 0.5062 | 107.9917 | P12:345:AEPW-WFEC:VALIANT7:HUGO7::: | TDF Impact | Add 3-winding transformer 520560 HUGOITC4 138 521157 HUGO 7 345 521189 HUGO TERTA 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49371 | 118.1518 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48752 | 118.1518 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79255 | 177.1779 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79255 | 177.1779 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49737 | 117.1709 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49172 | 117.1709 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.51043 | 122.3772 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.50494 | 122.3772 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49775 | 115.8028 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49152 | 115.8028 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79255 | 173.9531 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79255 | 173.9531 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.47937 | 116.6608 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.47344 | 116.6608 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 334 | 0.48752 | 110.9052 | System Intact | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 334 | 0.48143 | 110.9052 | System Intact | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48699 | 116.1144 | GEN542951 5 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4809 | 116.1144 | GEN542951 5 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79255 | 177.2062 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79255 | 177.2062 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49672 | 118.5285 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49074 | 118.5285 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.72239 | 155.8711 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.72601 | 155.8711 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 1 | 200.6197 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.72705 | 166.394 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.73058 | 166.394 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.72239 | 159.8953 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.72601 | 159.8953 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 204.675 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.72705 | 170.4241 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.73058 | 170.4241 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 72 | 0.084717 | 107.387 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 72 | 0.08363 | 107.387 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089784 | 103.3206 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088609 | 103.3206 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089544 | 101.8356 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089544 | 101.8356 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.073872 | 108.3311 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.072876 | 108.3311 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13463 | 141.1515 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13289 | 141.1515 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089544 | 100.6856 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089544 | 100.6856 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089544 | 101.797 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089544 | 101.797 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092243 | 106.1492 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091037 | 106.1492 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091997 | 104.6236 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091997 | 104.6236 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13832 | 145.0158 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13653 | 145.0158 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091997 | 103.4421 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091997 | 103.4421 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091997 | 104.5839 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091997 | 104.5839 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.07513 | 110.1639 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.074117 | 110.1639 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81846 | 196.0182 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81846 | 196.0182 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.512 | 133.8021 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50613 | 133.8021 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52527 | 138.5776 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51864 | 138.5776 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52529 | 139.0671 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51959 | 139.0671 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81846 | 192.6826 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81846 | 192.6826 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49419 | 132.7999 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.48803 | 132.7999 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.50188 | 127.3651 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.49556 | 127.3651 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50139 | 132.1639 | GEN542951 5 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49507 | 132.1639 | GEN542951 5 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81846 | 196.0328 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81846 | 196.0328 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52442 | 138.1674 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.5178 | 138.1674 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51041 | 134.4167 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50419 | 134.4167 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 204.3549 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60245 | 143.8518 | GEN-2024-206_POI_548807_Generator_outage | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60245 | 143.4631 | Single 548807 BLUVLY-161 161 783151 GEN-2024-206 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.61503 | 127.524 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.63093 | 133.7175 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 200.2672 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60245 | 124.6352 | Single 783151 GEN-2024-206 161 783166 G24-206GEN5 13 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.59463 | 125.5192 | Single 542972 HAWTH7 345 783480 G24-217-TAP 345 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | A | 334 | 0.60245 | 119.8438 | System Intact | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 204.3469 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.61033 | 126.3035 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Rebuild line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.095588 | 108.0961 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.094343 | 108.0961 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29WP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.070401 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54661 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42813 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42813 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54661 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.54661 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42813 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.42813 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.079161 | 153.2384 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57167 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27668 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27668 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57167 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57167 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27668 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.27668 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.067987 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.067948 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.076247 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.079576 | 146.9522 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056695 | 133.2571 | P13:115-345:NPPD:OLIVECREEK 3:T1::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060857 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.52497 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37428 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37428 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.52497 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.52497 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37428 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.37428 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.063193 | 136.2325 | Single 640277 MOORE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.63051 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32899 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32899 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.63051 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.63051 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32899 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32899 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.036015 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.035983 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.055534 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.04758 | 125.2052 | System Intact | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62935 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32789 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32789 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62935 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.62935 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32789 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32789 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056983 | 136.4086 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61206 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61206 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61206 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056171 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056115 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.081629 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.076031 | 142.0115 | Single 645458 S34583 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056695 | 133.2571 | P13:116-345:NPPD:OLIVECREEK 3:T2::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61206 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61206 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.61206 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.31352 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056171 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056115 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.081629 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.076031 | 141.4534 | Single 640139 COOPER3 345 778170 G24-040-TAP 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64382 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33082 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056695 | 133.2571 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.070134 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57266 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44959 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44959 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57266 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57266 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44959 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.44959 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.086339 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052233 | 160.3375 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | B | 239 | 0.18195 | 125.0229 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1 | B | 239 | 0.18195 | 125.0229 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | Rebuild line 655943 W.BANK.S-MW7 115 655945 WHEELS_T-MW7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | B | 435 | 0.29458 | 127.9484 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659070 W.BANK.S-BE3 345 655943 W.BANK.S-MW7 115 1 | B | 435 | 0.29458 | 127.9484 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 2-winding transformer 655943 W.BANK.S-MW7 115 659070 W.BANK.S-BE3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 112.0967 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 112.0967 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 111.1995 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 111.1995 | Single 659070 W.BANK.S-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36743 | 106.3669 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36743 | 106.3669 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36743 | 106.3669 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36743 | 106.3669 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 109.7481 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 109.7459 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | B | 151 | 0.030024 | 103.867 | Single 509784 A.A.---4 138 786510 G24-318-TAP 138 1 | TDF Impact | Rebuild line 509817 T.NO.--4 138 509900 46ST-TP-4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | B | 151 | 0.066504 | 103.867 | Single 509784 A.A.---4 138 786510 G24-318-TAP 138 1 | TDF Impact | Rebuild line 509817 T.NO.--4 138 509900 46ST-TP-4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035077 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030435 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032587 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033729 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033729 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037091 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033133 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033972 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030435 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030458 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037809 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034019 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033765 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030985 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030379 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034121 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.12721 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039137 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035657 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03413 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034181 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033113 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033113 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032587 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032108 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030865 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030151 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030373 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030385 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03036 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030378 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030463 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.097523 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030924 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037322 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030372 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030062 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03026 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.049929 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030426 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032133 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030329 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035117 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030399 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031507 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036047 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03051 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03051 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032756 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030508 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030353 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035282 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033344 | 125.7821 | Single 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-006 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031822 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.042438 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036456 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034795 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039509 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-050 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033388 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-052 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-063 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034466 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036375 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036767 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035707 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03484 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03455 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034142 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03411 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037873 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040114 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036046 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035784 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040494 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036162 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-153 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033829 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036504 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037257 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034611 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036605 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039973 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-165 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035397 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.041348 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038078 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-184 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030418 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03568 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03498 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040109 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036939 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035236 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-232 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031302 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033213 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037913 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036845 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-250 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036182 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036392 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036404 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-267 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034891 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035711 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036378 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035635 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036394 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036473 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.12299 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0369 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039704 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036391 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036099 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034656 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036282 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.054354 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-324 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035779 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-325 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035897 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032127 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036444 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038013 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035863 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037522 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036414 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037465 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.04239 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036205 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-364 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039227 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-368 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032224 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037941 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036373 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-376 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030008 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03771 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035163 | 119.5374 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-006 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031822 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.042438 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036456 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034795 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039509 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-050 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033388 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-052 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-063 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034466 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036375 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036767 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035707 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03484 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03455 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034142 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03411 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037873 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040114 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036046 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035784 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040494 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036162 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-153 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033829 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036504 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037257 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034611 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036605 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039973 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-165 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035397 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.041348 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038078 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-184 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030418 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03568 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03498 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040109 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036939 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035236 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-232 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031302 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033213 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037913 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036845 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-250 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036182 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036392 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036404 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-267 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034891 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035711 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036378 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035635 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036394 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036473 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0369 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039704 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036391 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036099 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034656 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036282 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.054354 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-324 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035779 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-325 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035897 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032127 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036444 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038013 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035863 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037522 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036414 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037465 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.04239 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036205 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-364 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039227 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-368 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032224 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037941 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036373 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-376 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030008 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03771 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035163 | 117.9768 | Single 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030179 | 107.9307 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-250 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030805 | 107.9307 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.063737 | 107.9307 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038035 | 107.9307 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030805 | 107.9307 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | A | 493 | 0.064046 | 102.2489 | System Intact | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | A | 493 | 0.037149 | 102.2489 | System Intact | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-006 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031822 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.042438 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036456 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034795 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039509 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-050 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033388 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-052 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-063 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034466 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036375 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036767 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035707 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03484 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03455 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034142 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03411 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037873 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040114 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036046 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035784 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040494 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036162 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-153 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033829 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036504 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037257 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034611 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036605 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039973 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-165 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035397 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.041348 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038078 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-184 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030418 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03568 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03498 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040109 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036939 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035236 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-232 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031302 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033213 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037913 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036845 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-250 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036182 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036392 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036404 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-267 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034891 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035711 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036378 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035635 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036394 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036473 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.12299 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0369 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039704 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036391 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036099 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034656 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036282 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.054354 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-324 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035779 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-325 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035897 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032127 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036444 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038013 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035863 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037522 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036414 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037465 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.04239 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036205 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-364 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039227 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-368 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032224 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037941 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036373 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-376 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030008 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03771 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035163 | 131.2898 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-006 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031822 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.042438 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036456 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034795 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039509 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-050 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033388 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-052 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-063 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034466 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036375 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036767 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035707 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03484 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03455 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034142 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03411 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037873 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040114 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036046 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035784 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040494 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036162 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-153 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033829 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036504 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037257 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034611 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036605 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039973 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-165 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035397 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.041348 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038078 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-184 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030418 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03568 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03498 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040109 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036939 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035236 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-232 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031302 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033213 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037913 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036845 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-250 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036182 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036392 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036404 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-267 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034891 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035711 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036378 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035635 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036394 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036473 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.12299 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0369 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039704 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036391 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036099 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034656 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036282 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.054354 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-324 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035779 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-325 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035897 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032127 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036444 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038013 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035863 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037522 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036414 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037465 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.04239 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036205 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-364 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039227 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-368 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032224 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037941 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036373 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-376 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030008 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03771 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035163 | 129.0993 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035077 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030435 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032587 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033729 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033729 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037091 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033133 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033972 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030435 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030458 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037809 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034019 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033765 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030985 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030379 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034121 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039137 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035657 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03413 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034181 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033113 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033113 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032587 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032108 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030865 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030151 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030373 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030385 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03036 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030378 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030463 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.097523 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030924 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037322 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030372 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030062 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03026 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.049929 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030426 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032133 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030329 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035117 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030399 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031507 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036047 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03051 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03051 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032756 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030508 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030353 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035282 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033344 | 119.7736 | Single 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030729 | 109.4219 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.063786 | 109.4219 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038651 | 109.4219 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-006 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031822 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.042438 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036456 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039553 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034795 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039509 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-050 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033388 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-052 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-063 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034466 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036375 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036767 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035707 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035118 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-083 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03484 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03455 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034142 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03411 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037873 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040114 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036046 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035784 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040494 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036162 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030274 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-153 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033829 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036504 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037257 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034611 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036605 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039973 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-165 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035397 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.041348 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038078 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-184 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030418 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03568 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03498 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.040109 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036939 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035236 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-226 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-227 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033919 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039332 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-232 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031302 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033213 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035962 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037913 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036845 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-250 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036182 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034425 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030793 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036392 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036404 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-267 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034891 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035711 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036378 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035635 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036394 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036473 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.12299 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0369 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034878 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039704 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036391 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036099 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-316 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034656 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036282 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.054354 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-324 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035779 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-325 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035789 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035897 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032127 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036444 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038013 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035863 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033842 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037522 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036414 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037465 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.04239 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036205 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-364 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031685 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036523 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.039227 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-368 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032224 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.037941 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.036373 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034604 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-376 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030008 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03771 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035163 | 131.0843 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031174 | 109.9323 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.064318 | 109.9323 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.038933 | 109.9323 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11052 | 103.6286 | P12:138:OKGE:BKRBKR1320:::HV: | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.040826 | 103.6286 | P12:138:OKGE:BKRBKR1320:::HV: | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11052 | 107.2622 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.040826 | 107.2622 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11052 | 102.579 | Single 514893 XEROX4 138 514894 CZECHAL4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.040826 | 102.579 | Single 514893 XEROX4 138 514894 CZECHAL4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11052 | 102.2489 | Single 514893 XEROX4 138 514896 MORGAN4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.040826 | 102.2489 | Single 514893 XEROX4 138 514896 MORGAN4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.10762 | 104.9767 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.036835 | 104.9767 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.079793 | 100.5543 | Single 514876 SW134TP4 138 514887 WESTMOR4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.075612 | 104.3782 | Single 514853 DVISION4 138 514861 MUSTANG4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.075612 | 104.5717 | P12:138:OKGE:BKRBKR1250:::HV: | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.10762 | 100.5407 | Single 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.036835 | 100.5407 | Single 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.10762 | 103.0526 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.036835 | 103.0526 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.10762 | 100.5563 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-369 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.036835 | 100.5563 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.075612 | 100.1641 | Single 514853 DVISION4 138 514861 MUSTANG4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.075612 | 100.3416 | P12:138:OKGE:BKRBKR1250:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | TO->FROM | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.062873 | 104.2229 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | TO->FROM | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.062873 | 104.2229 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | TO->FROM | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.039044 | 104.2229 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.062873 | 108.2023 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.062873 | 108.2023 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.039044 | 108.2023 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | TO->FROM | 514925 PENN 4 138 514926 SANTAFE4 138 1 | B | 191 | 0.12317 | 116.1264 | Single 514876 SW134TP4 138 514887 WESTMOR4 138 1 | TDF Impact | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | TO->FROM | 514925 PENN 4 138 514926 SANTAFE4 138 1 | B | 191 | 0.12322 | 105.1735 | 272052 | TDF Impact | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | TO->FROM | 514925 PENN 4 138 514926 SANTAFE4 138 1 | B | 191 | 0.12317 | 104.4993 | 272053 | TDF Impact | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | TO->FROM | 514925 PENN 4 138 514926 SANTAFE4 138 1 | B | 191 | 0.12317 | 104.4993 | Single 514887 WESTMOR4 138 514925 PENN4 138 1 | TDF Impact | Rebuild line 514925 PENN 4 138 514926 SANTAFE4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | B | 267 | 0.032472 | 100.0165 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | B | 267 | 0.046692 | 100.0165 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | B | 267 | 0.46381 | 100.0165 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | B | 267 | 0.032477 | 100.3872 | Single 514933 DRAPER4 138 515003 BARNES4 138 1 | TDF Impact | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-119 | FROM->TO | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | B | 267 | 0.046698 | 100.3872 | Single 514933 DRAPER4 138 515003 BARNES4 138 1 | TDF Impact | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-332 | FROM->TO | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | B | 267 | 0.46386 | 100.3872 | Single 514933 DRAPER4 138 515003 BARNES4 138 1 | TDF Impact | Rebuild line 514959 FOSTER 4 138 515387 NEWDOMI4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-164 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.05095 | 103.9043 | P12:138:OKGE:BKRBKR2170:::HV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.04916 | 103.9043 | P12:138:OKGE:BKRBKR2170:::HV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.3378 | 103.9043 | P12:138:OKGE:BKRBKR2170:::HV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.040636 | 106.8401 | Single 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.066328 | 121.5317 | Single 528626 LE-PLNSINT2 69 528709 LE-PLNSGOAB2 69 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.040636 | 123.5295 | Single 527864 CUNNINHAM3 115 528348 BUCKEYE_TP3 115 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.040636 | 117.8159 | Single 528348 BUCKEYE_TP3 115 528627 LE-TXACO_TP3 115 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.040636 | 106.9601 | P12:115:SPS:V98.1.CUNN.LE-SNANDR:::HV: | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.040636 | 106.8401 | Single 528622 LE-SANANDRS2 69 528341 LE-SANANDRS3 115 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.032028 | 109.9248 | P12:069:OPPD:W BROCK-S963:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.035816 | 109.9248 | P12:069:OPPD:W BROCK-S963:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.044395 | 114.2433 | Single 646263 S12635 161 647111 WBROCK8 69 648263 'S1263T19 ' 13 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.047724 | 114.2433 | Single 646263 S12635 161 647111 WBROCK8 69 648263 'S1263T19 ' 13 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.17591 | 103.6747 | Single 646280 S12805 161 778140 G24-039-TAP 161 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.14221 | 103.6747 | Single 646280 S12805 161 778140 G24-039-TAP 161 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.03493 | 113.5845 | P13:069-161:OPPD:S1263 T1:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.037692 | 113.5845 | P13:069-161:OPPD:S1263 T1:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-038 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.045799 | 127.5765 | P12:161:OPPD:S1263-S1280:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.067421 | 127.5765 | P12:161:OPPD:S1263-S1280:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | FROM->TO | 640234 HUMBOLT5 161 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.068889 | 127.5765 | P12:161:OPPD:S1263-S1280:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-016 | TO->FROM | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | B | 128 | 0.040054 | 108.2004 | Single 640066 AXTELL7 115 640250 KEARNEY7 115 1 | TDF Impact | Rebuild line 640261 LOWELL 7 115 640275 MINDEN 7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.032028 | 108.4754 | P12:069:OPPD:W BROCK-S963:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.035816 | 108.4754 | P12:069:OPPD:W BROCK-S963:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.044395 | 113.2048 | Single 646263 S12635 161 647111 WBROCK8 69 648263 'S1263T19 ' 13 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.047724 | 113.2048 | Single 646263 S12635 161 647111 WBROCK8 69 648263 'S1263T19 ' 13 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.17591 | 103.6632 | Single 646280 S12805 161 778140 G24-039-TAP 161 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.14221 | 103.6632 | Single 646280 S12805 161 778140 G24-039-TAP 161 1 | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.03493 | 112.0667 | P13:069-161:OPPD:S1263 T1:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.037692 | 112.0667 | P13:069-161:OPPD:S1263 T1:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-038 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.045799 | 126.9703 | P12:161:OPPD:S1263-S1280:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-039 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.067421 | 126.9703 | P12:161:OPPD:S1263-S1280:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-231 | TO->FROM | 647975 S975 8 69 3WXFMR 645:S975 T4 69 1 | B | 67.2 | 0.068889 | 126.9703 | P12:161:OPPD:S1263-S1280:::HV: | TDF Impact | Rebuild 3-winding transformer 640234 HUMBOLT5 161 647975 S975 8 69 648275 S975T4 9 13 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-216 | TO->FROM | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.034235 | 147.0496 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-326 | TO->FROM | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.03574 | 147.0496 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-328 | TO->FROM | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.034883 | 147.0496 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-359 | TO->FROM | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.031258 | 147.0496 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-372 | TO->FROM | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | A | 600 | 0.032729 | 104.6808 | System Intact | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-372 | FROM->TO | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | A | 600 | 0.032729 | 104.6217 | System Intact | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-216 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.034235 | 148.3193 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-326 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.03574 | 148.3193 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-328 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.034883 | 148.3193 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-359 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | B | 119 | 0.031258 | 148.3193 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-216 | TO->FROM | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | B | 120 | 0.034235 | 147.864 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-326 | TO->FROM | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | B | 120 | 0.03574 | 147.864 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-328 | TO->FROM | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | B | 120 | 0.034883 | 147.864 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-359 | TO->FROM | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | B | 120 | 0.031258 | 147.864 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | TDF Impact | Rebuild line 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-069 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | B | 84 | 0.034769 | 102.2131 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | TDF Impact | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-091 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | B | 84 | 0.038042 | 102.2131 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | TDF Impact | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | B | 84 | 0.048255 | 102.2131 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | TDF Impact | Add 3-winding transformer 505487 CRG X1 1 13 505488 CARTHAG5 161 505490 CARTHG 2 69 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-069 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | B | 84 | 0.034531 | 101.605 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | TDF Impact | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-091 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | B | 84 | 0.037781 | 101.605 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | TDF Impact | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | B | 84 | 0.047925 | 101.605 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | TDF Impact | Add 3-winding transformer 505488 CARTHAG5 161 505489 CRG X2 1 13 505490 CARTHG 2 69 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035644 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031705 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030311 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034545 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034545 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030334 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033716 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030713 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031177 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031119 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030581 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030581 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030075 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031984 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034287 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030682 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031185 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034703 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0303 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031253 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031871 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030129 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031336 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033635 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031358 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035415 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032433 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031184 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03012 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033767 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03134 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030716 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033709 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033709 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030311 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031833 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032117 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03153 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031692 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031699 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03111 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031701 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031059 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-280 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031698 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031773 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.1496 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-295 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032166 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030408 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030408 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-305 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033899 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-306 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031693 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-311 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031456 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031219 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-321 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.043939 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-324 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031175 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-325 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031184 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-332 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030456 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-336 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031719 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-337 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03194 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031938 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-351 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03172 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-355 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032512 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-360 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035911 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-362 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030961 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-365 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031793 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-366 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031793 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-367 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033478 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-369 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032372 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-371 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031683 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032102 | 105.1494 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-013 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035644 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-015 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031705 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-025 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030311 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034545 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034545 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030334 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-044 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033716 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-068 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030713 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-071 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031177 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-073 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031119 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-079 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030581 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-080 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030581 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-092 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030075 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-119 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031984 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-122 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034287 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-123 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030682 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-124 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031185 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.034703 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-132 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.0303 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-157 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031253 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-158 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031871 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-159 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030129 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-161 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031336 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-164 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033635 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031358 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-177 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.035415 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-178 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032433 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-186 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031184 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-187 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03012 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-219 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033767 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-220 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03134 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030716 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-229 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033709 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-230 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.033709 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-241 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.030311 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-242 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031833 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-246 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.032117 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-251 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03153 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031692 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-265 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031699 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-271 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.03111 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-273 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031701 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-278 | FROM->TO | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | B | 493 | 0.031059 | 123.0977 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Add 2-winding transformer 509915 ANTHEM7 345 510442 GUAVA 4 138 M2