## Executive Summary
Executive Summary: GEN-2024-292 Interim Availability Interconnection System Impact Study
Interconnection Customer (GEN-2024-292) has requested an Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Seasonal LOIS Tab.
Study Limitations
Interim Availability Interconnection Service Available between April 1 - May 31 : 1481.04 MW
Interim Availability Interconnection Service Available between June 1 - Sept 30 : 1481.04 MW
Interim Availability Interconnection Service Available between Oct 1 - Nov 30 : 1481.04 MW
Interim Availability Interconnection Service Available between Dec 1 - March 31 : 1481.04 MW
In the event that an Interconnection Request, with queue priority equal to or higher than an Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
The study has been performed excluding upgrades that are not expected to be in service by the request's COD (10/24/2025). SPP's 2Q 2025 Quarterly Project Tracking Report has been used to determine the upgrades meeting the criteria for exclusion.
DISIS Manual Version 4.1
https://www.spp.org/media/2360/gi-manual-business-practice-7250-20250715.pdf
2Q 2025 Quraterly Tracking Report
2Q 2025 Quarterly Project Tracking Report
Models Used in Study
Power Flow Analysis: DISIS-2021-001 Phase 2 (2022 ITP Series)* * modified to exclude network upgrades assigned through DISIS-1701, DISIS-1702, DISIS-1801,DISIS-2018-002/DISIS-2019-001, and DISIS-2020. The model excludes any upgrades from DISIS-2021-001.
Summer: 2024 (24SP), 2027 (27SP)
Winter: 2027 (27WP)
Stability Analysis: DISIS-2021-001 Phase 2 (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1701, DISIS-1702, DISIS-1801,DISIS-2018-002/DISIS-2019-001, and DISIS-2020. The model excludes any upgrades from DISIS-2021-001.
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2021-001 Phase 2 (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1701, DISIS-1702, DISIS-1801,DISIS-2018-002/DISIS-2019-001, and DISIS-2020. The model excludes any upgrades from DISIS-2021-001.
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 8/28/2025

## Revision History
Revision History
Date | Author | Change Description
2025-08-28 | SPP

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status | Notes
GEN-2024-292 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1481.04 | 1481.04 | 1481.04 | 1481.04 | 1481.04 | 1481.04 | 1481.04 | 1481.04 | 1481.04 | 0 | ER | OKGE | Redbud 345 kV Substation | DISIS STAGE | The 1481.04 MW includes the uprate as well as the existing capability of Rosebud. The 1481.04 MW is based on latest submitted models by the customer.
ASGI-2024-001 | 03 CENTRAL | 26 | DIS-22-1 | Gas | 15 | [9 empty] | ER | BEPC-SPP | FARM_TAP8 69 kV | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEP | Fitzhugh 161kV | DISIS STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal: CTG | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | [9 empty] | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | DISIS STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | DISIS STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | DISIS STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | DISIS STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | DISIS STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | DISIS STAGE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | NPPD | Antelope 345kV substation | DISIS STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | DISIS STAGE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | [9 empty] | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | DISIS STAGE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | DISIS STAGE
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | DISIS STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | DISIS STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | DISIS STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | INDN | Independence Power & Light, Blue Valley Substation, 161kV Bus | DISIS STAGE
GEN-2021-050 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 200 | [9 empty] | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-051 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | DISIS STAGE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER/NR | MIDW | ITC Post Rock 345 kV Substation | DISIS STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Hybrid: Solar and Storage | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | DISIS STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | DISIS STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | DISIS STAGE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | DISIS STAGE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | DISIS STAGE
GEN-2021-015 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 74.9 | [9 empty] | ER | OKGE | Bobcat 345 kV interconnection substation | DISIS STAGE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEP | Sunnyside-Johnston 345 kV | DISIS STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Grand Prairie 161kV Substation | DISIS STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEP | Craig to Patterson 138 kV Transmission Line | DISIS STAGE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEP | Welsh 345kV Substation | DISIS STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | DISIS STAGE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | DISIS STAGE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | DISIS STAGE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 155 | [9 empty] | ER/NR | AEP | Craig JCT 138kV | DISIS STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 100 | [9 empty] | ER/NR | AEP | Carnegie South 138kV | DISIS STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | DISIS STAGE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | SOLAR/BATTERY/STORAGE | 75 | [9 empty] | ER/NR | SPS |  | DISIS STAGE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | SOLAR/BATTERY/STORAGE | 60 | [9 empty] | ER/NR | SPS |  | DISIS STAGE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
J1519 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | St. Francois to Lutesville 345 kV | Active: Phase 2
J1649 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 60 | [9 empty] | ER/NR | BREC | McCracken County to Shell 69kV | Active: Phase 2
J1836 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery- Callaway- 7 | Active: Phase 2
GIA-116 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | THERMAL | 26 | [9 empty] | ER/NR | AECI
GIA-117 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | THERMAL | 46 | [9 empty] | ER/NR | AECI
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [9 empty] | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | [9 empty] | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [9 empty] | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [9 empty] | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | DISIS STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | SOLAR/BATTERY/STORAGE | 45 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | SOLAR/BATTERY/STORAGE | 45 | [9 empty] | ER | KCPL |  | DISIS STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | WERE | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | WERE | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [9 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | DISIS STAGE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [9 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [9 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | DISIS STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [9 empty] | ER/NR | AEP | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEP | Lydia 345 kV Station | DISIS STAGE
GEN-2020-074 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEP | Lawton to Sunnyside 345 kV Substation | DISIS STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEP | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-085 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEP | Lawton to Sunnyside 345 kV Line | DISIS STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEP | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEP | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-068 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 400 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid: Storage and Wind | 110 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEP | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEP | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEP | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [9 empty] | ER/NR | AEP | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [9 empty] | ER | AEP | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | BEPC | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA PENDING
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA PENDING
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA PENDING
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | INDN | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [9 empty] | ER | WERE | Neosho 345kV Substation | FACILITY STUDY STAGE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEP | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA PENDING
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [9 empty] | ER/NR | AEP | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEP | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEP | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEP | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEP | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA PENDING
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done: Phase 3
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done: Phase 3
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | Done: Phase 3
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done: Phase 3
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | Done: Phase 3
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | Done: Phase 3
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | Done: Phase 3
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Active: Phase 3
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | Done: Phase 3
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done: Phase 3
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Magnolia 161 kV substation | Done: Phase 3
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | Done: Phase 3
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done: Phase 3
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Active: Phase 3
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Active: Phase 3
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Active: Phase 3
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | Active: Phase 3
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | Active: Phase 3
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Active: Phase 3
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Active: Phase 3
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | Active: Phase 3
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | Active: Phase 3
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | Active: Phase 3
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 174 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | Active: Phase 3
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Pipestone to Split Rock 115kV | Active: Phase 3
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Active: Phase 3
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Active: Phase 3
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 120 | [9 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Active: Phase 3
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | DPC | Barron 161 kV | Active: Phase 3
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done: Phase 3
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL | Adams 345kV Substation | Done: Phase 3
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 170 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 130 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 300 | [9 empty] | ER/NR | OTP
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done: Phase 3
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done: Phase 3
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done: Phase 3
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done: Phase 3
J1181 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done: Phase 3
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done: Phase 3
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done: Phase 3
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Active: Phase 3
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW | Traer 161-kV Substation | Active: Phase 3
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Active: Phase 3
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | Active: Phase 3
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Active: Phase 3
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Active: Phase 3
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Active: Phase 3
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | Active: Phase 3
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done: Phase 3
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done: GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 400 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done: GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done: GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done: GIA
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Active
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Active
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Active
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Active
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Active
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done: GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done: GIA
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Montgomery 161kV Substation | Done: GIA
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Guthrie 161 kV Substation | Done: GIA
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | [9 empty] | ER | AECI
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done: GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done: GIA
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done: GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 500 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done: GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done: GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done: GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done: GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done: GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done: Phase 3
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done: Phase 3
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | Done: Phase 3
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: Phase 3
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done: Phase 3
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done: Phase 3
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done: Phase 3
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: Phase 3
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done: Phase 3
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done: Phase 3
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | Done: Phase 3
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done: Phase 3
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done: Phase 3
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | Active: Phase 3
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Active: Phase 3
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Active: Phase 3
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Active: Phase 3
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | Done: Phase 3
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES | Goos Ferry | Active: Phase 3
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Active: Phase 3
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Active: Phase 3
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Active: Phase 3
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Active: Phase 3
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Active: Phase 3
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Active: Phase 3
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Active: Phase 3
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Active: Phase 3
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | Active: Phase 3
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Active: Phase 3
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | Active: Phase 3
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Active: Phase 3
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Active: Phase 3
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | Active: Phase 3
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Active: Phase 3
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | Active: Phase 3
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [9 empty] | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEP | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEP | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEP | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEP | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEP | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation | Done: Phase 3
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation | Done: Phase 3
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Done: Phase 3
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: Phase 3
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: Phase 3
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: Phase 3
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation | Done: Phase 3
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: Phase 3
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEP | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | AEP | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEP | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEP | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEP | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEP | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | Done: GIA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | Done: GIA
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEP | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEP | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEP | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEP | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEP | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEP | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | WIND | 100 | [9 empty] | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | WIND | 246 | [9 empty] | ER/NR | AMMO
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEP | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 169.2 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 10.3 | [9 empty] | ER | AEP | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 16 | [9 empty] | ER/NR | BEPC
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 34 | [9 empty] | ER/NR | BEPC
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV | 0
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV | 0
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV | NONE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEP | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 SOUTHWEST | 8 | PQ | Thermal: Gas | 604 | [9 empty] | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | [9 empty] | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27L | ERIS 27WP | NRIS 24SP | NRIS 27SP | NRIS 27L | NRIS 27WP | Stability 25SP | Stability 25WP
GEN-2024-292 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 1481.04 | 1481.04 | None | None | N/A | 1481.04 | N/A | 1481.04 | N/A | N/A | N/A | N/A | 1481.04 | 1481.04
GEN-2024-292 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 1481.04 | 1481.04 | None | None | 1481.04 | N/A | N/A | 1481.04 | N/A | N/A | N/A | N/A | 1481.04 | 1481.04
GEN-2024-292 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 1481.04 | 1481.04 | None | None | N/A | N/A | N/A | 1481.04 | N/A | N/A | N/A | N/A | N/A | 1481.04
GEN-2024-292 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 1481.04 | 1481.04 | None | None | N/A | N/A | N/A | 1481.04 | N/A | N/A | N/A | N/A | N/A | 1481.04
GEN-2024-292 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 1481.04 | 1481.04 | None | None | N/A | 1481.04 | N/A | N/A | N/A | N/A | N/A | N/A | 1481.04 | N/A
GEN-2024-292 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 1481.04 | 1481.04 | None | None | 1481.04 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1481.04 | N/A
GEN-2024-292 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 1481.04 | 1481.04 | None | None | N/A | 1481.04 | N/A | 1481.04 | N/A | N/A | N/A | N/A | 1481.04 | 1481.04
GEN-2024-292 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 1481.04 | 1481.04 | None | None | 1481.04 | N/A | N/A | 1481.04 | N/A | N/A | N/A | N/A | 1481.04 | 1481.04

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | GEN-2024-292 Interim Study | ERIS | Thermal | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | GEN-2024-292 Interim Study | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | GEN-2024-292 Interim Study | ERIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | GEN-2024-292 Interim Study | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2024-292 Interim Study | 00ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None | N/A | None
Thermal | GEN-2024-292 Interim Study | 00ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None | N/A | None
Thermal | GEN-2024-292 Interim Study | 00ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None | N/A | None
Non-Converge | GEN-2024-292 Interim Study | 00ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None | N/A | None
Non-Converge | GEN-2024-292 Interim Study | 00ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None | N/A | None
Non-Converge | GEN-2024-292 Interim Study | 00ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None | N/A | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2024-292 Interim Study | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2024-292 Interim Study | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2024-292 Interim Study | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on DAWSONT4 138.00 (509803) 138 kV Bus a. Apply fault at the DAWSONT4 138.00 (509803) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.3. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.4. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 b.5. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.6. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.7. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on 77MEM-W4 138.00 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 138.00 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 (509766) 138.0 kV to E.61ST-4 (509831) 138.0 kV Transmission Circuit #1 b.2. 77MEM-W4 (509766) 138.0 kV to 96YALE-4 (509847) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on 136YALE4 138.00 (509775) 138 kV Bus a. Apply fault at the 136YALE4 138.00 (509775) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 (509775) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.2. 136YALE4 (509775) 138.0 kV to KIMCLRK4 (509845) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on EC.HEN-4 138.00 (510923) 138 kV Bus a. Apply fault at the EC.HEN-4 138.00 (510923) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV to EC.HEN-4 (510923) 138.0 kV Transmission Circuit #1 b.2. WELETK4 (510902) 138.0 kV to EC.HEN-4 (510923) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-082 (763134,763137). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on EXPGLNT4 138.00 (515473) 138 kV Bus a. Apply fault at the EXPGLNT4 138.00 (515473) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 b.2. BEELINE4 (515247) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 b.3. EXPLGLN4 (515248) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G17-150 (761232), BCVI_WTG1 (520522), G18-055 (762903), G17-173 ( 760979), G17-172 (760958), G17-171 (760937), MNCO5G (515986, 515984, 515985, 515969, 515968, 515967), RKYRDGW1 (511970, 511971), MAJSTC-WT ( 523941, 523942) and CB_WTG (585423, 585426) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to KINZE 4 (515008) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.5. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.4. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.6. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.7. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on BURGETT4 138.00 (514510) 138 kV Bus a. Apply fault at the BURGETT4 138.00 (514510) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 (514510) 138.0 kV to DANFRTH4 (514833) 138.0 kV Transmission Circuit #1 b.2. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on LGARBER4 138.00 (515465) 138 kV Bus a. Apply fault at the LGARBER4 138.00 (515465) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONESSB4 (515480) 138.0 kV to CHTWOOD4 (514842) 138.0 kV Transmission Circuit # b.2. CHTWOOD4 (514842) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on NE10TH 4 138.00 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 138.00 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to MIDWAY 4 (514966) 138.0 kV Transmission Circuit #1 b.2. NE10TH 4 (514964) 138.0 kV to MIDWAY 4 (514966) 138.0 kV Transmission Circuit #1 b.3. NE10TH 4 (514964) 138.0 kV to RENO 4 (514973) 138.0 kV Transmission Circuit #1 b.4. NE10TH 4 (514964) 138.0 kV to GLENDAL4 (514986) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on DUNJEE 4 138.00 (514884) 138 kV Bus a. Apply fault at the DUNJEE 4 138.00 (514884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 (514884) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 b.2. DUNJEE 4 (514884) 138.0 kV to RENO 4 (514973) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on HSL 4 138.00 (514941) 138 kV Bus a. Apply fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to SE15TH 4 (514993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on HAMMTAP4 138.00 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 138.00 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to HAMMTAP4 (515046) 138.0 kV Transmission Circuit #1 b.2. HAMMTAP4 (515046) 138.0 kV to LINCOLN4 (515442) 138.0 kV Transmission Circuit #1 b.3. HAMMTAP4 (515046) 138.0 kV to HAMMETT4 (520951) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on SQUIRCK4 138.00 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 138.00 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to DALE 4 (514987) 138.0 kV Transmission Circuit #1 b.2. DALE 4 (514987) 138.0 kV to SQUIRCK4 (515059) 138.0 kV Transmission Circuit #1 b.3. SQUIRCK4 (515059) 138.0 kV to INGLEWD4 (515060) 138.0 kV Transmission Circuit #1 b.4. SQUIRCK4 (515059) 138.0 kV to STRLGTP4 (515286) 138.0 kV Transmission Circuit #1 b.5. FRSTHIL4 (515075) 138.0 kV to STRLGTP4 (515286) 138.0 kV Transmission Circuit #1 b.6. STRLGTP4 (515286) 138.0 kV to STERLNG4 (520449) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on 5TRIBES5 161.00 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 161.00 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 (515228) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on AGENCY 5 161.00 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 161.00 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 (515230) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on 4MEMORALT 138.00 (300136) 138 kV Bus a. Apply fault at the 4MEMORALT 138.00 (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER (300135) 138.0 kV to 4MEMORALT (300136) 138.0 kV Transmission Circuit #1 b.2. 4MEMORALT (300136) 138.0 kV to JNSKAMO4 (514906) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on HSL 4 138.00 (514941) 138 kV Bus a. Apply fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 (514937) 69.0 kV to HSL 4 (514941) 138.0 kV to HSL 1 (515731) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020-GEN1 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on PECANCK7 345.00 (515235) 345 kV Bus a. Apply fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on PECANCK7 345.00 (515235) 345 kV Bus a. Apply fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on 4MEMORALT 138.00 (300136) 138 kV Bus a. Apply fault at the 4MEMORALT 138.00 (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT (300136) 138.0 kV to 4MEMORAL (301541) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on ORU W4 138.00 (509732) 138 kV Bus a. Apply fault at the ORU W4 138.00 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 (509732) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on ORU E4 138.00 (509738) 138 kV Bus a. Apply fault at the ORU E4 138.00 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 (509738) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on 116JENK4 138.00 (509753) 138 kV Bus a. Apply fault at the 116JENK4 138.00 (509753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 (509753) 138.0 kV to JENKS--4 (509759) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on 116JENK4 138.00 (509753) 138 kV Bus a. Apply fault at the 116JENK4 138.00 (509753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 (509753) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on JENKS--4 138.00 (509759) 138 kV Bus a. Apply fault at the JENKS--4 138.00 (509759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 (509759) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on BA101ST4 138.00 (509768) 138 kV Bus a. Apply fault at the BA101ST4 138.00 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 (509768) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on BA101-N4 138.00 (509769) 138 kV Bus a. Apply fault at the BA101-N4 138.00 (509769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 (509769) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on RSS T1 4 138.00 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 138.00 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to 52DELWT4 (509814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to RSS T2 4 (509875) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to OKMULGE4 (510898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on T.P.S.-4 138.00 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 138.00 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 (509788) 138.0 kV to 52DELWT4 (509814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-027 (762628) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on T.P.S.-4 138.00 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 138.00 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 (509788) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-027 (762628) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on 81YALES4 138.00 (509810) 138 kV Bus a. Apply fault at the 81YALES4 138.00 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 (509810) 138.0 kV to WAREN-W4 (509857) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on 81YALES4 138.00 (509810) 138 kV Bus a. Apply fault at the 81YALES4 138.00 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 (509810) 138.0 kV to WARNTAP4 (509858) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on SHILETP4 138.00 (509813) 138 kV Bus a. Apply fault at the SHILETP4 138.00 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 (509813) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on 52DELWT4 138.00 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 138.00 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 (509814) 138.0 kV to S HILLW4 (509859) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on OAKS--E4 138.00 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 138.00 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 (509846) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on 96YALE-4 138.00 (509847) 138 kV Bus a. Apply fault at the 96YALE-4 138.00 (509847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 (509847) 138.0 kV to WARNTAP4 (509858) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on OAKSWTP4 138.00 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 138.00 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 (509848) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on ORU ETP4 138.00 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 138.00 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 (509849) 138.0 kV to WARNTAP4 (509858) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on SAPLPRD4 138.00 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 138.00 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to 72ELWOD4 (509888) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on SAPLPRD4 138.00 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 138.00 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to DENV_WTAP4 (509896) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV to KELCO 4 (510931) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to G16-119-TAP (587804) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G16-119 (587953, 587958) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on HSL 4 138.00 (514941) 138 kV Bus a. Apply fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to JONESSB4 (515480) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on HSL345 345.00 (599143) 345 kV Bus a. Apply fault at the HSL345 345.00 (599143) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HSL345 (599143) 345.0 kV to HSL 4 (514941) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO21 (515757) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on PECANCK5 161.00 (515234) 161 kV Bus a. Apply fault at the PECANCK5 161.00 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to PECANCK5 (515234) 161.0 kV to PECANC31 (515750) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on ORU E4 138.00 (509738) 138 kV Bus a. Apply fault at the ORU E4 138.00 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 (509738) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on 77MEM-W4 138.00 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 138.00 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 (509766) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on G16133G16146345.00 (588039) 345 kV Bus a. Apply fault at the G16133G16146345.00 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 (588039) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on G16133_765GS765.00 (588041) 765 kV Bus a. Apply fault at the G16133_765GS765.00 (588041) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133_765GS (588041) 765.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on G16133_765MP765.00 (588043) 765 kV Bus a. Apply fault at the G16133_765MP765.00 (588043) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133_765MP (588043) 765.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CB_WTG1 (585423) and CB_WTG2 (585426) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CB_WTG1 (585423) and CB_WTG2 (585426) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to GI106_POI (999700) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-092-PROX (763215) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CB_WTG1 (585423) and CB_WTG2 (585426) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply Fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to OKMULGE4 (510898) 138.0 kV Transmission Circuit #1 b.2. OKMULGE4 (510898) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 b.3. OKMULGE4 (510898) 138.0 kV to EC.HEN-4 (510923) 138.0 kV Transmission Circuit #1 b.4. OKMULGE4 (510898) 138.0 kV to KELCO 4 (510931) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on KIMCLRK4 138.00 (509845) 138 kV Bus a. Apply Fault at the KIMCLRK4 138.00 (509845) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. B111---4 (509767) 138.0 kV to KIMCLRK4 (509845) 138.0 kV Transmission Circuit #1 b.2. 136YALE4 (509775) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.3. 136YALE4 (509775) 138.0 kV to KIMCLRK4 (509845) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on T.P.S.-4 138.00 (509788) 138 kV Bus a. Apply Fault at the T.P.S.-4 138.00 (509788) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 36&OLY-4 (509724) 138.0 kV to T.P.S.-4 (509788) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 b.3. T.P.S.-4 (509788) 138.0 kV to OAKSWTP4 (509848) 138.0 kV Transmission Circuit #1 b.4. T.P.S.-4 (509788) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 b.5. OAKSWTP4 (509848) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 b.6. T.P.S.-4 (509788) 138.0 kV to T.P.S.-2 (509789) 69.0 kV to TPS5-1 (509880) 13.8 kV Three Winding #1 b.9. T.P.S.-4 (509788) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to RSS NG3 (511844) 13.8 kV to RSS NG4 (511845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to RSS NG3 (511844) 13.8 kV to RSS NG4 (511845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 116JENK4 (509753) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to 52DELWT4 (509814) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to OKMULGE4 (510898) 138.0 kV Transmission Circuit #1 b.2. RSS1-1 (511842) 24.0 kV to R.S.S.-4 (509783) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to RSS T2 4 (509875) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 136YALE4 (509775) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.2. RSS2-1 (511843) 22.0 kV to R.S.S.-4 (509783) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on RSS T1 4 138.00 (509773) 138 kV Bus a. Apply Fault at the RSS T1 4 138.00 (509773) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKSWTP4 (509848) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENKS--4 (509759) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on RNDBARN4 138.00 (515461) 138 kV Bus a. Apply Fault at the RNDBARN4 138.00 (515461) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.2. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ARCADIA4 138.00 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 138.00 (514907) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.2. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ARCADIA4 138.00 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 138.00 (514907) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.2. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HSL 4 138.00 (514941) 138 kV Bus a. Apply Fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNJEE 4 (514884) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 b.2. JNSKAMO4 (514906) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 b.3. HSLEAST2 (514927) 69.0 kV to HSLWEST2 (514937) 69.0 kV Transmission Circuit #1 b.4. HSLEAST2 (514927) 69.0 kV to GRNPAST2 (514971) 69.0 kV Transmission Circuit #1 b.5. HSLEAST2 (514927) 69.0 kV to TXSTELA2 (514985) 69.0 kV Transmission Circuit #1 b.6. HSLEAST2 (514927) 69.0 kV to MCLOUDT2 (515504) 69.0 kV Transmission Circuit #1 b.7. HSL 4 (514941) 138.0 kV to HSL 6G (514935) 17.1 kV Two Winding #1 b.8. HSL 4 (514941) 138.0 kV to HSL 7S (514936) 20.9 kV Two Winding #1 b.9. HSL 4 (514941) 138.0 kV to HSL 8G (514939) 22.8 kV Two Winding #1 b.10. HSL 4 (514941) 138.0 kV to HSL 9G (514944) 13.8 kV Two Winding #1 b.11. HSL 4 (514941) 138.0 kV to HSL 10G (514945) 13.8 kV Two Winding #1 b.12. HSL 4 (514941) 138.0 kV to MIDWAY 4 (514966) 138.0 kV Transmission Circuit #1 b.13. HSL 4 (514941) 138.0 kV to DALE 4 (514987) 138.0 kV Transmission Circuit #1 b.14. HSL 4 (514941) 138.0 kV to SE15TH 4 (514993) 138.0 kV Transmission Circuit #1 b.15. HSL 4 (514941) 138.0 kV to HAMMTAP4 (515046) 138.0 kV Transmission Circuit #1 b.16. HSL 4 (514941) 138.0 kV to JONESSB4 (515480) 138.0 kV Transmission Circuit #1 b.17. HSL 4 (514941) 138.0 kV to GEN-2018-029 (762647) 138.0 kV Transmission Circuit #1 b.18. HSL345 (599143) 345.0 kV to HSL 4 (514941) 138.0 kV Two Winding #1 b.19. HSLWEST2 (514937) 69.0 kV to HSL 4 (514941) 138.0 kV to HSL 1 (515731) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply Fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4MEMORALT (300136) 138.0 kV to JNSKAMO4 (514906) 138.0 kV Transmission Circuit #1 b.2. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply Fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.2. JNSKAMO4 (514906) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AGENCY 5 (515230) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TRIBES5 (515228) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to G16-119-TAP (587804) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to G16133G16146 (588039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #3 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #1 b.2. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #1 b.2. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on G16133G16146345.00 (588039) 345 kV Bus a. Apply Fault at the G16133G16146345.00 (588039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133G16146 (588039) 345.0 kV to G16133_345GS (588040) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on G16133G16146345.00 (588039) 345 kV Bus a. Apply Fault at the G16133G16146345.00 (588039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133G16146 (588039) 345.0 kV to G16133_345GS (588040) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAPLPRD7 (509870) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on G16133_765GS765.00 (588041) 765 kV Bus a. Apply Fault at the G16133_765GS765.00 (588041) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133_765GS (588041) 765.0 kV to G16133_765MP (588043) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on G16133_765GS765.00 (588041) 765 kV Bus a. Apply Fault at the G16133_765GS765.00 (588041) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133_765GS (588041) 765.0 kV to G16133_765MP (588043) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA4 (514907) 138.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on HSL345 (599143) 345 kV Bus a. Apply Fault at the HSL345 (599143) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSL345 (599143) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE1 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE2 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE3 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE4 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP1 | Single Phase Fault with Stuck Breaker on Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP2 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP3 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP4 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP5 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP6 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP7 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP8 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP9 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_AEP10 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on 8EL DORADO% 500.00 (337561) 500 kV Bus a. Apply Fault at the 8EL DORADO% 500.00 (337561) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. 8EL DORADO% (337561) 500.0 kV to 7EL DORADO (337562) 345.0 kV to 1EL DORADO2 (337565) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G08-047 (515905) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071_TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to GI106_POI (999700) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to GI106_POI (999700) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.2. FTSMITH7 (515302) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on DAWSONT4 138.00 (509803) 138 kV Bus a. Apply fault at the DAWSONT4 138.00 (509803) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.2. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.3. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.4. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 b.5. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.6. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.7. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on 77MEM-W4 138.00 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 138.00 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 (509766) 138.0 kV to E.61ST-4 (509831) 138.0 kV Transmission Circuit #1 b.2. 77MEM-W4 (509766) 138.0 kV to 96YALE-4 (509847) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on 136YALE4 138.00 (509775) 138 kV Bus a. Apply fault at the 136YALE4 138.00 (509775) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 (509775) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.2. 136YALE4 (509775) 138.0 kV to KIMCLRK4 (509845) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on EC.HEN-4 138.00 (510923) 138 kV Bus a. Apply fault at the EC.HEN-4 138.00 (510923) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV to EC.HEN-4 (510923) 138.0 kV Transmission Circuit #1 b.2. WELETK4 (510902) 138.0 kV to EC.HEN-4 (510923) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-082 (763134, 763137) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on EXPGLNT4 138.00 (515473) 138 kV Bus a. Apply fault at the EXPGLNT4 138.00 (515473) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 b.2. BEELINE4 (515247) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 b.3. EXPLGLN4 (515248) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 3.5 cycles. Lower clearing time is required in base case.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to KINZE 4 (515008) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.5. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.4. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.6. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.7. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on BURGETT4 138.00 (514510) 138 kV Bus a. Apply fault at the BURGETT4 138.00 (514510) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 (514510) 138.0 kV to DANFRTH4 (514833) 138.0 kV Transmission Circuit #1 b.2. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on LGARBER4 138.00 (515465) 138 kV Bus a. Apply fault at the LGARBER4 138.00 (515465) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONESSB4 (515480) 138.0 kV to CHTWOOD4 (514842) 138.0 kV Transmission Circuit # b.2. CHTWOOD4 (514842) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on NE10TH 4 138.00 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 138.00 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to MIDWAY 4 (514966) 138.0 kV Transmission Circuit #1 b.2. NE10TH 4 (514964) 138.0 kV to MIDWAY 4 (514966) 138.0 kV Transmission Circuit #1 b.3. NE10TH 4 (514964) 138.0 kV to RENO 4 (514973) 138.0 kV Transmission Circuit #1 b.4. NE10TH 4 (514964) 138.0 kV to GLENDAL4 (514986) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on DUNJEE 4 138.00 (514884) 138 kV Bus a. Apply fault at the DUNJEE 4 138.00 (514884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 (514884) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 b.2. DUNJEE 4 (514884) 138.0 kV to RENO 4 (514973) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on HSL 4 138.00 (514941) 138 kV Bus a. Apply fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to SE15TH 4 (514993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on HAMMTAP4 138.00 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 138.00 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to HAMMTAP4 (515046) 138.0 kV Transmission Circuit #1 b.2. HAMMTAP4 (515046) 138.0 kV to LINCOLN4 (515442) 138.0 kV Transmission Circuit #1 b.3. HAMMTAP4 (515046) 138.0 kV to HAMMETT4 (520951) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on SQUIRCK4 138.00 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 138.00 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to DALE 4 (514987) 138.0 kV Transmission Circuit #1 b.2. DALE 4 (514987) 138.0 kV to SQUIRCK4 (515059) 138.0 kV Transmission Circuit #1 b.3. SQUIRCK4 (515059) 138.0 kV to INGLEWD4 (515060) 138.0 kV Transmission Circuit #1 b.4. SQUIRCK4 (515059) 138.0 kV to STRLGTP4 (515286) 138.0 kV Transmission Circuit #1 b.5. FRSTHIL4 (515075) 138.0 kV to STRLGTP4 (515286) 138.0 kV Transmission Circuit #1 b.6. STRLGTP4 (515286) 138.0 kV to STERLNG4 (520449) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on 5TRIBES5 161.00 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 161.00 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 (515228) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on AGENCY 5 161.00 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 161.00 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 (515230) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on 4MEMORALT 138.00 (300136) 138 kV Bus a. Apply fault at the 4MEMORALT 138.00 (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER (300135) 138.0 kV to 4MEMORALT (300136) 138.0 kV Transmission Circuit #1 b.2. 4MEMORALT (300136) 138.0 kV to JNSKAMO4 (514906) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. This behavior was also observed in the base case. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on HSL 4 138.00 (514941) 138 kV Bus a. Apply fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 (514937) 69.0 kV to HSL 4 (514941) 138.0 kV to HSL 1 (515731) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO11 (515756) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on PECANCK7 345.00 (515235) 345 kV Bus a. Apply fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on PECANCK7 345.00 (515235) 345 kV Bus a. Apply fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on 4MEMORALT 138.00 (300136) 138 kV Bus a. Apply fault at the 4MEMORALT 138.00 (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT (300136) 138.0 kV to 4MEMORAL (301541) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on ORU W4 138.00 (509732) 138 kV Bus a. Apply fault at the ORU W4 138.00 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 (509732) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on ORU E4 138.00 (509738) 138 kV Bus a. Apply fault at the ORU E4 138.00 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 (509738) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on 116JENK4 138.00 (509753) 138 kV Bus a. Apply fault at the 116JENK4 138.00 (509753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 (509753) 138.0 kV to JENKS--4 (509759) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on 116JENK4 138.00 (509753) 138 kV Bus a. Apply fault at the 116JENK4 138.00 (509753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 (509753) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on JENKS--4 138.00 (509759) 138 kV Bus a. Apply fault at the JENKS--4 138.00 (509759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 (509759) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on BA101ST4 138.00 (509768) 138 kV Bus a. Apply fault at the BA101ST4 138.00 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 (509768) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on BA101-N4 138.00 (509769) 138 kV Bus a. Apply fault at the BA101-N4 138.00 (509769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 (509769) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on RSS T1 4 138.00 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 138.00 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to 52DELWT4 (509814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to RSS T2 4 (509875) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to OKMULGE4 (510898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 (509783) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on T.P.S.-4 138.00 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 138.00 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 (509788) 138.0 kV to 52DELWT4 (509814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on T.P.S.-4 138.00 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 138.00 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 (509788) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-027GEN1 (762628). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on 81YALES4 138.00 (509810) 138 kV Bus a. Apply fault at the 81YALES4 138.00 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 (509810) 138.0 kV to WAREN-W4 (509857) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on 81YALES4 138.00 (509810) 138 kV Bus a. Apply fault at the 81YALES4 138.00 (509810) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 (509810) 138.0 kV to WARNTAP4 (509858) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on SHILETP4 138.00 (509813) 138 kV Bus a. Apply fault at the SHILETP4 138.00 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 (509813) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on 52DELWT4 138.00 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 138.00 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 (509814) 138.0 kV to S HILLW4 (509859) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on OAKS--E4 138.00 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 138.00 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 (509846) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on 96YALE-4 138.00 (509847) 138 kV Bus a. Apply fault at the 96YALE-4 138.00 (509847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 (509847) 138.0 kV to WARNTAP4 (509858) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on OAKSWTP4 138.00 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 138.00 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 (509848) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on ORU ETP4 138.00 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 138.00 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 (509849) 138.0 kV to WARNTAP4 (509858) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on SAPLPRD4 138.00 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 138.00 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to 72ELWOD4 (509888) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on SAPLPRD4 138.00 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 138.00 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to DENV_WTAP4 (509896) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV to KELCO 4 (510931) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to G16-119-TAP (587804) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on HSL 4 138.00 (514941) 138 kV Bus a. Apply fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 (514941) 138.0 kV to JONESSB4 (515480) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on HSL345 345.00 (599143) 345 kV Bus a. Apply fault at the HSL345 345.00 (599143) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HSL345 (599143) 345.0 kV to HSL 4 (514941) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO21 (515757) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on PECANCK5 161.00 (515234) 161 kV Bus a. Apply fault at the PECANCK5 161.00 (515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 (515233) 138.0 kV to PECANCK5 (515234) 161.0 kV to PECANC31 (515750) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on ORU E4 138.00 (509738) 138 kV Bus a. Apply fault at the ORU E4 138.00 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 (509738) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on 77MEM-W4 138.00 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 138.00 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 (509766) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 (510898) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 (515045) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on G16133G16146345.00 (588039) 345 kV Bus a. Apply fault at the G16133G16146345.00 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 (588039) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on G16133_765GS765.00 (588041) 765 kV Bus a. Apply fault at the G16133_765GS765.00 (588041) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133_765GS (588041) 765.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on G16133_765MP765.00 (588043) 765 kV Bus a. Apply fault at the G16133_765MP765.00 (588043) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133_765MP (588043) 765.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 4 cycles. Same clearing time is required in base case.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 3.5 cycles. Lower clearing time is required in base case.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 3.5 cycles. Lower clearing time is required in base case.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to GI106_POI (999700) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-092-PROX (763215) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on OKMULGE4 138.00 (510898) 138 kV Bus a. Apply Fault at the OKMULGE4 138.00 (510898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to OKMULGE4 (510898) 138.0 kV Transmission Circuit #1 b.2. OKMULGE4 (510898) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 b.3. OKMULGE4 (510898) 138.0 kV to EC.HEN-4 (510923) 138.0 kV Transmission Circuit #1 b.4. OKMULGE4 (510898) 138.0 kV to KELCO 4 (510931) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on KIMCLRK4 138.00 (509845) 138 kV Bus a. Apply Fault at the KIMCLRK4 138.00 (509845) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. B111---4 (509767) 138.0 kV to KIMCLRK4 (509845) 138.0 kV Transmission Circuit #1 b.2. 136YALE4 (509775) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.3. 136YALE4 (509775) 138.0 kV to KIMCLRK4 (509845) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on T.P.S.-4 138.00 (509788) 138 kV Bus a. Apply Fault at the T.P.S.-4 138.00 (509788) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 36&OLY-4 (509724) 138.0 kV to T.P.S.-4 (509788) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 b.3. T.P.S.-4 (509788) 138.0 kV to OAKSWTP4 (509848) 138.0 kV Transmission Circuit #1 b.4. T.P.S.-4 (509788) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 b.5. OAKSWTP4 (509848) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 b.6. T.P.S.-4 (509788) 138.0 kV to T.P.S.-2 (509789) 69.0 kV to TPS5-1 (509880) 13.8 kV Three Winding #1 b.9. T.P.S.-4 (509788) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDROCKRD4 (511548) 138.0 kV to DARLINGTNRD4 (511559) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to RSS NG3 (511844) 13.8 kV to RSS NG4 (511845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to OAKSETP4 (509850) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to RSS NG3 (511844) 13.8 kV to RSS NG4 (511845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 116JENK4 (509753) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to 52DELWT4 (509814) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU-WTP4 (509853) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to EXP_OKM4 (510904) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to OKMULGE4 (510898) 138.0 kV Transmission Circuit #1 b.2. RSS1-1 (511842) 24.0 kV to R.S.S.-4 (509783) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to RSS T2 4 (509875) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 136YALE4 (509775) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 b.2. RSS2-1 (511843) 22.0 kV to R.S.S.-4 (509783) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on RSS T1 4 138.00 (509773) 138 kV Bus a. Apply Fault at the RSS T1 4 138.00 (509773) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-4 (509783) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKSWTP4 (509848) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENKS--4 (509759) 138.0 kV to SAPLPRD4 (509871) 138.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on RNDBARN4 138.00 (515461) 138 kV Bus a. Apply Fault at the RNDBARN4 138.00 (515461) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.2. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ARCADIA4 138.00 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 138.00 (514907) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.2. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ARCADIA4 138.00 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 138.00 (514907) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.2. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HSL 4 138.00 (514941) 138 kV Bus a. Apply Fault at the HSL 4 138.00 (514941) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNJEE 4 (514884) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 b.2. JNSKAMO4 (514906) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 b.3. HSLEAST2 (514927) 69.0 kV to HSLWEST2 (514937) 69.0 kV Transmission Circuit #1 b.4. HSLEAST2 (514927) 69.0 kV to GRNPAST2 (514971) 69.0 kV Transmission Circuit #1 b.5. HSLEAST2 (514927) 69.0 kV to TXSTELA2 (514985) 69.0 kV Transmission Circuit #1 b.6. HSLEAST2 (514927) 69.0 kV to MCLOUDT2 (515504) 69.0 kV Transmission Circuit #1 b.7. HSL 4 (514941) 138.0 kV to HSL 6G (514935) 17.1 kV Two Winding #1 b.8. HSL 4 (514941) 138.0 kV to HSL 7S (514936) 20.9 kV Two Winding #1 b.9. HSL 4 (514941) 138.0 kV to HSL 8G (514939) 22.8 kV Two Winding #1 b.10. HSL 4 (514941) 138.0 kV to HSL 9G (514944) 13.8 kV Two Winding #1 b.11. HSL 4 (514941) 138.0 kV to HSL 10G (514945) 13.8 kV Two Winding #1 b.12. HSL 4 (514941) 138.0 kV to MIDWAY 4 (514966) 138.0 kV Transmission Circuit #1 b.13. HSL 4 (514941) 138.0 kV to DALE 4 (514987) 138.0 kV Transmission Circuit #1 b.14. HSL 4 (514941) 138.0 kV to SE15TH 4 (514993) 138.0 kV Transmission Circuit #1 b.15. HSL 4 (514941) 138.0 kV to HAMMTAP4 (515046) 138.0 kV Transmission Circuit #1 b.16. HSL 4 (514941) 138.0 kV to JONESSB4 (515480) 138.0 kV Transmission Circuit #1 b.17. HSL 4 (514941) 138.0 kV to GEN-2018-029 (762647) 138.0 kV Transmission Circuit #1 b.18. HSL345 (599143) 345.0 kV to HSL 4 (514941) 138.0 kV Two Winding #1 b.19. HSLWEST2 (514937) 69.0 kV to HSL 4 (514941) 138.0 kV to HSL 1 (515731) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply Fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4MEMORALT (300136) 138.0 kV to JNSKAMO4 (514906) 138.0 kV Transmission Circuit #1 b.2. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply Fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.2. JNSKAMO4 (514906) 138.0 kV to HSL 4 (514941) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to G17-092-TAP (588839) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AGENCY 5 (515230) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TRIBES5 (515228) 161.0 kV to PECANCK5 (515234) 161.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #2 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC11 (515749) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to G16-119-TAP (587804) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to G16133G16146 (588039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #3 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #1 b.2. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #1 b.2. SEMINOL7 (515045) 345.0 kV to DRAPER 7 (514934) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on G16133G16146345.00 (588039) 345 kV Bus a. Apply Fault at the G16133G16146345.00 (588039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133G16146 (588039) 345.0 kV to G16133_345GS (588040) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on G16133G16146345.00 (588039) 345 kV Bus a. Apply Fault at the G16133G16146345.00 (588039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133G16146 (588039) 345.0 kV to G16133_345GS (588040) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAPLPRD7 (509870) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on G16133_765GS765.00 (588041) 765 kV Bus a. Apply Fault at the G16133_765GS765.00 (588041) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133_765GS (588041) 765.0 kV to G16133_765MP (588043) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on G16133_765GS765.00 (588041) 765 kV Bus a. Apply Fault at the G16133_765GS765.00 (588041) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16133_765GS (588041) 765.0 kV to G16133_765MP (588043) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on R.S.S.-4 138.00 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 138.00 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to ORU ETP4 (509849) 138.0 kV Transmission Circuit #1 b.2. R.S.S.-4 (509783) 138.0 kV to EXPGLNT4 (515473) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on PECANCK7 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK7 (515235) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-4 (509783) 138.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA4 (514907) 138.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on HSL345 (599143) 345 kV Bus a. Apply Fault at the HSL345 (599143) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSL345 (599143) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEMINOL7 (515045) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to HSL345 (599143) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE1 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE2 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE3 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_OKGE4 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to Remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP1 | Single Phase Fault with Stuck Breaker on Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP2 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP3 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP4 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP5 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP6 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP7 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP8 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP9 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_AEP10 | Single Phase Fault with Stuck Breaker on Riverside (509782) 345 kV Bus a. Apply Fault at the Riverside (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on 8EL DORADO% 500.00 (337561) 500 kV Bus a. Apply Fault at the 8EL DORADO% 500.00 (337561) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. 8EL DORADO% (337561) 500.0 kV to 7EL DORADO (337562) 345.0 kV to 1EL DORADO2 (337565) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071_TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to GI106_POI (999700) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to GI106_POI (999700) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G20-009-TAP (766291) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G17-141-GEN1 (760412) unit. | Reduce the simulation time step to 1/8 cycle.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.2. FTSMITH7 (515302) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Base | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Base | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Base | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Base | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25S | Base | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | The output power of G18-115 units (763321, 763324) drops to zero at 6.12 seconds and remains at zero until 21.1 seconds at which point, the units' power rapidly ramps up to 1 p.u. within 2 seconds, followed by a subsequent decrease. After updating the dynamic model of these units to the DISIS2023 version, the output power issue was completely resolved. | Dynamic model correction for G18-115.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 3.25 cycles.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 4 cycles.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 3 cycles.
04 SOUTHEAST | GEN-2024-292 Interim Study | 25W | Base | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 3 cycles.

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2024-292 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.888 | 8.888 | 0
GEN-2024-292 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 22.3337 | 22.3337 | 0
GEN-2024-292 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 22.1034 | 22.1034 | 0
GEN-2024-292 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.5212 | 7.5212 | 0
GEN-2024-292 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 24.4481 | 24.4481 | 0
GEN-2024-292 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.2156 | 24.2156 | 0
GEN-2024-292 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.5727 | 10.5727 | 0
GEN-2024-292 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.4742 | 9.4742 | 0
GEN-2024-292 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.7808 | 12.7808 | 0
GEN-2024-292 | 04 SOUTHEAST | 509727 | OAKS W4 | 138 | 16.3655 | 16.3655 | 0
GEN-2024-292 | 04 SOUTHEAST | 509731 | S.HIL E4 | 138 | 22.5758 | 22.5758 | 0
GEN-2024-292 | 04 SOUTHEAST | 509732 | ORU W4 | 138 | 24.552 | 24.552 | 0
GEN-2024-292 | 04 SOUTHEAST | 509733 | BA.NO-N4 | 138 | 12.0152 | 12.0152 | 0
GEN-2024-292 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.8944 | 18.8944 | 0
GEN-2024-292 | 04 SOUTHEAST | 509738 | ORU E4 | 138 | 25.9773 | 25.9773 | 0
GEN-2024-292 | 04 SOUTHEAST | 509741 | CARSN-N4 | 138 | 9.7533 | 9.7533 | 0
GEN-2024-292 | 04 SOUTHEAST | 509742 | DENVR-C4 | 138 | 13.4636 | 13.4636 | 0
GEN-2024-292 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 21.6426 | 21.6426 | 0
GEN-2024-292 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.9024 | 18.9024 | 0
GEN-2024-292 | 04 SOUTHEAST | 509748 | DENVR-W4 | 138 | 10.0274 | 10.0274 | 0
GEN-2024-292 | 04 SOUTHEAST | 509750 | WILLPIP2 | 69 | 5.6885 | 5.6885 | 0
GEN-2024-292 | 04 SOUTHEAST | 509751 | OGMARTN2 | 69 | 5.6536 | 5.6536 | 0
GEN-2024-292 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 45.3871 | 45.3871 | 0
GEN-2024-292 | 04 SOUTHEAST | 509754 | WHORSE-4 | 138 | 4.0886 | 4.0886 | 0
GEN-2024-292 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.7905 | 23.7905 | 0
GEN-2024-292 | 04 SOUTHEAST | 509756 | CARSN-S4 | 138 | 18.6413 | 18.6413 | 0
GEN-2024-292 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 35.4827 | 35.4827 | 0
GEN-2024-292 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.7646 | 26.7646 | 0
GEN-2024-292 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.6469 | 16.6469 | 0
GEN-2024-292 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 19.6112 | 19.6112 | 0
GEN-2024-292 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 20.5321 | 20.5321 | 0
GEN-2024-292 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 54.2538 | 54.2538 | 0
GEN-2024-292 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 24.6416 | 24.6416 | 0
GEN-2024-292 | 04 SOUTHEAST | 509777 | KENSH-W4 | 138 | 15.6632 | 15.6632 | 0
GEN-2024-292 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.9675 | 33.9675 | 0
GEN-2024-292 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 65.4672 | 65.4672 | 0
GEN-2024-292 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 19.4897 | 19.4897 | 0
GEN-2024-292 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 25.0494 | 25.0494 | 0
GEN-2024-292 | 04 SOUTHEAST | 509788 | T.P.S.-4 | 138 | 41.9822 | 41.9822 | 0
GEN-2024-292 | 04 SOUTHEAST | 509789 | T.P.S.-2 | 69 | 9.7 | 9.7 | 0
GEN-2024-292 | 04 SOUTHEAST | 509795 | DX----E2 | 69 | 5.4687 | 5.4687 | 0
GEN-2024-292 | 04 SOUTHEAST | 509796 | DX----W2 | 69 | 3.944 | 3.944 | 0
GEN-2024-292 | 04 SOUTHEAST | 509798 | HWY20--4 | 138 | 3.1291 | 3.1291 | 0
GEN-2024-292 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 28.6518 | 28.6518 | 0
GEN-2024-292 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.7878 | 8.7878 | 0
GEN-2024-292 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 52.6494 | 52.6494 | 0
GEN-2024-292 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.8042 | 30.8042 | 0
GEN-2024-292 | 04 SOUTHEAST | 509810 | 81YALES4 | 138 | 21.0875 | 21.0875 | 0
GEN-2024-292 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 27.487 | 27.487 | 0
GEN-2024-292 | 04 SOUTHEAST | 509813 | SHILETP4 | 138 | 29.3841 | 29.3841 | 0
GEN-2024-292 | 04 SOUTHEAST | 509814 | 52DELWT4 | 138 | 24.0508 | 24.0508 | 0
GEN-2024-292 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 30.4515 | 30.4515 | 0
GEN-2024-292 | 04 SOUTHEAST | 509816 | S.S.---2 | 69 | 6.5722 | 6.5722 | 0
GEN-2024-292 | 04 SOUTHEAST | 509821 | HWY20-T4 | 138 | 4.0976 | 4.0976 | 0
GEN-2024-292 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 20.274 | 20.274 | 0
GEN-2024-292 | 04 SOUTHEAST | 509832 | W.ED.-W4 | 138 | 12.1416 | 12.1416 | 0
GEN-2024-292 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 31.4571 | 31.4571 | 0
GEN-2024-292 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.497 | 30.497 | 0
GEN-2024-292 | 04 SOUTHEAST | 509845 | KIMCLRK4 | 138 | 23.3577 | 23.3577 | 0
GEN-2024-292 | 04 SOUTHEAST | 509846 | OAKS--E4 | 138 | 14.33 | 14.33 | 0
GEN-2024-292 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 26.2913 | 26.2913 | 0
GEN-2024-292 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 36.0328 | 36.0328 | 0
GEN-2024-292 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 28.5013 | 28.5013 | 0
GEN-2024-292 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 16.0837 | 16.0837 | 0
GEN-2024-292 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 25.8157 | 25.8157 | 0
GEN-2024-292 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 31.4997 | 31.4997 | 0
GEN-2024-292 | 04 SOUTHEAST | 509856 | 52DEL-W4 | 138 | 12.6197 | 12.6197 | 0
GEN-2024-292 | 04 SOUTHEAST | 509857 | WAREN-W4 | 138 | 16.0492 | 16.0492 | 0
GEN-2024-292 | 04 SOUTHEAST | 509858 | WARNTAP4 | 138 | 30.2829 | 30.2829 | 0
GEN-2024-292 | 04 SOUTHEAST | 509859 | S HILLW4 | 138 | 17.6005 | 17.6005 | 0
GEN-2024-292 | 04 SOUTHEAST | 509861 | E41ST_E4 | 138 | 17.7207 | 17.7207 | 0
GEN-2024-292 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.5814 | 12.5814 | 0
GEN-2024-292 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 18.4924 | 18.4924 | 0
GEN-2024-292 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 24.1075 | 24.1075 | 0
GEN-2024-292 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.9557 | 34.9557 | 0
GEN-2024-292 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 55.2213 | 55.2213 | 0
GEN-2024-292 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.636 | 24.636 | 0
GEN-2024-292 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 16.483 | 16.483 | 0
GEN-2024-292 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 24.3641 | 24.3641 | 0
GEN-2024-292 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 37.699 | 37.699 | 0
GEN-2024-292 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 29.6695 | 29.6695 | 0
GEN-2024-292 | 04 SOUTHEAST | 509897 | WLDCT_HIL4 | 138 | 4.0894 | 4.0894 | 0
GEN-2024-292 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 12.0729 | 12.0729 | 0
GEN-2024-292 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 12.3082 | 12.3082 | 0
GEN-2024-292 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 19.8587 | 19.8587 | 0
GEN-2024-292 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.9418 | 11.9418 | 0
GEN-2024-292 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 10.3514 | 10.3514 | 0
GEN-2024-292 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.3069 | 15.3069 | 0
GEN-2024-292 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.4622 | 14.4622 | 0
GEN-2024-292 | 04 SOUTHEAST | 510923 | EC.HEN-4 | 138 | 9.0527 | 9.0527 | 0
GEN-2024-292 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.0191 | 15.0191 | 0
GEN-2024-292 | 04 SOUTHEAST | 510931 | KELCO 4 | 138 | 10.6537 | 10.6537 | 0
GEN-2024-292 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 6.9743 | 6.9743 | 0
GEN-2024-292 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.5362 | 10.5362 | 0
GEN-2024-292 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 7.0145 | 7.0145 | 0
GEN-2024-292 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 16.7045 | 16.7045 | 0
GEN-2024-292 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 18.4348 | 18.4348 | 0
GEN-2024-292 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.8971 | 23.8971 | 0
GEN-2024-292 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.293 | 21.293 | 0
GEN-2024-292 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.1081 | 20.1081 | 0
GEN-2024-292 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.4201 | 8.4201 | 0
GEN-2024-292 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 19.5553 | 19.5553 | 0
GEN-2024-292 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.0454 | 33.0454 | 0
GEN-2024-292 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.5648 | 30.5648 | 0
GEN-2024-292 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.3491 | 11.3491 | 0
GEN-2024-292 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 16.1675 | 16.1675 | 0
GEN-2024-292 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 15.9692 | 15.9692 | 0
GEN-2024-292 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.0203 | 19.0203 | 0
GEN-2024-292 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.2064 | 28.2064 | 0
GEN-2024-292 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 13.0237 | 13.0237 | 0
GEN-2024-292 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.8549 | 9.8549 | 0
GEN-2024-292 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.2501 | 15.2501 | 0
GEN-2024-292 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 27.6955 | 27.6955 | 0
GEN-2024-292 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 28.7068 | 28.7068 | 0
GEN-2024-292 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 22.6515 | 22.6515 | 0
GEN-2024-292 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 31.2348 | 31.2348 | 0
GEN-2024-292 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 34.7847 | 34.7847 | 0
GEN-2024-292 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 33.3598 | 33.3598 | 0
GEN-2024-292 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 23.0066 | 23.0066 | 0
GEN-2024-292 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 27.8804 | 27.8804 | 0
GEN-2024-292 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.6901 | 23.6901 | 0
GEN-2024-292 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.5531 | 28.5531 | 0
GEN-2024-292 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.9165 | 46.9165 | 0
GEN-2024-292 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3661 | 34.3661 | 0
GEN-2024-292 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.4716 | 24.4716 | 0
GEN-2024-292 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 23.5846 | 23.5846 | 0
GEN-2024-292 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 29.9131 | 29.9131 | 0
GEN-2024-292 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 18.7425 | 18.7425 | 0
GEN-2024-292 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.8072 | 45.8072 | 0
GEN-2024-292 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 35.1645 | 35.1645 | 0
GEN-2024-292 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 22.5091 | 22.5091 | 0
GEN-2024-292 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 46.4399 | 46.4399 | 0
GEN-2024-292 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 33.4835 | 33.4835 | 0
GEN-2024-292 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 31.6996 | 31.6996 | 0
GEN-2024-292 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 11.984 | 11.984 | 0
GEN-2024-292 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.0582 | 42.0582 | 0
GEN-2024-292 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.3791 | 27.3791 | 0
GEN-2024-292 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 12.6743 | 12.6743 | 0
GEN-2024-292 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 57.4148 | 57.4148 | 0
GEN-2024-292 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 29.0737 | 29.0737 | 0
GEN-2024-292 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 17.7403 | 17.7403 | 0
GEN-2024-292 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.3038 | 20.3038 | 0
GEN-2024-292 | 04 SOUTHEAST | 514964 | GEN-2021-043 | 115 | 19.6553 | 19.6553 | 0
GEN-2024-292 | 04 SOUTHEAST | 514966 | GEN-2021-048 | 115 | 20.5542 | 20.5542 | 0
GEN-2024-292 | 04 SOUTHEAST | 514973 | GEN-2021-108 | 345 | 30.1188 | 30.1188 | 0
GEN-2024-292 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 14.0262 | 14.0262 | 0
GEN-2024-292 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 15.1308 | 15.1308 | 0
GEN-2024-292 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 16.0706 | 16.0706 | 0
GEN-2024-292 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.8201 | 16.8201 | 0
GEN-2024-292 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 42.1446 | 42.1446 | 0
GEN-2024-292 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 31.8659 | 31.8659 | 0
GEN-2024-292 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 18.6046 | 18.6046 | 0
GEN-2024-292 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.0978 | 21.0978 | 0
GEN-2024-292 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.9187 | 14.9187 | 0
GEN-2024-292 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.6395 | 10.6395 | 0
GEN-2024-292 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 29.882 | 29.882 | 0
GEN-2024-292 | 04 SOUTHEAST | 515227 | 5TRIBES2 | 69 | 13.3035 | 13.3035 | 0
GEN-2024-292 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 16.3671 | 16.3671 | 0
GEN-2024-292 | 04 SOUTHEAST | 515229 | AGENCY 2 | 69 | 13.6051 | 13.6051 | 0
GEN-2024-292 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.8451 | 14.8451 | 0
GEN-2024-292 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 10.1081 | 10.1081 | 0
GEN-2024-292 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 22.349 | 22.349 | 0
GEN-2024-292 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 23.6404 | 23.6404 | 0
GEN-2024-292 | 04 SOUTHEAST | 515247 | BEELINE4 | 138 | 23.1493 | 23.1493 | 0
GEN-2024-292 | 04 SOUTHEAST | 515248 | EXPLGLN4 | 138 | 25.1221 | 25.1221 | 0
GEN-2024-292 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 5.8211 | 5.8211 | 0
GEN-2024-292 | 04 SOUTHEAST | 515250 | HANCOK-5 | 161 | 14.94 | 14.94 | 0
GEN-2024-292 | 04 SOUTHEAST | 515251 | EUCLID 5 | 161 | 14.5066 | 14.5066 | 0
GEN-2024-292 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 24.5163 | 24.5163 | 0
GEN-2024-292 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.6512 | 10.6512 | 0
GEN-2024-292 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.9362 | 8.9362 | 0
GEN-2024-292 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.8323 | 14.8323 | 0
GEN-2024-292 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 21.7238 | 21.7238 | 0
GEN-2024-292 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.3503 | 10.3503 | 0
GEN-2024-292 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.0502 | 18.0502 | 0
GEN-2024-292 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8041 | 11.8041 | 0
GEN-2024-292 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 16.0291 | 16.0291 | 0
GEN-2024-292 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 19.4924 | 19.4924 | 0
GEN-2024-292 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5746 | 12.5746 | 0
GEN-2024-292 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 28.6987 | 28.6987 | 0
GEN-2024-292 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 43.9565 | 43.9565 | 0
GEN-2024-292 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.7961 | 22.7961 | 0
GEN-2024-292 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 22.7757 | 22.7757 | 0
GEN-2024-292 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 25.5811 | 25.5811 | 0
GEN-2024-292 | 04 SOUTHEAST | 515480 | JONESSB4 | 138 | 32.3698 | 32.3698 | 0
GEN-2024-292 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.1146 | 34.1146 | 0
GEN-2024-292 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.0391 | 14.0391 | 0
GEN-2024-292 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 12.9782 | 12.9782 | 0
GEN-2024-292 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.9461 | 15.9461 | 0
GEN-2024-292 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.8139 | 8.8139 | 0
GEN-2024-292 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.0121 | 14.0121 | 0
GEN-2024-292 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.5371 | 13.5371 | 0
GEN-2024-292 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 11.0185 | 11.0185 | 0
GEN-2024-292 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 12.0635 | 12.0635 | 0
GEN-2024-292 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.6822 | 16.6822 | 0
GEN-2024-292 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 12.3452 | 12.3452 | 0
GEN-2024-292 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.4421 | 19.4421 | 0
GEN-2024-292 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.8128 | 9.8128 | 0
GEN-2024-292 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.8161 | 6.8161 | 0
GEN-2024-292 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 18.0998 | 18.0998 | 0
GEN-2024-292 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 18.0953 | 18.0953 | 0
GEN-2024-292 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 12.0836 | 12.0836 | 0
GEN-2024-292 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 9.4624 | 9.4624 | 0
GEN-2024-292 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.9931 | 11.9931 | 0
GEN-2024-292 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 13.7125 | 13.7125 | 0
GEN-2024-292 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 41.1951 | 41.1951 | 0
GEN-2024-292 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.0467 | 7.0467 | 0
GEN-2024-292 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 5.2106 | 5.2106 | 0
GEN-2024-292 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.7154 | 7.7154 | 0
GEN-2024-292 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.7615 | 17.7615 | 0
GEN-2024-292 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.6991 | 17.6991 | 0
GEN-2024-292 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 12.3364 | 12.3364 | 0
GEN-2024-292 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 13.6597 | 13.6597 | 0
GEN-2024-292 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.4201 | 8.4201 | 0
GEN-2024-292 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 9.3991 | 9.3991 | 0
GEN-2024-292 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 15.917 | 15.917 | 0
GEN-2024-292 | 04 SOUTHEAST | 529306 | OMHOMNY4 | 138 | 2.6244 | 2.6244 | 0
GEN-2024-292 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 18.015 | 18.015 | 0
GEN-2024-292 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 20.6281 | 20.6281 | 0
GEN-2024-292 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 35.4827 | 35.4827 | 0
GEN-2024-292 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.4431 | 10.4431 | 0
GEN-2024-292 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 20.4206 | 20.4206 | 0
GEN-2024-292 | 04 SOUTHEAST | 585410 | GREAT_WESTRN | 345 | 9.9129 | 9.9129 | 0
GEN-2024-292 | 04 SOUTHEAST | 585420 | COWBOY_RIDGE | 345 | 7.7501 | 7.7501 | 0
GEN-2024-292 | 04 SOUTHEAST | 585430 | PRSIMN_CRK1 | 345 | 11.8603 | 11.8603 | 0
GEN-2024-292 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.8577 | 10.8577 | 0
GEN-2024-292 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 7.838 | 7.838 | 0
GEN-2024-292 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 16.0821 | 16.0821 | 0
GEN-2024-292 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.4967 | 9.4967 | 0
GEN-2024-292 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 8.1719 | 8.1719 | 0
GEN-2024-292 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.9675 | 33.9675 | 0
GEN-2024-292 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 18.6087 | 18.6087 | 0
GEN-2024-292 | 04 SOUTHEAST | 588041 | G16133_765GS | 765 | 6.4621 | 6.4621 | 0
GEN-2024-292 | 04 SOUTHEAST | 588043 | G16133_765MP | 765 | 4.1341 | 4.1341 | 0
GEN-2024-292 | 04 SOUTHEAST | 588045 | G16133_765CS | 765 | 3.6449 | 3.6449 | 0
GEN-2024-292 | 04 SOUTHEAST | 588046 | G16133_345CS | 345 | 8.2291 | 8.2291 | 0
GEN-2024-292 | 04 SOUTHEAST | 588050 | ZONE-1 SUB | 345 | 6.5655 | 6.5655 | 0
GEN-2024-292 | 04 SOUTHEAST | 588060 | ZONE-2 SUB | 345 | 6.5761 | 6.5761 | 0
GEN-2024-292 | 04 SOUTHEAST | 588070 | ZONE-3 SUB | 345 | 6.8018 | 6.8018 | 0
GEN-2024-292 | 04 SOUTHEAST | 588080 | ZONE-4 SUB | 345 | 8.1115 | 8.1115 | 0
GEN-2024-292 | 04 SOUTHEAST | 588090 | ZONE-5 SUB | 345 | 6.7757 | 6.7757 | 0
GEN-2024-292 | 04 SOUTHEAST | 588100 | ZONE-6 SUB | 345 | 7.3268 | 7.3268 | 0
GEN-2024-292 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.955 | 4.955 | 0
GEN-2024-292 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 20.3985 | 20.3985 | 0
GEN-2024-292 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.9112 | 20.9112 | 0
GEN-2024-292 | 04 SOUTHEAST | 588839 | GEN-2021-043 | 115 | 20.9112 | 20.9112 | 0
GEN-2024-292 | 04 SOUTHEAST | 589140 | GEN-2021-048 | 115 | 21.5803 | 21.5803 | 0
GEN-2024-292 | 04 SOUTHEAST | 589300 | GEN-2021-108 | 345 | 16.7183 | 16.7183 | 0
GEN-2024-292 | 04 SOUTHEAST | 599143 | HSL345 | 345 | 29.9296 | 29.9296 | 0
GEN-2024-292 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 6.5096 | 6.5096 | 0
GEN-2024-292 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.9336 | 1.9336 | 0
GEN-2024-292 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.9203 | 1.9203 | 0
GEN-2024-292 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.9662 | 3.9662 | 0
GEN-2024-292 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 19.0155 | 19.0155 | 0
GEN-2024-292 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 19.0453 | 19.0453 | 0
GEN-2024-292 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.8843 | 11.8843 | 0
GEN-2024-292 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.2971 | 8.2971 | 0
GEN-2024-292 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 20.2346 | 20.2346 | 0
GEN-2024-292 | 04 SOUTHEAST | 762625 | GEN-2018-027 | 138 | 35.913 | 35.913 | 0
GEN-2024-292 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 37.6816 | 37.6816 | 0
GEN-2024-292 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 57.3911 | 57.3911 | 0
GEN-2024-292 | 04 SOUTHEAST | 762680 | GEN-2018-032 | 345 | 11.9178 | 11.9178 | 0
GEN-2024-292 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 17.848 | 17.848 | 0
GEN-2024-292 | 04 SOUTHEAST | 763065 | GEN-2018-071 | 345 | 15.4395 | 15.4395 | 0
GEN-2024-292 | 04 SOUTHEAST | 763069 | G18-071_TAP | 345 | 15.502 | 15.502 | 0
GEN-2024-292 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.8996 | 9.8996 | 0
GEN-2024-292 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 19.0127 | 19.0127 | 0
GEN-2024-292 | 04 SOUTHEAST | 765350 | GEN-2021-006 | 345 | 17.9469 | 17.9469 | 0
GEN-2024-292 | 04 SOUTHEAST | 765470 | GEN-2021-018 | 345 | 7.1549 | 7.1549 | 0
GEN-2024-292 | 04 SOUTHEAST | 765480 | GEN-2021-019 | 345 | 11.9647 | 11.9647 | 0
GEN-2024-292 | 04 SOUTHEAST | 765720 | GEN-2021-047 | 345 | 16.3436 | 16.3436 | 0
GEN-2024-292 | 04 SOUTHEAST | 765721 | G21-047-TAP | 345 | 16.7101 | 16.7101 | 0
GEN-2024-292 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.2644 | 7.2644 | 0
GEN-2024-292 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.8388 | 5.8388 | 0
GEN-2024-292 | 04 SOUTHEAST | 900003 | TRAVERSE1 | 345 | 5.4117 | 5.4117 | 0
GEN-2024-292 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.5055 | 6.5055 | 0