## P0-P1-P2 Thermal Results
P0-P1-P2 Thermal Loadings
*Maximum top 10 worst outage conditions reported
Season | Event | Monitored Facility | Areas Name | MVA Rating | Con Label | Primary Outage* | Base Loading | Project Loading
25L | P1 | 300530 2GEOGT2 69.000 300541 2SEDALI 69.000 1 | AECI | 47 | SING 300117-300541(3) | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 15.1 | 99
25W | P1 | 300124 5HOLDENB2 161.00 300336 2HOLDEN 69.000 1 | AECI | 95 | SING 300110-301561(1) | OPEN LINE FROM BUS 300110 [5PITTSV 161.00] TO BUS 301561 [5HOLDENB1 161.00] CKT 1 | 84.7 | 89.4
25W | P1 | 301201 2DONIPH 69.000 505440 DONIPHN5 161.00 1 | AECI/SWPA | 22 | SING 301201-505440(2) | OPEN BRANCH FROM BUS 301201 [2DONIPH 69.000] TO BUS 505440 [DONIPHN5 161.00] CKT 2 | 124.4 | 96.4
25S | P1 | 300124 5HOLDENB2 161.00 300336 2HOLDEN 69.000 1 | AECI | 84 | SING 300110-301561(1) | OPEN LINE FROM BUS 300110 [5PITTSV 161.00] TO BUS 301561 [5HOLDENB1 161.00] CKT 1 | 97.6 | 99.1
25S | P1 | 300137 4BRISTOW 138.00 300889 2BRIISTOW 69.000 2 | AECI | 56 | SING 300135-301372(1) | OPEN LINE FROM BUS 300135 [4LUTHER 138.00] TO BUS 301372 [4LUTHERD 138.00] CKT 1 | 102.1 | 73.3
25S | P1 | 300194 2CHILLI 69.000 300195 2CHILLR 69.000 1 | AECI | 35 | SING 300201-301648(1) | OPEN LINE FROM BUS 300201 [2INGROV 69.000] TO BUS 301648 [2TMHILLB2 69.000] CKT 1 | 92.9 | 98.2
25S | P1 | 300194 2CHILLI 69.000 300218 5CHILLIS 161.00 1 | AECI | 56 | P12:161:AECI:CHILLI:HCKRYCRK:1 | OPEN BRANCH FROM BUS 300068 [5CHILLIN 161.00] TO BUS 300087 [5HICKCK 161.00] CKT 1 OPEN BRANCH FROM BUS 300068 [5CHILLIN 161.00] TO BUS 300218 [5CHILLIS 161.00] CKT Z1 | 82.5 | 91.3
25S | P1 | 300194 2CHILLI 69.000 300218 5CHILLIS 161.00 1 | AECI | 56 | P12:161:AECI:CHLLCTH:HCKRYCRK:1 | OPEN BRANCH FROM BUS 300068 [5CHILLIN 161.00] TO BUS 300087 [5HICKCK 161.00] CKT 1 OPEN BRANCH FROM BUS 300068 [5CHILLIN 161.00] TO BUS 300218 [5CHILLIS 161.00] CKT Z1 | 82.5 | 91.3
25S | P1 | 300323 2CENTRV 69.000 300336 2HOLDEN 69.000 1 | AECI | 51 | P12:161:AECI:PITTSVIL:ECKLES:1:::PK_259050_6 | OPEN BRANCH FROM BUS 300110 [5PITTSV 161.00] TO BUS 300320 [5LEVASY 161.00] CKT 1 OPEN BRANCH FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 78.3 | 81.8
25S | P1 | 300323 2CENTRV 69.000 300336 2HOLDEN 69.000 1 | AECI | 51 | SING 300110-300320(1) | OPEN LINE FROM BUS 300110 [5PITTSV 161.00] TO BUS 300320 [5LEVASY 161.00] CKT 1 | 78.4 | 81.8
25S | P1 | 300323 2CENTRV 69.000 300336 2HOLDEN 69.000 1 | AECI | 51 | SING 300320-548808(1) | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 77.2 | 80.7
25S | P1 | 300327 2ELM 69.000 300336 2HOLDEN 69.000 1 | AECI | 51 | SING 300110-301561(1) | OPEN LINE FROM BUS 300110 [5PITTSV 161.00] TO BUS 301561 [5HOLDENB1 161.00] CKT 1 | 89.8 | 96
25S | P1 | 300530 2GEOGT2 69.000 300541 2SEDALI 69.000 1 | AECI | 47 | SING 300117-300541(3) | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 30 | 87.8
25S | P1 | 300530 2GEOGT2 69.000 300541 2SEDALI 69.000 1 | AECI | 47 | SING 300117-541209(1) | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [MITCHELL 161.00] CKT 1 | 23.1 | 86.8
25S | P1 | 301201 2DONIPH 69.000 505440 DONIPHN5 161.00 1 | AECI/SWPA | 18 | SING 301201-505440(2) | OPEN LINE FROM BUS 301201 [2DONIPH 69.000] TO BUS 505440 [DONIPHN5 161.00] CKT 2 | 120.8 | 96.3
25S | P1 | 301443 5THMHLB4 161.00 543062 SALSBRY5 161.00 1 | AECI/KCPL | 334 | P12:161:AECI:HIGBEE:THHILL:MBRLY | OPEN BRANCH FROM BUS 300126 [5MOBTAP 161.00] TO BUS 301494 [5HIGBEEB2 161.00] CKT 1 OPEN BRANCH FROM BUS 300126 [5MOBTAP 161.00] TO BUS 300132 [5THMHLB2 161.00] CKT 1 OPEN BRANCH FROM BUS 300126 [5MOBTAP 161.00] TO BUS 345221 [5MOBERLY 1 161.00] CKT Z1 | 92.5 | 97.4
25S | P1 | 301443 5THMHLB4 161.00 543062 SALSBRY5 161.00 1 | AECI/KCPL | 334 | P12:161:AMMO-AECI::MOBERLY:THOMASHILL:1 | OPEN BRANCH FROM BUS 300126 [5MOBTAP 161.00] TO BUS 300132 [5THMHLB2 161.00] CKT 1 OPEN BRANCH FROM BUS 300126 [5MOBTAP 161.00] TO BUS 301494 [5HIGBEEB2 161.00] CKT 1 OPEN BRANCH FROM BUS 300126 [5MOBTAP 161.00] TO BUS 345221 [5MOBERLY 1 161.00] CKT Z1 | 92.5 | 97.4