## Executive Summary
Executive Summary: 2025 Annual Interim Availability Interconnection System Impact Study
Interconnection Customers GEN-2024-003 (Group 04) and ASGI-2024-001 (Group 03) have requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Seasonal LOIS Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than an Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 4.4
https://www.spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
Models Used in Study
Power Flow Analysis: DISIS-2022-001 Phase 2 Restudy (2022 ITP Series) * modified to exclude network upgrades assigned through DISIS-1701 to DISIS-2021. This model excludes upgrades assigned through DISIS-2022.
Summer: 2024 (24SP), 2027 (27SP)
Winter: 2027 (27WP)
Stability Analysis: DISIS-2022-001 Phase 2 (P2) (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1701 to DISIS-2020. This model excludes upgrades assigned through DISIS-2022.
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2022-001 Phase 2 (P2) (2020 Series MDWG Dynamics) * modified to exclude network upgrades assigned through DISIS-1701 to DISIS-2020. This model excludes upgrades assigned through DISIS-2022.
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 12/19/2025

## Revision History
Revision History
Date | Author | Change Description
2025-12-19 | SPP | Draft Report
2025-12-19 | SPP | Final Report

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 | June 1 - Sept 30 | Oct 1 - Nov 30 | Dec 1 - March 31 | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
ASGI-2024-001 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 15 | 12.5 | 12.5 | 12.5 | 15 | -0.4 | ER | WAPA | Pinelake 69kV | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal: CT | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | -0.1 | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
J1849 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES | Cypress 230 kV | Done: Phase 3
J1855 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 500 | [5 empty] | ER/NR | EES-EAI | MALLORY 161 | Done: Phase 3
J1856 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 140 | [5 empty] | ER/NR | EES-EAI | SHOFFNER - NEWPORT | Done: Phase 3
J1858 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 440 | [5 empty] | ER/NR | EES-EAI | Sandy Bayou | Done: Phase 3
J1872 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Done: Phase 3
J1873 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Done: Phase 3
J1890 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 270 | [5 empty] | ER/NR | EES | HARTBURG - AEP LAYFIELD 500.0kV | Done: Phase 3
J1891 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [5 empty] | ER/NR | EES-EMI | 230 kV McAdams Substation | Done: Phase 3
J1897 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [5 empty] | ER/NR | EES-EAI | DELL EHV - SAN SOUCI 500.0kV | Done: Phase 3
J1899 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [5 empty] | ER/NR | EES-EAI | DELL EHV - SAN SOUCI 500.0kV | Done: Phase 3
J1946 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 350 | [5 empty] | ER/NR | SMEPA | 230 kV Missionary Substation | Done: Phase 3
J2010 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 75 | [5 empty] | ER/NR | EES-EAI | STUTTGART RICUSKEY - WOODWARD 230 SUB 230.0kV | Done: Phase 3
J2047 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 199 | [5 empty] | ER/NR | EES-EMI | Robinsonville 230 kV | Done: Phase 3
J2071 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 198 | [5 empty] | ER/NR | EES | RYE CO - CYPRESS 138.0kV | Done: Phase 3
J2075 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES | China (Bus# 334204) to Sheco Batiste Creek (Bus# 334240) | Done: Phase 3
J2088 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 400 | [5 empty] | ER/NR | XEL | WEST MEMPHIS EHV - KEO EHV 500 kV (854.0) | Done: Phase 3
J2089 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | Line tap DELL to Manilla AECC 161 kV | Done: Phase 3
J2091 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Battery/Storage | 250 | [5 empty] | ER/NR | EES-EMI | TWINKLETOWN 230 KV | Done: Phase 3
J2127 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 172.5 | [5 empty] | ER/NR | SMEPA | Silver Creek 115kV | Done: Phase 3
J2133 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 100 | [5 empty] | ER/NR | EES-EAI | Garner 115 kV Substation | Done: Phase 3
J2134 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 195 | [5 empty] | ER/NR | EES-EAI | WHITE BLUFF EHV - WRIGHTSVILLE 115.0kV | Done: Phase 3
J2143 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | Lake Village Bagby 115 KV | Done: Phase 3
J2149 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 112 | [5 empty] | ER/NR | EES-EAI | WHITE BLUFF EHV - HENSLEY 115.0kV | Done: Phase 3
J2153 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 134 | [5 empty] | ER/NR | EES-EAI | Ashley County Switchyard | Done: Phase 3
J2165 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 145 | [5 empty] | ER | EES | JACINTO - SHECO BATISTE CREEK 230.0kV | Done: Phase 3
J2173 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 396 | [5 empty] | ER/NR | EES-EMI | BOLTON | Done: Phase 3
J2180 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | CLEC | Fisher | Done: Phase 3
J2181 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | 161 kV line tap of DELL EAST to Blytheville | Done: Phase 3
J2190 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [5 empty] | ER/NR | EES-EAI | DELL EHV - SAN SOUCI 500.0kV | Done: Phase 3
J2208 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 99 | [5 empty] | ER/NR | CLEC | Mansfield (Bus #500530) to Red River Tap (Bus #500762) 138 kV | Done: Phase 3
J2228 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES | Red Gum | Done: Phase 3
J2237 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 185 | [5 empty] | ER/NR | EES-EAI | Brinkley East - Aubrey 230 kV Line | Done: Phase 3
J2252 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 300 | [5 empty] | ER/NR | EES-EAI | Cash - Newport AB | Done: Phase 3
J2261 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 625 | [5 empty] | ER/NR | EES-EAI | INDEPENDENCE-ISES - POWERLINE ROAD 500.0kV | Done: Phase 3
J2262 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 625 | [5 empty] | ER/NR | EES-EAI | INDEPENDENCE-ISES - POWERLINE ROAD 500.0kV | Done: Phase 3
J2287 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 122 | [5 empty] | ER/NR | EES-EMI | DELTA SES SWITCHYARD 115kV | Done: Phase 3
J2289 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER | EES-EMI | Indianola 230/130 Sub | Done: Phase 3
J2292 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 50 | [5 empty] | ER/NR | LAGN | GOOS FERRY | Done: Phase 3
J2294 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | Dell to Nucor 161 kV | Done: Phase 3
J2297 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 100 | [5 empty] | ER | EES-EMI | Indianola 230kV Substation | Done: Phase 3
J2298 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | Gainesville Switching Station | Done: Phase 3
J2314 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 150 | [5 empty] | ER/NR | EES | PETRY WOODS SS | Done: Phase 3
J2317 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 202.5 | [5 empty] | ER/NR | EES | BASTROP (CAHOON) - STERLINGTON 115 SWYD 115.0kV | Done: Phase 3
J1846 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [5 empty] | ER/NR | XEL | PANTHER | Active: Phase 2
J1888 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 175 | [5 empty] | ER/NR | MP | Square Butte 230 kV Substation East | Active: Phase 2
J1898 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [5 empty] | ER/NR | XEL | Byron 161 kV | Active: Phase 2
J2027 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 150 | [5 empty] | ER/NR | GRE | CHUB LAKE - 304JB21/22 - HAMPTON - 8S50/51 345.0kV | Active: Phase 2
J2053 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 151.47 | [5 empty] | ER/NR | XEL | Cedar Mountain - Lyon County 345.0kV | Active: Phase 2
J2068 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 75 | [5 empty] | ER/NR | XEL | Herbert 69 kV Substation | Active: Phase 2
J2080 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [5 empty] | ER/NR | MP | Square Butte 230 kV Substation East | Active: Phase 2
J2084 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 45 | [5 empty] | ER/NR | MDU | Linton NW (not in power flow case yet) | Active: Phase 2
J2085 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 40 | [5 empty] | ER/NR | MDU | Linton NW 115 kV (radial to Wishek 115 kV) | Active: Phase 2
J2087 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 125 | [5 empty] | ER/NR | XEL | FRANKLIN | Active: Phase 2
J2097 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [5 empty] | ER/NR | MP | Tri-County 230 kV Substation | Active: Phase 2
J2101 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [5 empty] | ER/NR | MDU | Mandan 230 kV | Active: Phase 2
J2104 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 230 | [5 empty] | ER/NR | XEL | Cedar Mountain - Lyon County 345.0kV | Active: Phase 2
J2157 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [5 empty] | ER/NR | MP | Tri-County 230 kV Substation | Active: Phase 2
J2199 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [5 empty] | ER/NR | XEL | COON CREEK | Active: Phase 2
J2219 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 180 | [5 empty] | ER/NR | DPC | ROCHESTER - WABACO 161.0kV | Active: Phase 2
J2227 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 80.1 | [5 empty] | ER/NR | DPC | Independence - Bridge Creek 69.0kV | Active: Phase 2
J2250 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [5 empty] | ER/NR | OTP | Ellendale 345 | Active: Phase 2
J2276 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 39.5 | [5 empty] | ER/NR | OTP | ALEXANDRIA | Active: Phase 2
J2309 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Chanarambie - ELLSBOROUGH (GRE) 115.0kV | Active: Phase 2
J1889 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 60 | [5 empty] | ER/NR | ALTW | Mount Vernon | Active: Phase 2
J2031 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Wind | 100 | [5 empty] | ER/NR | ALTW | Toledo | Active: Phase 2
J2078 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | ALTW | Fernald | Active: Phase 2
J2120 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [5 empty] | ER/NR | ALTW | Fairfax | Active: Phase 2
J2268 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 370 | [5 empty] | ER/NR | ALTW | Duane Arnold | Active: Phase 2
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Wind | 200 | [5 empty] | ER/NR | ALTW | Quinn | Active: Phase 2
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [5 empty] | ER/NR | OTP
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [5 empty] | ER | BEPC | Judson Substation 345 kV | FACILITY STUDY STAGE
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [5 empty] | ER | BEPC | Judson Substation 345 kV | FACILITY STUDY STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal: CTG | 250 | [5 empty] | ER | BEPC | Judson Substation 345 kV | FACILITY STUDY STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [5 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [5 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [5 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | FACILITY STUDY STAGE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [5 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | FACILITY STUDY STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [5 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [5 empty] | ER/NR | KCPL | Nashua 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [5 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid: Solar and Storage | 80 | [5 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [5 empty] | ER | WERE | Burns 345kV Substation | FACILITY STUDY STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [5 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [5 empty] | ER/NR | OGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [5 empty] | ER/NR | OGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [5 empty] | ER | AEP | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.82 | [5 empty] | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER/NR | OGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.08 | [5 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid: Solar and Storage | 150 | [5 empty] | ER/NR | AEP | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER/NR | OGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [5 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [5 empty] | ER | AEP | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | OGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [5 empty] | ER | AEP | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | OGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER | GRDA | Silver City 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [5 empty] | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2022-234 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER/NR | AEP | Alluwe Tap â€“ Chelsea 138 kV line | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [5 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [5 empty] | ER/NR | OGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal: CTG | 203 | [5 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
J1519 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 180 | [5 empty] | ER/NR | AMMO | St. Francois to Lutesville 345 kV | Done: GIA
J1649 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 60 | [5 empty] | ER/NR | BREC | Shell - McCracken County 69.0kV | Done: GIA
J1836 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 275 | [5 empty] | ER/NR | AMMO | Montgomery- Callaway- 7 | Done: GIA
GIA-116 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | Thermal | 26 | [5 empty] | ER/NR | AECI
GIA-117 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | Thermal | 46 | [5 empty] | ER/NR | AECI
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | [5 empty] | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | FACILITY STUDY STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [5 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [5 empty] | ER | LES | Rokeby 115 kV Substation | FACILITY STUDY STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [5 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [5 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | FACILITY STUDY STAGE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [5 empty] | ER/NR | LES | Wagener 115kV Substation | FACILITY STUDY STAGE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [5 empty] | ER/NR | LES | Wagener 115kV Substation | FACILITY STUDY STAGE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | [5 empty] | ER | NPPD | Antelope 345kV substation | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [5 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | FACILITY STUDY STAGE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | [5 empty] | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | FACILITY STUDY STAGE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [5 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [5 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [5 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [5 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [5 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [5 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [5 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [5 empty] | ER | WERE | Viola 345kV Substation | FACILITY STUDY STAGE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [5 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [5 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [5 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [5 empty] | ER/NR | MIDW | ITC Post Rock 345 kV Substation | FACILITY STUDY STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Hybrid: Solar and Storage | 95 | [5 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [5 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [5 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | FACILITY STUDY STAGE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [5 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | FACILITY STUDY STAGE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [5 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | FACILITY STUDY STAGE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OKGE | 138kV Brown Substation | FACILITY STUDY STAGE
GEN-2021-015 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 74.9 | [5 empty] | ER | OKGE | Bobcat 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [5 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [5 empty] | ER | OKGE | Sooner 345 kV | FACILITY STUDY STAGE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [5 empty] | ER/NR | OKGE | Sooner 345 kV | FACILITY STUDY STAGE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [5 empty] | ER | WERE | Wild Plains 345kV Substation | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [5 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [5 empty] | ER | OKGE | Branch 161kV Substation | FACILITY STUDY STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [5 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | FACILITY STUDY STAGE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [5 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OKGE | Mustang 138kV Substation | FACILITY STUDY STAGE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [5 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | FACILITY STUDY STAGE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [5 empty] | ER | OKGE | Pecan Creek 345kV substation | FACILITY STUDY STAGE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [5 empty] | ER | OKGE | Pecan Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 155 | [5 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 100 | [5 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | FACILITY STUDY STAGE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar/Battery/Storage | 125 | [5 empty] | ER/NR | SPS |  | 0
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar/Battery/Storage | 100 | [5 empty] | ER/NR | SPS |  | 0
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 400 | [5 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [5 empty] | ER/NR | BEPC | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | [5 empty] | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | FACILITY STUDY STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [5 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [5 empty] | ER/NR | BEPC | Patent Gate Substation 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [5 empty] | ER | OPPD | 6846 Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [5 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [5 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [5 empty] | ER | OPPD | Substation 1363; 161kV Substation | FACILITY STUDY STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [5 empty] | ER | OPPD | Substation 1363; 161kV Substation | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [5 empty] | ER | OPPD | Substation 1363; 161kV Substation | FACILITY STUDY STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [5 empty] | ER | OPPD | Substation 3740; 345kV | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [5 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | FACILITY STUDY STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [5 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | FACILITY STUDY STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [5 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | FACILITY STUDY STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [5 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [5 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [5 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [5 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar/Battery/Storage | 45 | [5 empty] | ER | KCPL |  | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar/Battery/Storage | 45 | [5 empty] | ER | KCPL |  | 0
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [5 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [5 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [5 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [5 empty] | ER/NR | SUNC | Russell 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [5 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [5 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 29 | [5 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [5 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [5 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [5 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [5 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [5 empty] | ER/NR | EDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [5 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [5 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | FACILITY STUDY STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [5 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [5 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | FACILITY STUDY STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [5 empty] | ER/NR | AEPW | Lydia 345 kV Station | FACILITY STUDY STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [5 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | FACILITY STUDY STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [5 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | FACILITY STUDY STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [5 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | FACILITY STUDY STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [5 empty] | ER | SPS | Lubbock East Substation 230 kV | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [5 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | FACILITY STUDY STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [5 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [5 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid: Storage and Wind | 110 | [5 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA PENDING
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [5 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [5 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [5 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [5 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [5 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [5 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [5 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [5 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [5 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [5 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [5 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | [5 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [5 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [5 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [5 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [5 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA PENDING
MPC04300 | 01 NORTH | 20.5 | DIS-18-2-PQ | Wind | 400 | [5 empty] | ER/NR | OTP
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 460 | [5 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 75 | [5 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [5 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [5 empty] | ER/NR | AECI
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [5 empty] | ER | BEPC-SPP | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [5 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [5 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [5 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [5 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [5 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA PENDING
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [5 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [5 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [5 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [5 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [5 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [5 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA PENDING
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [5 empty] | ER | AEPW | Pittsburg 345kV Substation | IA PENDING
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [5 empty] | ER | AEPW | Longwood 345kV substation | IA PENDING
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [5 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [5 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [5 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | [5 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done: GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | [5 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done: GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [5 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done: GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [5 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done: GIA
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [5 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done: GIA
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [5 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done: GIA
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [5 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done: GIA
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [5 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done: GIA
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 | [5 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Done: GIA
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | [5 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done: GIA
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done: GIA
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | [5 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done: GIA
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Done: GIA
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Done: GIA
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 500 | [5 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done: GIA
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 1000 | [5 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done: GIA
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done: GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [5 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done: GIA
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | AMMO | Montgomery 161kV Substation | Done: GIA
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | AMMO | Guthrie 161 kV Substation | Done: GIA
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [5 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done: GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done: GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done: GIA
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | [5 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done: GIA
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | [5 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done: GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done: GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 | [5 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done: GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [5 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done: GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done: GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [5 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done: GIA
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 | [5 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done: GIA
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER | EES | Rilla 115 kV Substation | Done: GIA
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: GIA
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [5 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done: GIA
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [5 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done: GIA
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [5 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done: GIA
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: GIA
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done: GIA
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done: GIA
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER | EES | Oak Ridge 115 kV Substation | Done: GIA
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [5 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done: GIA
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | [5 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done: GIA
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | Driver 230kV | Done: GIA
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | MORELAND | Done: GIA
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Done: GIA
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | BLYTHEVILLE I-55 - AECC BLYTHEVILLE NORTH 161.0kV | Done: GIA
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | HARDIN WEST SS - SHERIDAN 115.0kV | Done: GIA
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [5 empty] | ER/NR | EES | Goos Ferry | Done: GIA
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [5 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Done: GIA
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Done: GIA
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [5 empty] | ER | EES | LAKE CHARLES BULK | Done: GIA
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Done: GIA
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Done: GIA
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Done: GIA
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | CLEC | Fisher - Marthaville 230.0kV | Done: GIA
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [5 empty] | ER/NR | EES-EAI | KEO EHV | Done: GIA
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | EES-EMI | J830 POI | Done: GIA
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Done: GIA
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [5 empty] | ER/NR | EES | Timberland 230kV | Done: GIA
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [5 empty] | ER/NR | EES-EAI | FISHER - CHERRY VALLEY 161.0kV | Done: GIA
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | WEST MEMPHIS EHV - KEO EHV 500.0kV | Done: GIA
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [5 empty] | ER/NR | EES | bastrop tap point | Done: GIA
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [5 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Done: GIA
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [5 empty] | ER | EES-EAI | FORREST CITY N SS - WYNNE SOUTH 161.0kV | Done: GIA
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [5 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done: GIA
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [5 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done: GIA
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | XEL | Adams 345 kV Substation | Done: GIA
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done: GIA
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Byron 345kV Substation | Done: GIA
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [5 empty] | ER | ALTW | Magnolia 161 kV Substation | Done: GIA
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER | XEL | Grant 115 kV Substation | Done: GIA
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [5 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done: GIA
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Done: GIA
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | XEL | Grant 115 kV Substation | Done: GIA
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done: GIA
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Benton County 115kV Substation | Done: GIA
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done: GIA
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [5 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Done: GIA
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | ALTW | Huntley | Done: GIA
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | ALTW | Huntley | Done: GIA
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Byron | Done: GIA
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | ALTW | Rutland | Done: GIA
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [5 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Done: GIA
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [5 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Done: GIA
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | XEL | NOBLES COUNTY | Done: GIA
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | XEL | BISON | Done: GIA
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | XEL | SHERBURNE CO | Done: GIA
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 120 | [5 empty] | ER/NR | XEL | Langdon 115 kV Sub | Done: GIA
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [5 empty] | ER/NR | XEL | Split Rock - Pipestone 115.0kV | Done: GIA
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Done: GIA
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [5 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Done: GIA
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | [5 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Done: GIA
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | [5 empty] | ER/NR | DPC | Barron 161 kV | Done: GIA
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [5 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done: GIA
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [5 empty] | ER/NR | XEL | Adams 345kV Substation | Done: GIA
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [5 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done: GIA
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done: GIA
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [5 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done: GIA
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [5 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done: GIA
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [5 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done: GIA
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done: GIA
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [5 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Done: GIA
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [5 empty] | ER/NR | ALTW | Traer 161-kV Substation | Done: GIA
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Done: GIA
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [5 empty] | ER/NR | ALTW | Other_ | Done: GIA
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Done: GIA
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Done: GIA
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Done: GIA
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [5 empty] | ER/NR | MEC | REMSEN TOWNSHIP | Done: GIA
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [5 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done: GIA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 170 | [5 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 130 | [5 empty] | ER | OTP |  | DISIS STAGE
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [5 empty] | ER/NR | OTP |  | DISIS STAGE
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | [5 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 300 | [5 empty] | ER/NR | OTP
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 97.5 | [5 empty] | ER | AECI
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [5 empty] | ER/NR | BEPC-SPP | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [5 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [5 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [5 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [5 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [5 empty] | ER | KCPL |  | 0
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [5 empty] | ER | KCPL |  | 0
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [5 empty] | ER | KCPL |  | 0
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [5 empty] | ER | KCPL |  | 0
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [5 empty] | ER | KCPL |  | 0
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [5 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [5 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [5 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [5 empty] | ER | WERE | Neosho 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [5 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [5 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [5 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [5 empty] | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [5 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [5 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [5 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [5 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [5 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [5 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [5 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [5 empty] | ER | XEL | Buffalo 115kV Substation | Done: GIA
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [5 empty] | ER | OTP | Big Stone South 230kV Substation | Done: GIA
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [5 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Done: GIA
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [5 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: GIA
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [5 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: GIA
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [5 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: GIA
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [5 empty] | ER | ALTW | Ledyard 345kV Substation | Done: GIA
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [5 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: GIA
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [5 empty] | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [5 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [5 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [5 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [5 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [5 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [5 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [5 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [5 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [5 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [5 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [5 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [5 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [5 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [5 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar | 310 | [5 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [5 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [5 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [5 empty] | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [5 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [5 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [5 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [5 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [5 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [5 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [5 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [5 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [5 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [5 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [5 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [5 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [5 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [5 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [5 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [5 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [5 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [5 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [5 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [5 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [5 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [5 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [5 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [5 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [5 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [5 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [5 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [5 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [5 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [5 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [5 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [5 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 45 | [5 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | Done: GIA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [5 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | Done: GIA
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [5 empty] | ER | WAPA | NELSON 7
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [5 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | BEPC-SPP | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [5 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [5 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [5 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [5 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [5 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [5 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [5 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [5 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [5 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [5 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [5 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [5 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [5 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [5 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [5 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [5 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [5 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | Wind | 100 | [5 empty] | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 246 | [5 empty] | ER/NR | AMMO
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [5 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [5 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [5 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [5 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [5 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [5 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [5 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [5 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [5 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [5 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [5 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [5 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [5 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [5 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [5 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [5 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [5 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [5 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [5 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [5 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [5 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [5 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [5 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [5 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 169.2 | [5 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [5 empty] | ER | SPS | Palo Duro 115kV
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [5 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [5 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 | [5 empty] | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [5 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [5 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [5 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 | [5 empty] | ER/NR | BEPC-SPP
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 10.3 | [5 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [5 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 219.96 | [5 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [5 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [5 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [5 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [5 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [5 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [5 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [5 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [5 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [5 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [5 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [5 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Solar | 73.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [5 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Solar | 50.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [5 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [5 empty] | ER | SPS | FE-Clovis Interchange 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [5 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [5 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [5 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [5 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [5 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [5 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [5 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [5 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [5 empty] | ER | NPPD | Tekamah & Oakland 115kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [5 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [5 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [5 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal: Gas | 550 | [5 empty] | ER | AEP | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Generation Interconnection Number or Upgrade ID | Assigned Study | Group | Service Type | Fuel Type | Point of Interconnection or Upgrade Name | MW Amount | Season | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27WP | Stability 25SP | Stability 25WP
ASGI-2024-001 | DISIS-2024-001 | 03 CENTRAL | ER | Thermal | Pinelake 69kV | 15 | April 1 - May 31 | 15 | None | None | N/A | N/A | N/A | 12.5 | 15
ASGI-2024-001 | DISIS-2024-001 | 03 CENTRAL | ER | Thermal | Pinelake 69kV | 12.5 | June 1 - Sept 30 | 12.5 | None | None | 12.5 | 12.5 | N/A | 12.5 | N/A
ASGI-2024-001 | DISIS-2024-001 | 03 CENTRAL | ER | Thermal | Pinelake 69kV | 15 | Oct 1 - Nov 30 | 15 | None | None | N/A | N/A | N/A | 12.5 | 15
ASGI-2024-001 | DISIS-2024-001 | 03 CENTRAL | ER | Thermal | Pinelake 69kV | 15 | Dec 1 - March 31 | 15 | None | None | N/A | N/A | 15 | N/A | 15
GEN-2024-003 | DISIS-2024-001 | 04 SOUTHEAST | ER | Thermal: CT | Fitzhugh 161kV | 102.2 | April 1 - May 31 | 102.2 | None | None | N/A | N/A | N/A | 102.2 | 102.2
GEN-2024-003 | DISIS-2024-001 | 04 SOUTHEAST | ER | Thermal: CT | Fitzhugh 161kV | 102.2 | June 1 - Sept 30 | 102.2 | None | None | 102.2 | 102.2 | N/A | 102.2 | N/A
GEN-2024-003 | DISIS-2024-001 | 04 SOUTHEAST | ER | Thermal: CT | Fitzhugh 161kV | 102.2 | Oct 1 - Nov 30 | 102.2 | None | None | N/A | N/A | N/A | 102.2 | 102.2
GEN-2024-003 | DISIS-2024-001 | 04 SOUTHEAST | ER | Thermal: CT | Fitzhugh 161kV | 102.2 | Dec 1 - March 31 | 102.2 | None | None | N/A | N/A | 102.2 | N/A | 102.2

## Upgrade Removal Summary
NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Source Study | Include/Exclude? | Estimated In-Service Date / Lead Time (months)
200477 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation. | DISIS-2016-002 | Exclude | 2025-04-20
200477 | 112395 | Device- Gypsum 69 kV Capacitor Bank | Gypsum 69 kV Capacitor Bank | Install a new 12 MVAR capacitor bank at Gypsum 69 kV substation. | 2019 ITP | Exclude | 2025-12-31
210682 | 159533 | Line - Bismarck 115 kV - East Bismarck 115 kV Rebuild | Bismarck 115 kV Terminal Upgrade | Install any necessary terminal equipment at Bismarck 115 kV substation to support the line from Bismarck 115 kV substation to East Bismarck 115 kV substation with a summer emergency rating of 145 MVA. | 2024 ITP | Exclude | 2025-04-17
210682 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Exclude | 2025-12-01
200477 | 122818 | Line - Cushing Tap - Shell Cushing Tap - Pipeline | Cushing - Shell Pipeline Cushing Tap 69 kV Ckt 1 Rebuild | Rebuild 4.71 miles of 69 kV line from Cushing to Shell Pipeline Cushing Tap and upgrade any necessary terminal equipment to achieve a summer emergency rating of 72 MVA | 2020 ITP | Exclude | 2025-09-01
210483 | 122819 | Line - Cushing Tap - Shell Cushing Tap - Pipeline | Pipeline - Shell Pipeline Cushing Tap 69 kV Ckt 1 Rebuild | Rebuild 1.19 miles of 69 kV line from Pipeline to Shell Pipeline Cushing Tap and upgrade any necessary terminal equipment to achieve a summer emergency rating of 72 MVA | 2020 ITP | Exclude | 2025-09-01
210483 | 112435 | Line - East Kingfisher - Kingfisher 138kV | East Kingfisher - Kingfisher 138 kV Rebuild | Rebuild 2.03 miles of 138 kV line from Kingfisher to East Kingfisher and upgrade any necessary terminal equipment at East Kingfisher and/or Kingfisher to increase the summer emergency rating to 187 MVA | 2019 ITP | Exclude | 2025-10-01
210483 | 143705 | Line - Kearney NE - Tower 115 kV | Kearney NE - Tower 115 kV Ckt 1 New Line | Build a new 115 kV 10 mile line from Kearney to Tower with a minimum summer emergency rating of 160 MVA | DPA-2021-February-1278 | Exclude | 2025-06-01
210483 | 144283 | Line - Kearney NE - Tower 115 kV | Tower 115 kV Terminal Equipment | Install terminal equipment at Tower 115 kV sub to support new line from Kearney 115 kV sub. | DPA-2021-February-1278 | Exclude | 2025-06-01
210545 | 144284 | Line - Kearney NE - Tower 115 kV | Kearney 115 kV Terminal Equipment | Install 115 kV terminal equipment at Kearney 115 kV sub to support a new line from Tower 115 kV sub. | DPA-2021-February-1278 | Exclude | 2025-06-01
210545 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Exclude | 2025-09-01
210586 | 122741 | Line - Scottsbluff - Victory Hill 115 kV Ckt 2 | Scottsbluff - Victory Hill 115kV Ckt 2 | Build second 9 mile 115 kV line from Scottsbluff to Victory Hill. | 2021 ITP | Exclude | 2025-06-01
210575 | 143599 | Line - Scottsbluff - Victory Hill 115 kV Ckt 2 | Scottsbluff 115 kV Ckt 2 Terminal Upgrades | Install terminal equipment at Scottsbluff 115 kV to support a second 115 kV line from Victory Hill. | 2021 ITP | Exclude | 2025-06-01
210645 | 143600 | Line - Scottsbluff - Victory Hill 115 kV Ckt 2 | Victory Hill 115 kV Ckt 2 Terminal Upgrades | Install terminal equipment at Victory Hill 115 kV to support a second 115 kV line from Scottsbluff with a summer emergency rating of 264 MVA | 2021 ITP | Exclude | 2025-06-01
210645 | 122730 | Line - South Shreveport - Wallace Lake 138 kV #2 | South Shreveport - Wallace Lake 138 kV Ckt 1 Rebuild #2 | Rebuild 11.18 miles of 138 kV line from South Shreveport to Wallace Lake and upgrade any necessary terminal equipment to achieve a summer emergency to 347 MVA | 2020 ITP | Exclude | 2025-12-18
220739 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Exclude | 2025-06-20
210583 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Exclude | 2025-10-09
210628 | 122722 | Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV | Dover Switch - O'Keene 138 kV Ckt 1 Terminal Upgrades | Upgrade any necessary terminal equipment, increase clearances, and replace conductor to achieve a summer emergency rating of 136 MVA | 2020 ITP | Exclude | 2025-12-31
210627 | 144277 | Multi - Elmore - Bradly 69 kV | Bradly Tap 69 kV Cap Bank | Install new 12 MVAR capacitor bank at Bradly Tap 69 kV. | DPA-2021-June-1332 | Exclude | 2025-10-30
210617 | 143253 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli - Lexington kV 138 kV | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | DPA-2020-May-1203 | Exclude | 2025-10-31
210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Exclude | 2025-12-31
210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Exclude | 2025-11-30
210645 | 72018 | Multi - Park Community - Sunshine 138 kV | Calumet - Watonga SW 138 kV Ckt 1 Voltage Conversion | Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. | DPA-2017-August-767-774-776 | Exclude | 2025-09-20
210645 | 72019 | Multi - Park Community - Sunshine 138 kV | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | DPA-2017-August-767-774-776 | Exclude | 2025-07-30
210648 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Exclude | 2025-11-30
210619 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Exclude | 2025-10-30
210656 | 143806 | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Marietta Tap (OKGE) – Marietta Switchyard (WFEC) 138 kV Ckt 1 New Line (OGE) | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC) | 2021 ITP | Exclude | 2025-06-30
210656 | 143815 | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Marietta 2 138 kV Voltage Conversion | Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4 | 2021 ITP | Exclude | 2025-06-30
210656 | 143816 | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Rocky Point - Marietta 2 138 kV Ckt 1 Rebuild | Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line | 2021 ITP | Exclude | 2025-06-30
210657 | 144173 | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Marietta Switchyard 138 kV Ckt 1 Terminal Equipment | Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta. | 2021 ITP | Exclude | 2025-10-20
210665 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Exclude | 2026-01-01
210664 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Exclude | 2025-10-01
210664 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Exclude | 2026-01-01
210664 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Exclude | 2026-01-01
210619 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Exclude | 2026-01-01
210619 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Exclude | 2026-01-01
210715 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Exclude | 2025-11-28
220739 | 144280 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Council - Mustang 138 kV Ckt 1 Reconductor | Reconductor of Mustang to Council 138 kV transmission line. | DPA-2021-March-1296 | Exclude | 2025-06-13
220739 | 144281 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen - Douglas Tap 138 kV Reconductor | Reconductor of Douglas Tap to Classen 138 kV transmission line. | DPA-2021-March-1296 | Exclude | 2025-11-28
220746 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Exclude | 2026-01-01
220739 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Exclude | 2026-01-01
220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Exclude | 2025-05-30
220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Exclude | 2025-12-31
220743 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Exclude | 2025-12-31
220743 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Exclude | 2025-12-31
220749 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Exclude | 2025-12-31
220749 | 157274 | Sub - Newman Grace Tap - Woodward Nitrogen 69 kV Terminal Upgrade | Woodward Nitrogen 69 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Woodward Nitrogen 69 kV substation on the Woodward Nitrogen to Newman Grace Tap 69 kV line to achieve a summer emergency rating of 71 MVA. | 2023 ITP | Exclude | 2025-06-01
220790 | 122739 | XFR - Columbus 230/115 | Columbus East 230/115 kV transformer | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 2021 ITP | Exclude | 2025-12-01
210589 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Exclude | 2025-12-01
210589 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Exclude | 2025-12-01
TBD | 170494 | Build new STRNDAHL-MW7 to BLKTLTAP-MW7 115kV Line 1 | Build new STRNDAHL-MW7 to BLKTLTAP-MW7 115kV Line 1 | Build a new STRNDAHL-MW7 to BLKTLTAP-MW7 115 kV line 1 (15 miles) to a standard rating of 239 MVA | GI STUDIES | Exclude | 2027-12-31
220885 | 170543 | Bus - Sidley 345 kV Bus Reconfiguration (JTIQ) | Hawthorn 345kV Terminal Equipment | Install terminal equipment at Hawthorn and re-terminate Hawthorn - Sibley 345 kV line. | 2024 JTIQ (DOE) | Exclude | 2032-09-01
220875 | 170539 | Bus - Sidley 345 kV Bus Reconfiguration (JTIQ) | Sibley 345 kV Bus Reconfiguration | Sibley 345 kV Bus Reconfiguration | 2024 JTIQ (DOE) | Exclude | 2032-09-01
220807 | 170381 | Device - Colbert 138 kV Capacitor | Colbert 138 kV Capacitor | Install 6 MVAR Capacitor at Colbert 138 kV substation | 2024 ITP | Exclude | 2029-06-30
220748 | 157280 | Device Dawson County-Fort Peck 230 kV 40 MVAR Line Reactor | Dawson County-Fort Peck 230 kV Line Reactor | Install 40 MVAR reactor on the Dawson County-Fort Peck 230 kV Line | 2023 ITP | Exclude | 2030-09-01
220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 2023 ITP | Exclude | 2027-06-30
220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Exclude | 2026-05-31
220812 | 170066 | Line - Beckham County - Potter -345 kV New Line | Beckham County 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2029-11-12
210708 | 156299 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis - 52nd & Delaware Tap 138 kV Ckt 1 Rebuild | Rebuild 138 kV line from 36th & Lewis to 52nd & Delaware Tap | 2022 ITP | Exclude | 2027-06-01
210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Exclude | 2027-06-01
220818 | 170192 | Line - Ainsworth Wind 115 kV - Bassett 115 kV New Line | Ainsworth Wind - Bassett 115 kV Ckt 1 New Line | Build a 25-mile 115 kV Ckt 1 new line from Ainsworth Wind 115 kV substation to Bassett 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of at least 228 MVA. | 2024 ITP | Exclude | 2029-06-01
220818 | 170193 | Line - Ainsworth Wind 115 kV - Bassett 115 kV New Line | Ainsworth Wind 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Ainsworth Wind 115 kV substation to support a new line from Ainsworth Wind 115 kV substation to Bassett 115 kV substation with a summer emergency rating of at least 228 MVA. | 2024 ITP | Exclude | 2029-06-01
220818 | 170194 | Line - Ainsworth Wind 115 kV - Bassett 115 kV New Line | Bassett 115 kV Ckt 1 Terminal Upgrade | : Install any necessary terminal equipment at Bassett 115 kV substation to support a new line from Bassett 115 kV substation to Ainsworth Wind 115 kV substation with a summer emergency rating of at least 228 MVA. | 2024 ITP | Exclude | 2029-06-01
220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Exclude | 2028-05-31
220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Exclude | 2027-12-31
220773 | 157396 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV substation to support a third line from Anadarko to Gracemont. | 2023 ITP | Exclude | 2028-05-31
220774 | 157879 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138 kV Ckt 3 New Line (OGE) | Build new 15 mile 138 kV Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Exclude | 2027-12-31
220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Exclude | 2027-12-31
220774 | 158637 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Gracemont 138 kV substation to support a third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA | 2023 ITP | Exclude | 2027-12-31
220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Exclude | 2028-05-31
220893 | 170542 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | Cooper - Moore 345 kV Line Tap | Tap the existing Cooper - Moore 345 kV line at Auburn | 2024 JTIQ (DOE) | Exclude | 2032-10-15
220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 JTIQ (DOE) | Exclude | 2032-09-01
220874 | 170538 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | Hoyt 345 kV Terminal Upgrade | Install any necessary terminal equipment at Hoyt 345 kV substation to support a new line from S3771 345 kV substation to Hoyt 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 JTIQ (DOE) | Exclude | 2032-09-01
220810 | 170147 | Line - Aurora 115 kV - Central City 115 kV New Line | Aurora - Central City 115 kV Ckt 1 New Line | Build a 13.2-mile 115 kV Ckt 1 new line from Aurora 115 kV substation to Central City 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of at least 228 MVA. | 2024 ITP | Exclude | 2028-12-31
220810 | 170148 | Line - Aurora 115 kV - Central City 115 kV New Line | Aurora 115 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Aurora 115 kV substation to support a new line from Aurora 115 kV substation to Central City 115 kV substation with a summer emergency rating of at least 228 MVA. | 2024 ITP | Exclude | 2028-12-31
220810 | 170149 | Line - Aurora 115 kV - Central City 115 kV New Line | Central City 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Central City 115 kV substation to support a new line from Central City 115 kV substation to Aurora 115 kV substation with a summer emergency rating of at least 228 MVA. | 2024 ITP | Exclude | 2028-12-31
220880 | 159385 | Line - Branson Northwest 161 kV - Branson North 161 kV - Reed Spring Rebuild | Reed Spring - Branson Northwest 161 kV Ckt 1 Rebuild | Rebuild 8.3 mile Ckt 1 line from Reed Spring 161 kV substation to Branson Northwest 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-03-01
220880 | 159387 | Line - Branson Northwest 161 kV - Branson North 161 kV - Reed Spring Rebuild | Branson Northwest 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Branson Northwest 161 kV Ckt1 substation to support the line from Branson Northwest 161 kV Ckt1 substation to Reed Spring 161 kV Ckt1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-03-01
220880 | 170401 | Line - Branson Northwest 161 kV - Branson North 161 kV - Reed Spring Rebuild | Branson Northwest - Branson North 161 kV Ckt 1 Rebuild | Rebuild 0.9 mile Ckt 1 line from Branson 161 kV substation to Branson North 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-05-01
220880 | 170402 | Line - Branson Northwest 161 kV - Branson North 161 kV - Reed Spring Rebuild | Branson Northwest 161 kV Ckt 1 Terminal Upgrade #2 | Install any necessary terminal equipment at Branson Northwest 161 kV Ckt1 substation to support the line from Branson Northwest 161 kV Ckt1 substation to Branson North 161 kV Ckt1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-05-01
220880 | 170403 | Line - Branson Northwest 161 kV - Branson North 161 kV - Reed Spring Rebuild | Branson North 161 kV Ckt 1 Terminal Upgrade #3 | Install any necessary terminal equipment at Branson North 161 kV Ckt1 substation to support the line from Branson North 161 kV Ckt1 substation to Branson Northwest 161 kV Ckt1 substation awith a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-05-01
220808 | 159305 | Line - Butler 138 kV - Midian 138 kV Rebuild | Butler - Midian 138 kV Ckt 1 Rebuild | Rebuild 3-mile Ckt 1 line from Butler 138 kV substation to Midian 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 286 MVA | 2024 ITP | Exclude | 2028-12-31
220808 | 159362 | Line - Butler South 138 kV - Tallgrass 138 kV Rebuild #2 | Butler South - Tallgrass 138 kV Ckt 1 Rebuild #1 | Rebuild 9.9-mile Ckt 1 line from Butler South 138 kV substation to Tallgrass 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 286 MVA. | 2024 ITP | Exclude | 2029-06-01
220808 | 159363 | Line - Butler South 138 kV - Tallgrass 138 kV Rebuild #2 | Butler South 138 kV Ckt 1 Terminal Upgrade #2 | Install any necessary terminal equipment at Butler South 138 kV substation to support the line from Butler South 138 kV substation to Tallgrass 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Exclude | 2029-06-01
220808 | 159364 | Line - Butler South 138 kV - Tallgrass 138 kV Rebuild #2 | Tallgrass 138 kV Ckt 1 Terminal Upgrade #2 | Install any necessary terminal equipment at Tallgrass 138 kV substation to support the line from Tallgrass 138 kV substation to Butler South 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Exclude | 2029-06-01
220804 | 170389 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Cherokee Data Center East - Tulsa North 138 kV Ckt 1 Rebuild | Rebuild 4.6-mile Ckt 1 line from Tulsa North 138 kV substation to Cherokee Data Center East 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA. | 2024 ITP | Exclude | 2027-10-01
220804 | 170390 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Cherokee Data Center East 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Cherokee Data Center East 138 kV substation to support the line from Cherokee Data Center East 138 kV substation to Tulsa North 138 kV substation with a summer emergency rating of 300 MVA. | 2024 ITP | Exclude | 2027-10-01
220804 | 170405 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Tulsa North 138 kV Ckt 1 Terminal Upgrade #3 | Install any necessary terminal equipment at Tulsa North 138 kV substation to support the line from Tulsa North 138 kV substation to Cherokee Data Center East 138 kV substation with a summer emergency rating of 300 MVA. | 2024 ITP | Exclude | 2027-10-01
220808 | 159449 | Line - Chisholm 138 kV - Maize 138 kV - Evan Energy Center North 138 KV Ct1 Rebuild | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 2024 ITP | Exclude | 2028-12-31
220808 | 170123 | Line - Chisholm 138 kV - Maize 138 kV - Evan Energy Center North 138 KV Ct1 Rebuild | Chisholm - Maize 138 kV Ckt 1 Rebuild | Rebuild 7.3-mile Ckt 1 line from Chisholm 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA | 2024 ITP | Exclude | 2031-12-31
220808 | 170124 | Line - Chisholm 138 kV - Maize 138 kV - Evan Energy Center North 138 KV Ct1 Rebuild | Chisholm 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Chisholm 138 kV substation to support the line from Chisholm 138 kV substation to Maize 138 kV substation with a summer emergency rating of 478 MVA. | 2024 ITP | Exclude | 2031-12-31
220808 | 170127 | Line - Chisholm 138 kV - Maize 138 kV - Evan Energy Center North 138 KV Ct1 Rebuild | Maize 138 kV Ckt 1 Terminal Upgrade #2 | Install any necessary terminal equipment at Maize 138 kV substation to support a line from Maize 138 kV substation to Chisholm 138 kV substation with a summer emergency rating of 478 MVA. | 2024 ITP | Exclude | 2031-12-31
210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Exclude | 2026-12-30
210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Exclude | 2026-02-28
210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Exclude | 2027-02-28
220869 | 169762 | Line - Dawson County 230 kV - Williston 230 kV New Line | Dawson County - Williston 230 kV Ckt 1 New Line | Build 103.7-mile 230 kV Ckt 1 line from Dawson County 230 kV substation to Williston 230 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 796 MVA. | 2024 ITP | Exclude | 2032-12-31
220869 | 169764 | Line - Dawson County 230 kV - Williston 230 kV New Line | Williston 230 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Williston 230 kV substation to support a new line from Williston 230 kV substation to Dawson County 230 kV substation with a summer emergency rating of 796 MVA. | 2024 ITP | Exclude | 2032-12-31
220901 | 159345 | Line - Farber 138 kV - Sumner County No. 10 Belle Plain 138 kV Rebuild | Farber - Sumner County No. 10 Belle Plain 138 kV Ckt 1 Rebuild | Rebuild 10.3-mile 138 kV Ckt 1 line from Farber 138 kV substation to Sumner County No. 10 Belle Plain 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 286 MVA. | 2024 ITP | Exclude | 2029-06-01
220739 | 157644 | Line - Fitzgerald Creek - Kinze 138 kV | Fitzgerald Creek - Kinze 138 kV Line Tap | Tap and extend the existing Fitzgerald Creek - Kinze 138 kV line by 2 miles to terminate at Valley 138 kV substation | 2023 ITP | Exclude | 2028-06-01
220737 | 157263 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Longwood - Oak Pan-Harr 138 kV Ckt 1 Rebuild | Rebuild 1.8 miles of 138 kV line from Longwood 138 kV to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 324 MVA. | 2023 ITP | Exclude | 2028-06-01
220737 | 157264 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Longwood 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Longwood 138 kV substation on the Longwood to Oak Pan-Harr 138 kV line to achieve a summer emergency rating of 324 MVA. | 2023 ITP | Exclude | 2028-06-01
220737 | 157266 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Flournoy - Oak Pan-Harr 138 kV Ckt 1 Rebuild | Rebuild 10.4 miles of 138 kV line from Flournoy 138 kV substation to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 287 MVA. | 2023 ITP | Exclude | 2028-06-01
220748 | 157946 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Exclude | 2027-04-01
220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Exclude | 2027-04-01
220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2029-12-31
220896 | 170230 | Line - Holt County 345 kV - Antelope 345 kV New Line | Holt County 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Holt County 345 kV Ck1 substation to support a new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ckt1 substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2029-12-31
220896 | 170231 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Antelope 345 kV Ck1 substation to support a new line from Antelope 345 kV Ck1 substation to Holt County 345 kV Ck1 substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2029-12-31
220810 | 159308 | Line - Hoskins 115 kV - Stanton North 115 kV Rebuild | Hoskins - Stanton North 115 kV Ckt 1 Rebuild | Rebuild 9.9-mile 115 kV Ckt 1 line from Hoskins 115 kV substation to Stanton North 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of at least 239 MVA. | 2024 ITP | Exclude | 2027-06-01
220810 | 159309 | Line - Hoskins 115 kV - Stanton North 115 kV Rebuild | Hoskins 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Hoskins 115 kV substation for the line from Hoskins 115 kV substation to Stanton North 115 kV substation with a summer emergency rating of at least 239 MVA. | 2024 ITP | Exclude | 2027-06-01
220810 | 159310 | Line - Hoskins 115 kV - Stanton North 115 kV Rebuild | Stanton North 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Stanton North 115 kV substation for the line from Stanton North 115 kV substation to Hoskins 115 kV substation with a summer emergency rating of at least 239 MVA. | 2024 ITP | Exclude | 2027-06-01
220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-12-31
220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-12-31
220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Exclude | 2026-12-31
220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-12-31
220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-12-31
220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-12-31
220808 | 159285 | Line - Lawrence Energy Center Unit 3 115 kV - Lawrence Hill 115 kV Rebuild | Lawrence Energy Center Unit 3 - Lawrence Hill 115 kV Ckt 1 Rebuild | Rebuild 0.5-mile 115 kV Ckt 1 line from Lawrence Energy Center Unit 3 115 kV substation to Lawrence Hill 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2024 ITP | Exclude | 2027-06-01
220808 | 159286 | Line - Lawrence Energy Center Unit 3 115 kV - Lawrence Hill 115 kV Rebuild | Lawrence Hill 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Lawrence Hill 115 kV substation for the line from Lawrence Hill 115 kV substation to Lawrence Energy Center Unit 3 115 kV substation with a summer emergency rating of 239 MVA. | 2024 ITP | Exclude | 2027-06-01
220808 | 159289 | Line - Lawrence Energy Center Unit 3 115 kV - Lawrence Hill 115 kV Rebuild | Lawrence Energy Center Unit 3 115 kV Ckt 1 Terminal Upgrade #2 | Install any necessary terminal equipment at Lawrence Energy Center Unit 3 115 kV substation for the line from Lawrence Energy Center Unit 3 115 kV substation to Lawrence Hill 115 kV substation with a summer emergency rating of 239 MVA. | 2024 ITP | Exclude | 2027-06-01
220772 | 158573 | Line - Mathewson 345 kV - Redbud 345 kV | Redbud 345 kV Terminal Upgrade | Install any necessary terminal equipment at Redbud 345 kV substation to support a new line from Redbud 345 kV substation to Matthewson 345 kV substation with a summer emergency rating of 1792 MVA. | 2023 ITP | Exclude | 2027-12-31
220772 | 158574 | Line - Mathewson 345 kV - Redbud 345 kV | Matthewson 345 kV Terminal Equipment #2 | Install any necessary terminal equipment at Matthewson 345 kV substation to support a new line from Matthewson 345 kV substation to Redbud 345 kV substation with a summer emergency rating of 1792 MVA. | 2023 ITP | Exclude | 2027-12-31
220880 | 159382 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring - S Reed Spring 161 kV Ckt 1 Rebuild | Rebuild 1.5 mile Ckt 1 line from N Reed Spring 161 kV substation to S Reed Spring 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2029-11-01
220880 | 159383 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at N Reeds Spring 161 kV Ckt 1 substation for the line from N Reeds Spring 161 kV Ckt 1 substation to S Reeds Spring 161 kV Ckt 1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2029-11-01
220880 | 159384 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | S Reed Spring 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at S Reeds Spring 161 kV Ckt 1 substation for the line from S Reeds Spring 161 kV Ckt substation to N Reeds Spring 161 kV Ckt 1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2028-11-01
220774 | 157530 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Osage 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 561 MVA. | 2023 ITP | Exclude | 2026-12-01
220774 | 157880 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Webb City Tap - Osage 138 kV Ckt 1 Rebuild (OGE) | Rebuild 20 miles of 138 kV line from Webb City Tap 138 kV substation to Osage 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MV | 2023 ITP | Exclude | 2026-12-01
220880 | 159438 | Line - Ozark Dam 161 kV - Branson North 161 kV Rebuild | Branson North - Ozark Dam 161 kV Ckt 1 Rebuild | Rebuild 7.1 mile Ckt 1 line from Ozark Dam 161 kV Ckt1 substation to Branson North 161 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-09-01
220880 | 159439 | Line - Ozark Dam 161 kV - Branson North 161 kV Rebuild | Ozark Dam 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Ozark Dam 161 kV Ckt1 substation to support the line from Ozark Dam 161 kV Ckt1 substation to Branson North 161 kV Ckt1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2028-03-01
220880 | 159440 | Line - Ozark Dam 161 kV - Branson North 161 kV Rebuild | Branson North 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Branson North 161 kV Ckt1 substation to support the line from Branson North 161 kV Ckt1 substation to Ozark Dam 161 kV Ckt1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Exclude | 2030-09-01
220737 | 157475 | Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild | Pine & Peoria Tap - 46Th Street Tap 138 kV Ckt 1 Rebuild | Rebuild 0.5 miles of 138 kV Ckt 1 line from Pine & Peoria Tap 138 kV substation to 46Th Street Tap 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 347 MVA. | 2023 ITP | Exclude | 2026-05-02
220737 | 157517 | Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild | Tulsa North - 46Th Street Tap 138 kV Ckt 1 Rebuild | Rebuild 5.2 miles of 138 kV Ckt 1 line from Tulsa North 138 kV substation to 46th Street Tap138 kV substation to achieve a summer emergency rating of 278 MVA. | 2023 ITP | Exclude | 2026-05-02
220737 | 157518 | Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild | Tulsa North 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Tulsa North 138 kV substation on the 46th Street Tap to Tulsa North 138 kV line to achieve a summer emergency rating of 278 MVA. | 2023 ITP | Exclude | 2026-05-02
220893 | 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Tekamah 345 kV Terminal Upgrade | Install any necessary terminal equipment at Tekamah 345 kV substation to support a new line from Raun 345 kV substation to Tekamah 345 kV substation with a summer emergency rating of 558 MVA. | 2024 JTIQ (DOE) | Exclude | 2032-01-15
220815 | 159593 | Line - Ren 115 kV - Williston 115 kV Rebuild | Williston 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Williston 115 kV substation for the line from Williston 115 kV substation to Ren 115 kV substation with a summer emergency rating of 239 MVA. | 2024 ITP | Exclude | 2027-09-30
210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Exclude | 2027-12-31
220815 | 159584 | Line - Spencer 69 kV - Wisdom 69 kV Rebuild | Spencer 69 kV Ckt 2 Terminal Upgrade | Install any necessary terminal equipment at Spencer 69 kV substation to support the line from Spencer 69 kV substation to Wisdom 69 kV substation with a summer emergency rating of 114 MVA. | 2024 ITP | Exclude | 2026-07-31
220808 | 159412 | Line - Weaver 138 kV - Tallgrass 138 kV Rebuild #1 | Weaver - Tallgrass 138 kV Ckt 1 Rebuild #1 | Rebuild 9.8 mile Ckt 1 line from Weaver 138 kV substation to Tallgrass 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 286 MVA. | 2024 ITP | Exclude | 2029-12-31
220808 | 159413 | Line - Weaver 138 kV - Tallgrass 138 kV Rebuild #1 | Weaver 138 kV Ckt 1 Terminal Upgrade #2 | Install any necessary terminal equipment at Weaver 138 kV substation for the line from Weaver 138 kV substation to Tallgrass 138 kV substation with a summer emergency rating of 239 MVA. | 2024 ITP | Exclude | 2029-12-31
220808 | 159414 | Line - Weaver 138 kV - Tallgrass 138 kV Rebuild #1 | Weaver - Tallgrass 138 kV Ckt 1 Rebuild #2 | Install any necessary terminal equipment at Tallgrass 138 kV substation for the line from Tallgrass 138 kV substation to Weaver 138 kV substation with a summer emergency rating of 239 MVA. | 2024 ITP | Exclude | 2029-06-01
220872 | 170005 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at New Underwood 2 345 kV substation to support a new line from New Underwood 2 345 kV substation to Laramie River 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-10-01
220872 | 170006 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 - Maurine 2 345 kV Ckt 1 New Line | Build a 78-mile 345 kV Ckt1 new line from New Underwood 2 345 kV substation to Maurine 2 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. This upgrade shall include 40 MVAR line reactor compensation at the New Underwood 2 and Maurine 2 terminals. | 2024 ITP | Exclude | 2034-10-01
220872 | 170012 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 345 kV Ckt 1 Terminal Upgrade #1 | : Install any necessary terminal equipment at New Underwood 2 345 kV substation to support a new line from New Underwood 2 345 kV substation to Maurine 2 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-10-01
220872 | 170014 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 345 kV New Substation | Build a new 345 kV substation at New Underwood 2 | 2024 ITP | Exclude | 2034-10-01
220872 | 170016 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 345/230 kV Transformer Ckt 1 (230 kV) | Install a new 345/230 transformer at the new New Underwood 2 230 kV substation. | 2024 ITP | Exclude | 2034-10-01
220872 | 170017 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 345/230 kV Transformer Ckt 1 (345 kV) | Install 345 kV terminal equipment to support 345/230 kV transformer at the new New Underwood 2 345 kV substation | 2024 ITP | Exclude | 2034-10-01
220872 | 170529 | Multi - Laramie River 345 kV - New Underwood 345 kV | New Underwood 2 230 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at New Underwood 2 substation to support a new line from New Underwood 2 substation to tie into an existing 230 kV substation in the vicinity with a summer emergency rating of 675 MVA. | 2024 ITP | Exclude | 2034-10-01
220822 | 170000 | Multi - Belfield 345 kV - Maurine 345 kV | Belfield 2 - Maurine 2 345 kV Ckt 1 New Line | Build a 154.2-mile 345 kV Ckt 1 new line from Belfield 2 345 kV substation to Maurine 2 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. This upgrade shall include 40 MVAR line reactor compensation at the Belfield 2 and Maurine 2 terminals. | 2024 ITP | Exclude | 2034-10-01
220822 | 170001 | Multi - Belfield 345 kV - Maurine 345 kV | Belfield 2 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Belfield 2 345 kV substation to support a new line from Belfield 2 345 kV substation to Maurine 2 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-11-01
220822 | 170002 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 2 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maurine 2 345 kV substation to support a new line from Maurine 2 345 kV substation to Belfield 2 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-10-01
220822 | 170013 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 2 345 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Maurine 2 345 kV substation to support a new line from Maurine 2 345 kV substation to New Underwood 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-10-01
220822 | 170015 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 2 345 kV New Substation | Build a 345 kV new substation at Maurine 2 | 2024 ITP | Exclude | 2034-10-01
220822 | 170018 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 345/230 kV Transformer Ckt 1 (230 kV) | Install a new 345/230 kV transformer at the new Maurine 2 345 kV substation | 2024 ITP | Exclude | 2034-10-01
220822 | 170019 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 2 345/230 kV Terminal Equipment | Install 345 kV and 230 kV terminal equipment to support 345/230 kV transformer at the new Maurine 2 345 kV substation tied to the 230 kV terminal equipment at the existing Maurine substation. | 2024 ITP | Exclude | 2034-10-01
220822 | 170519 | Multi - Belfield 345 kV - Maurine 345 kV | Belfield 2 345/230 kV Transformer Ckt 1 (230 kV) | Install a new 345/230 kV transformer at the new Belfield 2 345 kV substation or replace existing parallel transformers at existing Belfield substation. | 2024 ITP | Exclude | 2034-11-01
220822 | 170520 | Multi - Belfield 345 kV - Maurine 345 kV | Belfield 230 kV Terminal Equipment | Install 230 kV terminal equipment to support 345/230 kV transformers at the Belfield 345 kV substation tied to the 230 kV terminal equipment at the existing Belfield substation. | 2024 ITP | Exclude | 2034-11-01
220822 | 170524 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 230 kV Terminal Upgrade | Install any necessary terminal equipment at Maurine substation to support a new line from Maurine 230 kV substation to Maurine 2 230 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2032-12-31
220822 | 170525 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine 2 230 kV Terminal Upgrade | Install any necessary terminal equipment at Maurine 2 230 kV substation to support a new line from Maurine 230 kV substation to Maurine 2 230 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-10-01
220822 | 170526 | Multi - Belfield 345 kV - Maurine 345 kV | Maurine – Maurine 2 230 kV Ckt 1 New Line | Build a 1-mile 230 kV Ckt 1 new line from Maurine 230 kV substation to Maurine 2 230 kV substation and install any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Exclude | 2034-10-01
220822 | 170527 | Multi - Belfield 345 kV - Maurine 345 kV | Belfield 345 kV Terminal Upgrade | Install 345 kV terminal equipment to support 345/230 kV transformers at the Belfield 345 kV substation tied to the 230 kV terminal equipment at the existing Belfield substation. | 2024 ITP | Exclude | 2034-11-01
210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Exclude | 2026-05-01
200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Exclude | 2027-12-31
200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Exclude | 2027-12-31
200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Exclude | 2027-12-31
210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Exclude | 2027-12-31
210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Exclude | 2026-09-30
220762 | 158042 | Multi - Norfolk-Stanton North 115 kV | Norfolk - Stanton North 115 kV line | Build new 7.5 mile 115 kV line from Norfolk to Stanton North | DPA-2021-October-1442 | Exclude | 2026-11-01
220762 | 158043 | Multi - Norfolk-Stanton North 115 kV | Hoskins 230/115 kV Transformer | Upgrade Hoskins 230/115 kV Transformer | DPA-2021-October-1442 | Exclude | 2026-11-01
210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Exclude | 2026-02-15
210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Exclude | 2026-07-31
210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Exclude | 2026-02-28
220868 | 159234 | Multi - Sioux Falls 115 kV System Reconfig | Sioux Falls 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Sioux Falls 115 kV substation to support tapping the existing line from Sioux Falls 115 kV substation to Beresford 115 kV substation for the new tap station Lincoln County 115 kV with a summer emergency rating of 193 MVA. | 2024 ITP | Exclude | 2028-06-30
220868 | 170518 | Multi - Sioux Falls 115 kV System Reconfig | Beresford 115 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at the Beresford 115 kV substation to support tapping the existing line from Beresford 115 kV substation to Sioux Falls 115 kV substation for the new tap station Lincoln County 115 kV with a summer emergency rating of 193 MVA. | 2024 ITP | Exclude | 2028-06-30
210544 | 112460 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sand Springs - Sheffield Steel 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA | 2019 ITP | Exclude | 2026-02-26
TBD | 170493 | Rebuild the MONT -MW7 to STRNDAHL-MW7 115kV Line 1 | Rebuild the MONT -MW7 to STRNDAHL-MW7 115kV Line 1 | Rebuild the existing MONT -MW7 to STRNDAHL-MW7 115 kV line 1 (11.97 miles) to a standard rating of 220 MVA | GI STUDIES | Exclude | 2027-12-31
TBD | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-06-01
TBD | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Exclude | 2026-06-01
TBD | 112307 | Sub - Oklaunion 345 kV Capacitive Reactive Power Support | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Exclude | 2026-05-15
TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | GI STUDIES | Exclude | 2027-08-01
TBD | 170191 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (GRDA) | Switch in the 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Exclude | 2027-04-01
TBD | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Exclude | 2027-10-01
TBD | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Exclude | 2027-04-01
TBD | 159460 | XFR - Edwardsville 161/115 kV | Edwardsville 161/115 kV Transformer Ckt 2 | Install new 161/115 transformer at Edwardsville 115 kV substation. | 2024 ITP | Exclude | 2027-12-31
TBD | 157620 | XFR - Franklin 161/69 kV Ckt 2 | Franklin 161/69 kV Transformer Ckt 2 | Install new 161/69 transformer Ckt 2 at Franklin 161/69 kV substation. | 2023 ITP | Exclude | 2026-12-31
TBD | 157383 | XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade | Sub 976 115/69 kV Transformer Ckt 2 (69 kV) | Install new 115/69 transformer at Fremont 115 kV substation | 2023 ITP | Exclude | 2027-12-31
TBD | 157384 | XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade | Fremont 115/69 kV Transformer Ckt 2 (115 kV) | Install 115 kV terminal equipment to support 115/69 transformer at Fremont 115 kV substation | 2023 ITP | Exclude | 2027-12-31
TBD | 50889 | XFR - Thedford 345/115 kV | Thedford 345/115 kV Transformer | Install new 345/115 kV 400 MVA transformer at Thedford substation. Install any necessary 115 kV terminal equipment. | HPILS | Exclude | 2027-12-31
TBD | 51002 | XFR - Thedford 345/115 kV | Thedford 345 kV Terminal Upgrades | Install any necessary 345 kV terminal equipment at Thedford associated with new 345/115 kV transformer. | HPILS | Exclude | 2027-12-31
TBD | 170384 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (138 kV) | Install new 345/138 transformer at Tulsa North 138 kV substation | 2024 ITP | Exclude | 2029-03-01
TBD | 170385 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/138 transformer at Tulsa North 345 kV substation with a summer emergency rating of 675 MVA. | 2024 ITP | Exclude | 2029-03-01
TBD | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Exclude | 2026-03-01
TBD | 102172 | Device - Clear Creek Tap 69 kV Cap Bank | Clear Creek Tap 69 kV Cap Bank | New cap bank(s) totaling 18 MVAR at Clear Creek Tap 69kV substation. | DPA-2018-June-902 | Include | 2024-01-31
TBD | 51560 | Line - Atoka - Atoka Pump - Pittsburg - Savanna - Army Ammo - McAlester City 69 kV Ckt 1 Rebuild | Atoka - Atoka Pump - Pittsburg 69 kV Ckt 1 Rebuild | Rebuild 27.1-mile 69 kV line from Atoka to Atoka Pump to Pittsburg. | 2016 ITPNT | Include | 2024-12-19
TBD | 82114 | Line - Cogar - OU SW 138 kV | Blanchard - OU SW 138 kV Ckt 1 Voltage Conversion | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. | DPA-2017-December-815 | Include | 2024-12-31
TBD | 169763 | Line - Dawson County 230 kV - Williston 230 kV New Line | Dawson County 230 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Dawson County 230 kV substation to support a new line from Dawson County 230 kV substation to Williston 230 kV substation with a summer emergency rating of 796 MVA. | 2024 ITP | Include | 2026-01-01
TBD | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Include | 2025-01-09
TBD | 144143 | Line - Ogallala Tri State - Ogallala NPPD 115 kV | Ogallala (Tri State) - Ogallala (NPPD) 115 kV (NPPD) | Upgrade the 115 kV tie from Ogallala Tri State to Ogallala NPPD. | 2021 ITP | Include | 2023-12-31
TBD | 157528 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Shidler 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Shidler 138 kV substation on the Webb City Tap to Shidler 138 kV line to achieve a summer emergency rating of 495 MVA. | 2023 ITP | Include | 2024-07-31
TBD | 112509 | Line - Wolf Creek - Blackberry 345 kV | Wolf Creek 345kV Terminal Equipment | Install terminal equipment at Wolf Creek and re-terminate Wolf Creek - Waverly 345 kV line to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 2019 ITP | Include | 2025-07-15
TBD | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Include | 2025-07-15
TBD | 143591 | Line- Catoosa - Blue Circle 69 kV | Blue Circle - Catoosa 69 kV Ckt 1 Rebuild | Rebuild 3.5 miles of 69 kV line from Catoosa to Blue Circle and upgrade any necessary terminal equipment at Catoosa and/or Blue Circle | 2021 ITP | Include | 2024-12-18
TBD | 158640 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 115 kV | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. | 2023 ITP | Include | 2025-04-02
TBD | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Include | 2025-04-02
TBD | 158646 | Multi - Atlantic- Craig - West Gardener 345/115 kV | West Gardner - Craig 345 kV | Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic – Eudora Township 115 kV line. | 2023 ITP | Include | 2025-04-02
TBD | 159064 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Terminal Equipment 345 kV Transformer(345 kV) | Install 345 kV terminal equipment to support 345/115 transformer at Atlantic 345 kV substation | 2023 ITP | Include | 2025-04-02
TBD | 170553 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic – Pacific #2 115 kV New Line | Build a 1.7-mile 115 kV new east line from Atlantic 115 kV substation to Atlantic 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Include | 2025-04-02
TBD | 158645 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Eudora Township – Atlantic 115 kV Tap | Tap the existing Eudora Township - Atlantic 115 kV near Atlantic | 2023 ITP | Include | 2025-04-01
TBD | 158648 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic 345/115 kV Transformer (115 kV) | Install two new 345/115 transformer at Atlantic 115 kV substation | 2023 ITP | Include | 2025-08-01
TBD | 170552 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic – Pacific #1 115 kV New Line | Build a 4.2-mile 115 kV new west line from Atlantic 115 kV substation to Pacific 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2023 ITP | Include | 2025-12-31
TBD | 122866 | Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV | Mooreland - Pic 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Mooreland 138 kV for the Mooreland to Pic 138 kV line to achieve a summer emergency rating of 187 MVA rating | 2020 ITP | Include | 2023-02-23
TBD | 51526 | Multi - Driftwood 138/69 kV Substation and Transformer | Driftwood 138 kV Substation | Tap the 138 kV line from Byron to Cherokee City to construct new Driftwood substation. Install any required 138 kV terminal upgrades required to install 138/69 kV transformer. | 2016 ITPNT | Include | 2023-07-31
TBD | 51527 | Multi - Driftwood 138/69 kV Substation and Transformer | Driftwood 138/69 kV Transformer | Install new 138/69 kV transformer at new Driftwood substation. Install new 69 kV terminal for 69 kV line from Hazelton Junction. | 2016 ITPNT | Include | 2023-07-31
TBD | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Include | 2025-01-29
TBD | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Include | 2024-11-18
TBD | 122850 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Transformer Ckt 1 | Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA | 2020 ITP | Include | 2024-11-18
TBD | 122851 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Transformer Ckt 2 | Install a new 345/138 kV transformer to achieve a summer emergency rating of 478 MVA | 2020 ITP | Include | 2024-12-18
TBD | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Include | 2025-01-01
TBD | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Include | 2025-01-29
TBD | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Include | 2025-01-23
TBD | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Include | 2025-01-23
TBD | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. | 2020 ITP | Include | 2024-12-18
TBD | 72024 | Multi - Park Community - Sunshine 138 kV | El Reno - Mustang 138 kV Ckt 1 Voltage Conversion | Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. | DPA-2017-August-767-774-776 | Include | 2024-05-30
TBD | 72025 | Multi - Park Community - Sunshine 138 kV | Mustang - Sara Road 138 kV Ckt 1 Voltage Conversion | Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. | DPA-2017-August-767-774-776 | Include | 2024-06-15
TBD | 72026 | Multi - Park Community - Sunshine 138 kV | Sara Road - Sunshine 138 kV Ckt 1 Voltage Conversion | Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. | DPA-2017-August-767-774-776 | Include | 2024-04-01
TBD | 72031 | Multi - Park Community - Sunshine 138 kV | Concho - Kingfisher SW 138 kV Ckt 1 New Line | Construct new 8.5 mile 138 kV line from Concho - Kingfisher SW. | DPA-2017-August-767-774-776 | Include | 2024-12-30
TBD | 156294 | Multi - Siloam Springs-Siloam Springs City 161 kV Terminal Upgrades | Siloam Springs City 161 kV Terminal Upgrade | Upgrade terminal equipment at Siloam Springs City 161 kV substation | 2022 ITP | Include | 2024-12-11
TBD | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Include | 2025-10-08
TBD | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Include | 2025-10-08
TBD | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Include | 2025-11-30
TBD | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Southgate - Westmoore Tap 138 kV Extend Line | Extend Southgate - Westmoore Tap 138 kV 0.76 miles to Westmoore 138 kV substation, including structures suited for double circuit configuration. | 2023 ITP | Include | 2025-12-01
TBD | 157392 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Westmoore 138 kV Terminal Upgrade #2 | Install any necessary terminal equipment at Westmoore 138 kV substation to support a new line from Westmoore substation to Southgate 138 kV substation with a summer emergency rating of 308 MVA. | 2023 ITP | Include | 2025-12-01
TBD | 157393 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Pennsylvania 138 kV Terminal Upgrade | Install a 2000 Amp switch at the Pennsylvania 138 kV substation. | 2023 ITP | Include | 2025-12-01
TBD | 122627 | Spring Creek to Sooner 345kV GEN-2016-119 Interconnection Costs | Sooner - Spring Creek GEN-2016-119 Tap 345kV Interconnection Substation (DISIS-2016-002-3) | Construct a new EHV substation. Install 4-345 kV 3000A breakers, line relaying, disconnect switches, and associated equipment. Costs of this new substation are split by GEN-2016-100, GEN-2016-101, and GEN-2016-119 | GI STUDIES | Include | 2025-08-15
TBD | 72006 | Sub - Bismarck 115 kV and North Bismarck 115 kV Terminal Upgrades | Bismarck 115 kV Terminal Upgrades | Replace CTs at Bismarck 115 kV substation to increase rating of Bismarck - East Bismarck 115 kV line to at least 85 MVA. This is a mitigation upgrade resulting from the Sponsored Upgrade Study #SUS-002 CPEC North Bismarck Breaker. Costs will be Directly Assigned to CPEC. | SUS-002 | Include | 2025-04-17
TBD | 112403 | Sub - Firth 115kV | Firth Cap Bank 115kV Ckt 1 | Install new 15 MVAR capacitor bank at Firth 115 kV substation. | 2019 ITP | Include | 2024-07-02
TBD | 112404 | Sub - Firth 115kV | Firth 115 kV Substation Expansion | Expand the existing Firth 115 kV substation to accommodate a new 15 MVAR capacitor bank. | 2019 ITP | Include | 2024-07-02
TBD | 122717 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 345 kV Terminal Upgrades Transformer Ckt 1 | Upgrade terminal equipment at GRDA1 345 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Include | 2023-05-01
TBD | 122718 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 161 kV Terminal Upgrades Transformer Ckt 1 | Upgrade terminal equipment at GRDA1 161 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Include | 2023-05-01
TBD | 122801 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 345 kV Terminal Upgrades Transformer Ckt 2 | Upgrade terminal equipment at GRDA1 345 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Include | 2023-05-01
TBD | 122802 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 161 kV Terminal Upgrades Transformer Ckt 2 | Upgrade terminal equipment at GRDA1 161 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Include | 2023-05-01
TBD | 71933 | Sub - Holt County 345kV (Tap Grand Prairie - Grand Island 345kV) - GEN-2015-023 Addition | Holt County 345kV (Tap Grand Prairie - Grand Island 345kV) - GEN-2015-023 Addition (TOIF) | Holt County 345kV Substation - Install 345kV line terminal to connect to the Interconnection Customer Interconnection Facilities. Work to include line switch, dead-end towers, metering, current transformers, potential transformers, and associated and miscellaneous material.; One (1) approximately five (5) mile 345 kV overhead transmission line from the Interconnection Customer's collector substation to the Transmission Owner's Holt County 345 kV substation. | GI STUDIES | Include | 2022-09-30
TBD | 71934 | Sub - Holt County 345kV (Tap Grand Prairie - Grand Island 345kV) - GEN-2015-023 Addition | Holt County 345kV (Tap Grand Prairie - Grand Island 345kV) - GEN-2015-023 Addition (NU) | Holt County 345 kV Substation – 345 kV substation bus work; add one (1) 345 kV line terminal, four (4) 345 kV circuit breakers, control panel, disconnect switches, and all associated and miscellaneous equipment. | GI STUDIES | Include | 2022-09-30
TBD | 51764 | Sub - Tupelo - Tupelo Tap 138 kV Terminal Upgrades | Tupelo 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Tupelo to increase the rating of the 138 kV line between Tupelo substation and Tupelo Tap substation. | 2017 ITP10 | Include | 2023-12-31
TBD | 122792 | Viola 345/138 kV Transformer CKT 2 | Viola 345/138 kV Transformer CKT 2 (DISIS-2016-002-2) | Install a new 345 kV terminal on a new rung consisting of two (2) breakers, four (4) switches, and two (2) control panels. Install a new 138 kV terminal on an existing rung consisting of one (1) breaker, three (3) switches, three (3) PTs, and one (1) 400/440 MVA 345-138 kV transformer with LTCs. Network Upgrade shared among fourteen requests: GEN-2016-100, GEN-2016-101, GEN-2016-119, GEN-2016-128, GEN-2016-133, GEN-2016-134, GEN-2016-137, GEN-2016-138, GEN-2016-139, GEN-2016-141, GEN-2016-142, GEN-2016-145, GEN-2016-146, GEN-2016-153 | GI STUDIES | Include | 2024-11-21
TBD | 158654 | XFR - 87th St. 345/115 kV. Ckt 2 | 87th St. 345/115 kV Transformer | Transformer ratings 400/440/400/440 MVA (SN/SE/WN/WE) must be met. Terminal equipment must support new 345/115 kV transformer with 675 MVA summer emergency rating. | 2023 ITP | Include | 2024-05-30
TBD | 122705 | Hoyt - JEC 345kV Rebuild (DISIS-2017-001) | Hoyt - JEC 345kV Rebuild (DISIS-2017-001) | Rebuild the existing JEC - Hoyt 345 kV with normal/minimal emergency rating of 1792 MVA. | DISIS-2017-001-P2 | Exclude | 48
TBD | 143236 | Neset to Tioga 230kV Rebuild (DISIS-2017-001) | Neset to Tioga 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Neset to Tioga 230kV 1 mile line to achieve a minimum summer/emergency rating of 615 MVA | DISIS-2017-001-P2 | Exclude | 12
TBD | 143237 | Tioga 230kV Terminal Upgrades (DISIS-2017-001) | Tioga 230kV Terminal Upgrades (DISIS-2017-001) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 615 MVA | DISIS-2017-001-P2 | Exclude | 18
TBD | 143226 | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001-P2 | Exclude | 36
TBD | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | Exclude | 36
TBD | 159067 | Partly rebuild the Elm Creek to North Manhattan 230 kV line | Partly rebuild the Elm Creek to North Manhattan 230 kV line | Partly reconductor 2.9 mile of the Elm Creek to North Manhattan 230 kV line to achieve a minimum rating of 390 MVA | DISIS-2017-002 | Exclude | 48
TBD | 156851 | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Exclude | 48
TBD | 156516 | Terminal Upgrades at Archie 161kV | Terminal Upgrades at Archie 161kV | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Exclude | 48
TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Exclude | 24
TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Exclude | 36
TBD | 158556 | Delaware Tap to T.S.E. 138 kV Rebuild | Delaware Tap to T.S.E. 138 kV Rebuild | Rebuild the existing Delaware Tap to T.S.E. 138 kV 2.09 mile line with a minimum summer emergency rating of 295 MVA | DISIS-2018-001 | Exclude | 36
TBD | 158555 | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 170 MVA | DISIS-2018-001 | Exclude | 36
TBD | 170507 | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | DISIS-2018-002 / DISIS-2019-001 | Exclude | TBD
TBD | 158601 | Rebuild Columbus SE to G19-039-TAP 115 kV | Rebuild Columbus SE to G19-039-TAP 115 kV | Rebuild the existing COL.SE 7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | DISIS-2018-002 / DISIS-2019-001 | Exclude | TBD
TBD | 158603 | Rebuild Rising to G19-039-TAP 115 kV | Rebuild Rising to G19-039-TAP 115 kV | Rebuild the existing RISNGCY7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | DISIS-2018-002 / DISIS-2019-001 | Exclude | TBD
TBD | 170575 | Catoosa Terminal Upgrade | Catoosa Terminal Upgrade | Replace switch, jumpers, and CTs at Catoosa 138 kV to achieve a minimum rating of 218 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170577 | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Rebuild the existing Comanche Tap to Duncan Bois D' Arc 138 kV line (17.69 miles) to a minimum rating of 190 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170581 | Duncan Eastside to Duncan Cherokee 138 kV Line Rebuild | Duncan Eastside to Duncan Cherokee 138 kV Line Rebuild | Rebuild the existing Duncan Eastside to Duncan Cherokee 138 kV line (3.53 miles) to a minimum rating of 140 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170579 | Duncan Eastside to OMDUNE-4 138 kV Line Rebuild | Duncan Eastside to OMDUNE-4 138 kV Line Rebuild | Rebuild the existing Duncan Eastside to OMDUNE-4 138 kV line (1.26 miles) to a minimum rating of 135 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170582 | Duncan Substation to Duncan Cherokee 138 kV Line Rebuild | Duncan Substation to Duncan Cherokee 138 kV Line Rebuild | Rebuild the existing Duncan Substation to Duncan Cherokee 138 kV line (1.6 miles) to a minimum rating of 144 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170578 | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Rebuild the existing Duncan to Duncan Bois D' Arc 138 kV line (3.9 miles) to a minimum rating of 190 MVA. Upgrade RCTL at Duncan | DISIS-2020-001 | Exclude | 36
TBD | 170612 | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 (2.98 miles) to a minimum rating of 400 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170588 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line 1 (19 miles) to a minimum rating of 215 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170585 | Rebuild the MARTCIT5 to REDEL 5 161 kV line 1 | Rebuild the MARTCIT5 to REDEL 5 161 kV line 1 | Rebuild the MARTCIT5 to REDEL 5 161 kV line 1 (3.86 miles) to a minimum rating of 400 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170586 | Rebuild the SHWNMSN5 to LENEXA 5 161 kV line 1 | Rebuild the SHWNMSN5 to LENEXA 5 161 kV line 1 | Rebuild the SHWNMSN5 to LENEXA 5 161 kV line 1 (3.91 miles) to a minimum rating of 400 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170587 | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 (4.22 miles) to a minimum rating of 400 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170621 | Replace Snyder 138/69 kV Transformer | Replace Snyder 138/69 kV Transformer | Replace the 138/69 kV transformer at Snyder to achieve an emergency rating of 89 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170576 | Sunnyside to G20-074-TAP 345 kV New Line Circuit 2 | Sunnyside to G20-074-TAP 345 kV New Line Circuit 2 | Build a new Sunnyside to G20-074-Tap 345 kV Line (13.1 miles) to a minimum SN/SE rating of 1151/1301 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170622 | Sunnyside to Uniroyal 138 kV Line Rebuild | Sunnyside to Uniroyal 138 kV Line Rebuild | Rebuild the existing Sunnyside to Uniroyal 138 kV line (5.58 miles) to a minimum of 255 MVA | DISIS-2020-001 | Exclude | 36
TBD | 170637 | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2021-001 | Exclude | 60
TBD | TBD | 5SEDALA to SEDALIA5 161 kV Ckt 1 Terminal Upgrade | 5SEDALA to SEDALIA5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the 5SEDALA to SEDALIA5 161 kV line Ckt 1 to achieve a minimum rating of 297 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the NMANHT6 to ELMCREK6 230 kV line Ckt 1 to achieve a minimum rating of 439 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | MIDLADN3 to MIDLADS3 115 kV Bus Tie Upgrade | MIDLADN3 to MIDLADS3 115 kV Bus Tie Upgrade | Upgrade Equipment on the MIDLADN3 to MIDLADS3 115 kV bus tie to achieve a minimum rating of 298 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at PHILL 7 345 kV to achieve a minimum rating of 880 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at PHILL 7 345 kV to achieve a minimum rating of 760 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 237 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild the ARCHIE 5 to G17-108-TAP 161 kV line Ckt 1 | Rebuild the ARCHIE 5 to G17-108-TAP 161 kV line Ckt 1 | Rebuild the ARCHIE 5 to G17-108-TAP 161 kV line Ckt 1 and Upgrade the Terminal Equipment to achieve a minimum rating of 470 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Build a new AXTELL 345/115 kV Transformer 2 | Build a new AXTELL 345/115 kV Transformer 2 | Build a new AXTELL 345/115 kV Transformer 2 to a minimum rating of 336 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | DISIS-2021-001 | Exclude | 0
TBD | TBD | Build a new 50 MVAR cap bank at Viola 138 kV | Build a new 50 MVAR cap bank at Viola 138 kV | Build a new 50 MVAR cap bank at VIOLA 138 kV | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Brown Substation Expansion | Brown Substation Expansion | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. Upgrade BROWN Substation to a breaker-and-a-half configuration. | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild ROSEVLY4 to MOORLND4 138 kV line 1 | Rebuild ROSEVLY4 to MOORLND4 138 kV line 1 | Rebuild the ROSEVLY4 to MOORLND4 138 kV line CKT1 (37.25) miles to a minimum rating of 205 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild NOELSW4 to ROSEVLY4 138 kV line 1 | Rebuild NOELSW4 to ROSEVLY4 138 kV line 1 | Rebuild the NOELSW4 to ROSEVALY4 138 kV line CKT1 (8.15 miles) to a minimum rating of 200 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild SOUTHRD4 to ROMNOSE4 138 kV line 1 | Rebuild SOUTHRD4 to ROMNOSE4 138 kV line 1 | Rebuild the SOUTHRD4 to ROMNOSE4 138 kV line CKT1 (17.28 miles) to a standard rating of 478 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild DEQUEEN2 to DEQUEEN 2 69 kV line 1 | Rebuild DEQUEEN2 to DEQUEEN 2 69 kV line 1 | Rebuild the DEQUEEN2 to DEQUEEN 2 69 kV line CKT1 (3.25 miles) to a minimum rating of 51 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild SW5th4 to CLASSEN4 138 kV line 1 | Rebuild SW5th4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a standard rating of 478 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Build a new North Hays to Chelotalah 115 kV line 1 | Build a new North Hays to Chelotalah 115 kV line 1 | Build a new NorthHays to Chelotalah 115kV line CKT1 (8 miles) to a minimum rating of 206/239 | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Rebuild AXTELL7 to KEARNEY7 115 kV line 1 | Rebuild AXTELL7 to KEARNEY7 115 kV line 1 | Rebuild the AXTELL7 to KERANEY7 115kV line CKT1 (10.74 miles) to a minimum rating of 254 MVA | DISIS-2021-001 | Exclude | TBD (36-month lead time)
TBD | TBD | Reconfigure Little City to Brown 138 kV Line | Reconfigure Little City to Brown 138 kV Line | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | DISIS-2021-001 | Exclude | TBD (36-month lead time)

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Solution
00ALL | 2025 Annual Interim | ERIS | Non-converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | 2025 Annual Interim | ERIS | Thermal | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | 2025 Annual Interim | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
03ALL | 2025 Annual Interim | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | 2025 Annual Interim | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Solution
Non-Converged | 00ALL | 0 | 24SP | " | Non-Converge | [5 empty] | None | N/A | None
Non-Converged | 00ALL | 0 | 27SP | " | Non-Converge | [5 empty] | None | N/A | None
Non-Converged | 00ALL | 0 | 27WP | " | Non-Converge | [5 empty] | None | N/A | None
Thermal | 00ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None | N/A | None
Thermal | 00ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None | N/A | None
Thermal | 00ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None | N/A | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on UNIONTP5 161.00 (636225) 161 kV Bus a. Apply fault at the UNIONTP5 161.00 (636225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 5 (636200) 161.0 kV to UNIONTP5 (636225) 161.0 kV Transmission Circuit #1 b.2. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. UNIONTP5 (636225) 161.0 kV to UNIONCF5 (638030) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on WRIGHT 5 161.00 (636050) 161 kV Bus a. Apply fault at the WRIGHT 5 161.00 (636050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBSTER5 (636001) 161.0 kV to WRIGHT 5 (636050) 161.0 kV Transmission Circuit #1 b.2. WRIGHT 5 (636050) 161.0 kV to WRIGHT 8 (636051) 69.0 kV Two Winding #1 b.3. WRIGHT 5 (636050) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips INTRPD W (635352 and 635354), POMEROY W (636027, 636033 and 636035). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on WASHBRN5 161.00 (636210) 161 kV Bus a. Apply fault at the WASHBRN5 161.00 (636210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DYSART 5 (631086) 161.0 kV to WASHBRN5 (636210) 161.0 kV Transmission Circuit #1 b.2. WASHBRN5 (636210) 161.0 kV to WASHBRN8 (636211) 69.0 kV Two Winding #1 b.3. WASHBRN5 (636210) 161.0 kV to SHAULISRD5 (636215) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on TRAER 5 161.00 (631083) 161 kV Bus a. Apply fault at the TRAER 5 161.00 (631083) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1365 POI (43654) 161.0 kV to TRAER 5 (631083) 161.0 kV Transmission Circuit #1 b.2. TRAER 5 (631083) 161.0 kV to TRAER 8 (630027) 69.0 kV Two Winding #1 b.3. TRAER 5 (631083) 161.0 kV to DYSART 5 (631086) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on SQUARED7 115.00 (631032) 115 kV Bus a. Apply fault at the SQUARED7 115.00 (631032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT7 (631015) 115.0 kV to SQUARED7 (631032) 115.0 kV Transmission Circuit #1 b.2. PRAR CK7 (631017) 115.0 kV to SQUARED7 (631032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP5 (631029) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on ABBOTT 5 161.00 (631000) 161 kV Bus a. Apply fault at the ABBOTT 5 161.00 (631000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABBOTT 5 (631000) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on TOLEDO 5 161.00 (631001) 161 kV Bus a. Apply fault at the TOLEDO 5 161.00 (631001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLEDO 5 (631001) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on TOLEDO 5 161.00 (631001) 161 kV Bus a. Apply fault at the TOLEDO 5 161.00 (631001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLEDO 5 (631001) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on NEWHAL5 161.00 (631009) 161 kV Bus a. Apply fault at the NEWHAL5 161.00 (631009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHAL5 (631009) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP5 (631029) 161.0 kV to NUTHTCH5 (631166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on ROSEHLW5 161.00 (631034) 161 kV Bus a. Apply fault at the ROSEHLW5 161.00 (631034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHLW5 (631034) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY 5 (631048) 161.0 kV to CGORDO_5 (631049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY 5 (631048) 161.0 kV to COLBY5 (631202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on MT VERN5 161.00 (631073) 161 kV Bus a. Apply fault at the MT VERN5 161.00 (631073) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MT VERN5 (631073) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN 5 (631081) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on TIMBRCK5 161.00 (631082) 161 kV Bus a. Apply fault at the TIMBRCK5 161.00 (631082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRCK5 (631082) 161.0 kV to M-TOWN_W5 (631128) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on DYSART 5 161.00 (631086) 161 kV Bus a. Apply fault at the DYSART 5 161.00 (631086) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DYSART 5 (631086) 161.0 kV to VINTON 5 (631087) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on PCI 5 161.00 (631090) 161 kV Bus a. Apply fault at the PCI 5 161.00 (631090) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCI 5 (631090) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 5 (631107) 161.0 kV to NEWTON 5 (631119) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 5 (631107) 161.0 kV to NEANKNY5 (635710) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on M-TOWN_W5 161.00 (631128) 161 kV Bus a. Apply fault at the M-TOWN_W5 161.00 (631128) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN_W5 (631128) 161.0 kV to STRY_CO5 (631156) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on NUTHTCH5 161.00 (631166) 161 kV Bus a. Apply fault at the NUTHTCH5 161.00 (631166) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 8 (630046) 69.0 kV to JASPER 5 (631107) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY S8 (630213) 69.0 kV to EMERY 5 (631048) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY N8 (630214) 69.0 kV to EMERY 5 (631048) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV to IAFINDP5 (631029) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on TIMBRCK5 161.00 (631082) 161 kV Bus a. Apply fault at the TIMBRCK5 161.00 (631082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCREEK8 (630963) 69.0 kV to TIMBRCK5 (631082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV to WELSBRG G (656301) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on STON PT5 161.00 (631080) 161 kV Bus a. Apply fault at the STON PT5 161.00 (631080) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT5 (631080) 161.0 kV to STON PT7 (631015) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on KILLDEER3 345.00 (631199) 345 kV Bus a. Apply fault at the KILLDEER3 345.00 (631199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KILLDEER3 (631199) 345.0 kV to EMERY 5 (631048) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on STON PT7 115.00 (631015) 115 kV Bus a. Apply fault at the STON PT7 115.00 (631015) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT7 (631015) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on FRANKLN5 161.00 (636230) 161 kV Bus a. Apply fault at the FRANKLN5 161.00 (636230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on WALL LK5 161.00 (636235) 161 kV Bus a. Apply fault at the WALL LK5 161.00 (636235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LK5 (636235) 161.0 kV to WALL LK8 (636236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SHEFFLD5 161.00 (656201) 161 kV Bus a. Apply fault at the SHEFFLD5 161.00 (656201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY 5 (631048) 161.0 kV to SHEFFLD5 (656201) 161.0 kV Transmission Circuit #1 b.2. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.3. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.4. SHEFFLD5 (656201) 161.0 kV to WSHEFFLD8 (656205) 69.0 kV Two Winding #1 b.5. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on LIME CK L2 5161.00 (631160) 161 kV Bus a. Apply fault at the LIME CK L2 5161.00 (631160) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIME CK L1 5 (631047) 161.0 kV to LIME CK L2 5 (631160) 161.0 kV Transmission Circuit #z b.2. EMERY 5 (631048) 161.0 kV to LIME CK L2 5 (631160) 161.0 kV Transmission Circuit #2 b.3. BARTON5 (631154) 161.0 kV to LIME CK L2 5 (631160) 161.0 kV Transmission Circuit #1 b.4. LIME CK L2 5 (631160) 161.0 kV to LIME CK J2 8 (630198) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on HAMPTONTAP5 161.00 (656207) 161 kV Bus a. Apply fault at the HAMPTONTAP5 161.00 (656207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.2. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.3. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.4. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on ALDNRRLTP8 69.000 (656795) 69 kV Bus a. Apply fault at the ALDNRRLTP8 69.000 (656795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALDNBUCKEYE8 (630859) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 b.2. ALDEN8 (656753) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 b.3. ALDENJCT8 (656755) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on ESHEFFTP8 69.000 (656185) 69 kV Bus a. Apply fault at the ESHEFFTP8 69.000 (656185) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ESHEFFLD8 (656183) 69.0 kV to ESHEFFTP8 (656185) 69.0 kV Transmission Circuit #1 b.2. ESHEFFTP8 (656185) 69.0 kV to GLCOATNG8 (656189) 69.0 kV Transmission Circuit #1 b.3. ESHEFFTP8 (656185) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on FERNTAP8 69.000 (656303) 69 kV Bus a. Apply fault at the FERNTAP8 69.000 (656303) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APLNGTON8 (656271) 69.0 kV to FERNTAP8 (656303) 69.0 kV Transmission Circuit #1 b.2. FERN8 (656287) 69.0 kV to FERNTAP8 (656303) 69.0 kV Transmission Circuit #1 b.3. FERNTAP8 (656303) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on HICKSTAP 69.000 (656307) 69 kV Bus a. Apply fault at the HICKSTAP 69.000 (656307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REINBECK8 (630861) 69.0 kV to HICKSTAP (656307) 69.0 kV Transmission Circuit #1 b.2. DINSDALE8 (656281) 69.0 kV to HICKSTAP (656307) 69.0 kV Transmission Circuit #1 b.3. HICKS8 (656293) 69.0 kV to HICKSTAP (656307) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on MELRSTAP8 69.000 (656297) 69 kV Bus a. Apply fault at the MELRSTAP8 69.000 (656297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD 8 (630350) 69.0 kV to MELRSTAP8 (656297) 69.0 kV Transmission Circuit #1 b.2. MELROSE8 (656295) 69.0 kV to MELRSTAP8 (656297) 69.0 kV Transmission Circuit #1 b.3. MELRSTAP8 (656297) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on ROLANDTP8 69.000 (656790) 69 kV Bus a. Apply fault at the ROLANDTP8 69.000 (656790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLAND8 (656783) 69.0 kV to ROLANDTP8 (656790) 69.0 kV Transmission Circuit #1 b.2. GARDEN C8 (656789) 69.0 kV to ROLANDTP8 (656790) 69.0 kV Transmission Circuit #1 b.3. ROLANDTP8 (656790) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on TRAERTAP8 69.000 (656299) 69 kV Bus a. Apply fault at the TRAERTAP8 69.000 (656299) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TRAER 8 (630027) 69.0 kV to TRAERTAP8 (656299) 69.0 kV Transmission Circuit #1 b.2. CLUTIER8 (656273) 69.0 kV to TRAERTAP8 (656299) 69.0 kV Transmission Circuit #1 b.3. DINSDALE8 (656281) 69.0 kV to TRAERTAP8 (656299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on WALLLKTP8 69.000 (656899) 69 kV Bus a. Apply fault at the WALLLKTP8 69.000 (656899) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LAK8 (656897) 69.0 kV to WALLLKTP8 (656899) 69.0 kV Transmission Circuit #1 b.2. WALLLKTP8 (656899) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 b.3. WALLLKTP8 (656899) 69.0 kV to PRESTAGE8 (656915) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on BUTLER 5 161.00 (636240) 161 kV Bus a. Apply fault at the BUTLER 5 161.00 (636240) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.2. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. BUTLER 5 (636240) 161.0 kV to BUTLER 9 (636241) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on ELDORA8 69.000 (630841) 69 kV Bus a. Apply fault at the ELDORA8 69.000 (630841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORA8 (630841) 69.0 kV to UNION_CB8 (630921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on CONRAD8 69.000 (630923) 69 kV Bus a. Apply fault at the CONRAD8 69.000 (630923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD8 (630923) 69.0 kV to GREENMNTN8 (630925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on MARION K2 7 115.00 (631195) 115 kV Bus a. Apply fault at the MARION K2 7 115.00 (631195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARION J2 8 (630759) 69.0 kV to MARION K2 7 (631195) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on HUBBRDRURAL869.000 (630840) 69 kV Bus a. Apply fault at the HUBBRDRURAL869.000 (630840) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUBBRDRURAL8 (630840) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on LATIMER8 69.000 (636317) 69 kV Bus a. Apply fault at the LATIMER8 69.000 (636317) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LATIMER8 (636317) 69.0 kV to WB LATM 8 (636318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to HUBBRDPUMPT8 (630842) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on GREENMNTN8 69.000 (630925) 69 kV Bus a. Apply fault at the GREENMNTN8 69.000 (630925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREENMNTN8 (630925) 69.0 kV to FLETCHR J1 8 (630929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on SCOTTTAP8 69.000 (636086) 69 kV Bus a. Apply fault at the SCOTTTAP8 69.000 (636086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTTAP8 (636086) 69.0 kV to LKCORNL8 (656875) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on COULTR 8 69.000 (630357) 69 kV Bus a. Apply fault at the COULTR 8 69.000 (630357) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTR 8 (630357) 69.0 kV to WB LATM 8 (636318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on CALAMUS7 115.00 (631023) 115 kV Bus a. Apply fault at the CALAMUS7 115.00 (631023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTLIFF7 (631022) 115.0 kV to CALAMUS7 (631023) 115.0 kV Transmission Circuit #1 b.2. CALAMUS7 (631023) 115.0 kV to CALAMUS9 (629093) 34.5 kV Two Winding #1 b.3. CALAMUS7 (631023) 115.0 kV to E CALMS7 (631024) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTNW8 (636315) 69.0 kV to LATIMER8 (636317) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on STATECENTER869.000 (630961) 69 kV Bus a. Apply fault at the STATECENTER869.000 (630961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATECENTER8 (630961) 69.0 kV to LAMOILLEREC8 (630962) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on BELMNDJ8 69.000 (630469) 69 kV Bus a. Apply fault at the BELMNDJ8 69.000 (630469) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELMNDJ8 (630469) 69.0 kV to EATNTAP8 (630470) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on COULTR 8 69.000 (630357) 69 kV Bus a. Apply fault at the COULTR 8 69.000 (630357) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTR 8 (630357) 69.0 kV to SCOTTTAP8 (636086) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on DIKEMORRISN869.000 (630860) 69 kV Bus a. Apply fault at the DIKEMORRISN869.000 (630860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIKEMORRISN8 (630860) 69.0 kV to REINBECK8 (630861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on IAFINDP8 69.000 (630341) 69 kV Bus a. Apply fault at the IAFINDP8 69.000 (630341) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTNW8 (636315) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on DIKEMORRISN869.000 (630860) 69 kV Bus a. Apply fault at the DIKEMORRISN869.000 (630860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIKEMORRISN8 (630860) 69.0 kV to GRNDYCTR8 (656289) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTNW8 (636315) 69.0 kV to SHEFFLD8 (636316) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on IAFINDP8 69.000 (630341) 69 kV Bus a. Apply fault at the IAFINDP8 69.000 (630341) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV to FARM_TAP8 (656769) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on NBELMDT8 69.000 (630467) 69 kV Bus a. Apply fault at the NBELMDT8 69.000 (630467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBELMDT8 (630467) 69.0 kV to BELMNDJ8 (630469) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on WELSBRGDIST869.000 (630862) 69 kV Bus a. Apply fault at the WELSBRGDIST869.000 (630862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRGDIST8 (630862) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to ELDORA8 (630841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on LAMOILLEREC869.000 (630962) 69 kV Bus a. Apply fault at the LAMOILLEREC869.000 (630962) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMOILLEREC8 (630962) 69.0 kV to TIMBERCREEK8 (630963) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on ACKLEY 5 161.00 (636229) 161 kV Bus a. Apply fault at the ACKLEY 5 161.00 (636229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on MEC WELSBRG5161.00 (636217) 161 kV Bus a. Apply fault at the MEC WELSBRG5161.00 (636217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEC WELSBRG5 (636217) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on BERTRAM5 161.00 (631092) 161 kV Bus a. Apply fault at the BERTRAM5 161.00 (631092) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.2. BERTRAM5 (631092) 161.0 kV to BERTRAM7 (631020) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV to IAFINDP5 (631029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on J1365 POI 161.00 (43654) 161 kV Bus a. Apply fault at the J1365 POI 161.00 (43654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1365 POI (43654) 161.0 kV to ABBOTT 5 (631000) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on J1952 POI 161.00 (49524) 161 kV Bus a. Apply fault at the J1952 POI 161.00 (49524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1952 POI (49524) 161.0 kV to EMERY 5 (631048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCN8 (630339) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the MGS ST (629216) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCN8 (630339) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the MGS ST (629216) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on CONRAD 8 69.000 (630350) 69 kV Bus a. Apply fault at the CONRAD 8 69.000 (630350) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD 8 (630350) 69.0 kV to CONRAD8 (656275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on BELMNDJ8 69.000 (630469) 69 kV Bus a. Apply fault at the BELMNDJ8 69.000 (630469) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELMNDJ8 (630469) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to PLEASANT8 (656781) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on FLETCHR J1 869.000 (630929) 69 kV Bus a. Apply fault at the FLETCHR J1 869.000 (630929) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR J1 8 (630929) 69.0 kV to FLETCHR J2 8 (630977) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on M-TOWN K2 7 115.00 (631004) 115 kV Bus a. Apply fault at the M-TOWN K2 7 115.00 (631004) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on STON PT7 115.00 (631015) 115 kV Bus a. Apply fault at the STON PT7 115.00 (631015) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT7 (631015) 115.0 kV to 6 ST 7 (631016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAR CK7 (631017) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on MARION K1 7 115.00 (631019) 115 kV Bus a. Apply fault at the MARION K1 7 115.00 (631019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARION K1 7 (631019) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on W.BRCH 7 115.00 (631021) 115 kV Bus a. Apply fault at the W.BRCH 7 115.00 (631021) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BRCH 7 (631021) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on SCOTTTAP8 69.000 (636086) 69 kV Bus a. Apply fault at the SCOTTTAP8 69.000 (636086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTTAP8 (636086) 69.0 kV to SCOTT8 (656913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on WALL LK8 69.000 (636236) 69 kV Bus a. Apply fault at the WALL LK8 69.000 (636236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LK8 (636236) 69.0 kV to BLAIRSBU8 (656843) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on WALL LK8 69.000 (636236) 69 kV Bus a. Apply fault at the WALL LK8 69.000 (636236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LK8 (636236) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on DUMONT 8 69.000 (636249) 69 kV Bus a. Apply fault at the DUMONT 8 69.000 (636249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMONT 8 (636249) 69.0 kV to DUMONT8 (656021) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on SHEFFLD8 69.000 (636316) 69 kV Bus a. Apply fault at the SHEFFLD8 69.000 (636316) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFLD8 (636316) 69.0 kV to MECSHDFT8 (656199) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on ACKLEY 8 69.000 (636319) 69 kV Bus a. Apply fault at the ACKLEY 8 69.000 (636319) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACKLEY 8 (636319) 69.0 kV to ACKLYTAP8 (656751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on BEAVERCK8 69.000 (656007) 69 kV Bus a. Apply fault at the BEAVERCK8 69.000 (656007) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERCK8 (656007) 69.0 kV to APLGTNJC8 (656269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on BRISTOW8 69.000 (656011) 69 kV Bus a. Apply fault at the BRISTOW8 69.000 (656011) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW8 (656011) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on DUMONT8 69.000 (656021) 69 kV Bus a. Apply fault at the DUMONT8 69.000 (656021) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMONT8 (656021) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on DUMONT8 69.000 (656021) 69 kV Bus a. Apply fault at the DUMONT8 69.000 (656021) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMONT8 (656021) 69.0 kV to GENEVA8 (656187) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on KESLEY8 69.000 (656035) 69 kV Bus a. Apply fault at the KESLEY8 69.000 (656035) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KESLEY8 (656035) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on NEAL8 69.000 (656049) 69 kV Bus a. Apply fault at the NEAL8 69.000 (656049) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL8 (656049) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKNER8 (656149) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKNER8 (656149) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKNER8 (656149) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on ALEXANDR8 69.000 (656179) 69 kV Bus a. Apply fault at the ALEXANDR8 69.000 (656179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALEXANDR8 (656179) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on ALEXANDR8 69.000 (656179) 69 kV Bus a. Apply fault at the ALEXANDR8 69.000 (656179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALEXANDR8 (656179) 69.0 kV to BELMOND8 (656841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on DOWS8 69.000 (656181) 69 kV Bus a. Apply fault at the DOWS8 69.000 (656181) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOWS8 (656181) 69.0 kV to HAMILTONT8 (656209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on DOWS8 69.000 (656181) 69 kV Bus a. Apply fault at the DOWS8 69.000 (656181) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOWS8 (656181) 69.0 kV to GALT8 (656859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on GENEVA8 69.000 (656187) 69 kV Bus a. Apply fault at the GENEVA8 69.000 (656187) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA8 (656187) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on GLCOATNG8 69.000 (656189) 69 kV Bus a. Apply fault at the GLCOATNG8 69.000 (656189) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLCOATNG8 (656189) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on HAMPTON8 69.000 (656193) 69 kV Bus a. Apply fault at the HAMPTON8 69.000 (656193) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTON8 (656193) 69.0 kV to HAMILTONT8 (656209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on MECSHDFT8 69.000 (656199) 69 kV Bus a. Apply fault at the MECSHDFT8 69.000 (656199) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MECSHDFT8 (656199) 69.0 kV to SWALEDAL8 (656203) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on MECSHDFT8 69.000 (656199) 69 kV Bus a. Apply fault at the MECSHDFT8 69.000 (656199) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MECSHDFT8 (656199) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on HAMILTONT8 69.000 (656209) 69 kV Bus a. Apply fault at the HAMILTONT8 69.000 (656209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMILTONT8 (656209) 69.0 kV to HAMILTON8 (656211) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on APLGTNJC8 69.000 (656269) 69 kV Bus a. Apply fault at the APLGTNJC8 69.000 (656269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APLGTNJC8 (656269) 69.0 kV to APLNGTON8 (656271) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on CONRAD8 69.000 (656275) 69 kV Bus a. Apply fault at the CONRAD8 69.000 (656275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD8 (656275) 69.0 kV to CRAMERJC8 (656279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on CRAMER8 69.000 (656277) 69 kV Bus a. Apply fault at the CRAMER8 69.000 (656277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAMER8 (656277) 69.0 kV to CRAMERJC8 (656279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on CRAMERJC8 69.000 (656279) 69 kV Bus a. Apply fault at the CRAMERJC8 69.000 (656279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAMERJC8 (656279) 69.0 kV to DINSDALE8 (656281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on GRNDYCTR8 69.000 (656289) 69 kV Bus a. Apply fault at the GRNDYCTR8 69.000 (656289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCTR8 (656289) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the MGS ST (629216) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on WELSBRG G 69.000 (656301) 69 kV Bus a. Apply fault at the WELSBRG G 69.000 (656301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG G (656301) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on WELSBRG G 69.000 (656301) 69 kV Bus a. Apply fault at the WELSBRG G 69.000 (656301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG G (656301) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on ALDEN8 69.000 (656753) 69 kV Bus a. Apply fault at the ALDEN8 69.000 (656753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALDEN8 (656753) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on ALDENJCT8 69.000 (656755) 69 kV Bus a. Apply fault at the ALDENJCT8 69.000 (656755) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALDENJCT8 (656755) 69.0 kV to BUCKEYE8 (656759) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on BOONDOCK8 69.000 (656757) 69 kV Bus a. Apply fault at the BOONDOCK8 69.000 (656757) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONDOCK8 (656757) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BUCKEYE8 69.000 (656759) 69 kV Bus a. Apply fault at the BUCKEYE8 69.000 (656759) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE8 (656759) 69.0 kV to PLEASANT8 (656781) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on ELSWORTH8 69.000 (656763) 69 kV Bus a. Apply fault at the ELSWORTH8 69.000 (656763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELSWORTH8 (656763) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on JEWELL8 69.000 (656777) 69 kV Bus a. Apply fault at the JEWELL8 69.000 (656777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEWELL8 (656777) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on IESLYONT8 69.000 (656778) 69 kV Bus a. Apply fault at the IESLYONT8 69.000 (656778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IESLYONT8 (656778) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on GALT8 69.000 (656859) 69 kV Bus a. Apply fault at the GALT8 69.000 (656859) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALT8 (656859) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on IAFINDP8 69.000 (630341) 69 kV Bus a. Apply fault at the IAFINDP8 69.000 (630341) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on HAMPTON8 69.000 (656193) 69 kV Bus a. Apply fault at the HAMPTON8 69.000 (656193) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTON8 (656193) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on DINSDALE8 69.000 (656281) 69 kV Bus a. Apply fault at the DINSDALE8 69.000 (656281) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DINSDALE8 (656281) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on WELSBRG G 69.000 (656301) 69 kV Bus a. Apply fault at the WELSBRG G 69.000 (656301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG G (656301) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G11-008 (539858), G22-065 (768284) and G19-063 (763926). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G11-008 (539858), G22-065 (768284) and G19-063 (763926). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD (541171) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD (541171) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD (541171) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-018 (588633 and 588637). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD (541171) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD (541171) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BL.PLN.5 161.00 (631012) 161 kV Bus a. Apply Fault at the BL.PLN.5 161.00 (631012) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2031 SUB (50313) 161.0 kV to TOLEDO 5 (631001) 161.0 kV Transmission Circuit #1 b.2. TOLEDO 5 (631001) 161.0 kV to TOLEDO 9 (629101) 34.5 kV Two Winding #1 b.3. TOLEDO 5 (631001) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 b.4. TOLEDO 5 (631001) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.5. NEWHAL5 (631009) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 b.6. BL.PLN.5 (631012) 161.0 kV to BL.PLN.9 (629102) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on EMERY 5 161.00 (631048) 161 kV Bus a. Apply Fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERY 5 (631048) 161.0 kV to EMERYGT2 (629068) 18.0 kV Two Winding #1 b.2. EMERY 5 (631048) 161.0 kV to SHEFFLD5 (656201) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NUTHTCH5 161.00 (631166) 161 kV Bus a. Apply Fault at the NUTHTCH5 161.00 (631166) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP5 (631029) 161.0 kV to NUTHTCH5 (631166) 161.0 kV Transmission Circuit #1 b.2. NUTHTCH5 (631166) 161.0 kV to WHISWIL5 (631171) 161.0 kV Transmission Circuit #1 b.3. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MGS ST1 18.000 (629216) 18 kV Bus a. Apply Fault at the MGS ST1 18.000 (629216) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.2. MGS ST1 (629216) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MGS CT1 18.000 (629214) 18 kV Bus a. Apply Fault at the MGS CT1 18.000 (629214) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 b.2. MGS CT1 (629214) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WALL LK5 161.00 (636235) 161 kV Bus a. Apply Fault at the WALL LK5 161.00 (636235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRIGHT 5 (636050) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.2. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.3. WALL LK5 (636235) 161.0 kV to CENTURY B2 9 (636234) 34.5 kV Two Winding #2 b.4. WALL LK5 (636235) 161.0 kV to WALL LK8 (636236) 69.0 kV Two Winding #1 b.5. WALL LK5 (636235) 161.0 kV to CENTURY B1 9 (636237) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BUTLER 5 161.00 (636240) 161 kV Bus a. Apply Fault at the BUTLER 5 161.00 (636240) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.2. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.4. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.5. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.6. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.7. BUTLER 5 (636240) 161.0 kV to BUTLER 9 (636241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FRANKLN5 161.00 (636230) 161 kV Bus a. Apply Fault at the FRANKLN5 161.00 (636230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.2. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.3. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.4. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.5. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.6. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on BUTLER 5 161.00 (636240) 161 kV Bus a. Apply Fault at the BUTLER 5 161.00 (636240) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 5 (636200) 161.0 kV to UNIONTP5 (636225) 161.0 kV Transmission Circuit #1 b.2. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. UNIONTP5 (636225) 161.0 kV to UNIONCF5 (638030) 161.0 kV Transmission Circuit #1 b.4. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.5. BUTLER 5 (636240) 161.0 kV to BUTLER 9 (636241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTHL CT3 (630773) 13.5 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 b.2. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2031 SUB (50313) 161.0 kV to TOLEDO 5 (631001) 161.0 kV Transmission Circuit #1 b.2. M-TOWN K1 7 (627026) 115.0 kV to M-TOWN K2 7 (631004) 115.0 kV Transmission Circuit #z b.3. TOLEDO 5 (631001) 161.0 kV to TOLEDO 9 (629101) 34.5 kV Two Winding #1 b.4. TOLEDO 5 (631001) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 b.5. TOLEDO 5 (631001) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.6. M-TOWN K2 7 (631004) 115.0 kV to M-TOWN 9 (629105) 34.5 kV Two Winding #1 b.7. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.8. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ABBOTT 5 161.00 (631000) 161 kV Bus a. Apply Fault at the ABBOTT 5 161.00 (631000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1365 POI (43654) 161.0 kV to ABBOTT 5 (631000) 161.0 kV Transmission Circuit #1 b.2. M-TOWN K1 7 (627026) 115.0 kV to M-TOWN K2 7 (631004) 115.0 kV Transmission Circuit #z b.3. ABBOTT 5 (631000) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.4. M-TOWN K2 7 (631004) 115.0 kV to M-TOWN 9 (629105) 34.5 kV Two Winding #1 b.5. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.6. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 b.7. VIENNA B1 9 (636250) 34.5 kV to ABBOTT 5 (631000) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HAMPTONTAP5 161.00 (656207) 161 kV Bus a. Apply Fault at the HAMPTONTAP5 161.00 (656207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERY 5 (631048) 161.0 kV to SHEFFLD5 (656201) 161.0 kV Transmission Circuit #1 b.2. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.3. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.4. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.5. SHEFFLD5 (656201) 161.0 kV to WSHEFFLD8 (656205) 69.0 kV Two Winding #1 b.6. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.2. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on JASPER 5 161.00 (631107) 161 kV Bus a. Apply Fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.2. JASPER 5 (631107) 161.0 kV to NEANKNY5 (635710) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WRIGHT 5 161.00 (636050) 161 kV Bus a. Apply Fault at the WRIGHT 5 161.00 (636050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER5 (636001) 161.0 kV to WRIGHT 5 (636050) 161.0 kV Transmission Circuit #1 b.2. WRIGHT 5 (636050) 161.0 kV to WRIGHT 8 (636051) 69.0 kV Two Winding #1 b.3. WRIGHT 5 (636050) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on JASPER 5 161.00 (631107) 161 kV Bus a. Apply Fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JASPER 8 (630046) 69.0 kV to JASPER 5 (631107) 161.0 kV Two Winding #1 b.2. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ACKLEY 5 161.00 (636229) 161 kV Bus a. Apply Fault at the ACKLEY 5 161.00 (636229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on TIMBRCK5 161.00 (631082) 161 kV Bus a. Apply Fault at the TIMBRCK5 161.00 (631082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TMBRCRK9 (629133) 34.5 kV to TIMBRCK5 (631082) 161.0 kV Two Winding #1 b.2. TIMBERCREEK8 (630963) 69.0 kV to TIMBRCK5 (631082) 161.0 kV Two Winding #1 b.3. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 b.4. TIMBRCK5 (631082) 161.0 kV to M-TOWN_W5 (631128) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply Fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to PR CRK4G (629066) 18.0 kV Two Winding #1 b.2. PRAR CK7 (631017) 115.0 kV to PR CRK1G (629085) 34.5 kV Two Winding #2 b.3. PRAR CK7 (631017) 115.0 kV to PR CRK3G (630787) 13.2 kV Two Winding #1 b.4. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.5. PRAR CK7 (631017) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 b.6. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to IAFINDP5 (631029) 161.0 kV Transmission Circuit #1 b.2. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.3. WELSBRG5 (631008) 161.0 kV to MEC WELSBRG5 (636217) 161.0 kV Transmission Circuit #1 b.4. WELSBRG5 (631008) 161.0 kV to WELSBRG G (656301) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREENMNTN8 (630925) 69.0 kV to FLETCHR J1 8 (630929) 69.0 kV Transmission Circuit #1 b.2. FLETCHR J1 8 (630929) 69.0 kV to FLETCHR J2 8 (630977) 69.0 kV Transmission Circuit #z b.3. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MARION K1 7 115.00 (631019) 115 kV Bus a. Apply Fault at the MARION K1 7 115.00 (631019) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARION J1 8 (629183) 69.0 kV to MARION K1 7 (631019) 115.0 kV Two Winding #1 b.2. MARION J2 8 (630759) 69.0 kV to MARION K2 7 (631195) 115.0 kV Two Winding #1 b.3. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 b.4. MARION K1 7 (631019) 115.0 kV to SWAMPFX7 (631027) 115.0 kV Transmission Circuit #1 b.5. MARION K1 7 (631019) 115.0 kV to OLDSETTLERS7 (631167) 115.0 kV Transmission Circuit #1 b.6. MARION K1 7 (631019) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FRANKLN5 161.00 (636230) 161 kV Bus a. Apply Fault at the FRANKLN5 161.00 (636230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.2. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.3. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.4. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.5. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.6. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ACKLEY 5 161.00 (636229) 161 kV Bus a. Apply Fault at the ACKLEY 5 161.00 (636229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN K1 7 (627026) 115.0 kV to SUTHL CT1 (630771) 13.5 kV Two Winding #1 b.2. M-TOWN K1 7 (627026) 115.0 kV to SUTHL CT2 (630772) 13.5 kV Two Winding #1 b.3. M-TOWN K1 7 (627026) 115.0 kV to M-TOWN K2 7 (631004) 115.0 kV Transmission Circuit #z b.4. M-TOWN K2 7 (631004) 115.0 kV to M-TOWN 9 (629105) 34.5 kV Two Winding #1 b.5. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.6. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BERTRAM5 161.00 (631092) 161 kV Bus a. Apply Fault at the BERTRAM5 161.00 (631092) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.2. PCI 5 (631090) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 b.3. BERTRAM5 (631092) 161.0 kV to BERTRAM7 (631020) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LAUREL_5 161.00 (631186) 161 kV Bus a. Apply Fault at the LAUREL_5 161.00 (631186) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.2. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.3. LAUREL B1 9 (635845) 34.5 kV to LAUREL_5 (631186) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on BERTRAM5 161.00 (631092) 161 kV Bus a. Apply Fault at the BERTRAM5 161.00 (631092) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1889 SUB (48893) 161.0 kV to MT VERN5 (631073) 161.0 kV Transmission Circuit #1 b.2. MT VERNoN 8 (629319) 69.0 kV to MT VERN5 (631073) 161.0 kV Two Winding #1 b.3. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.4. MT VERN5 (631073) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 b.5. MT VERN5 (631073) 161.0 kV to WYOMING5 (631099) 161.0 kV Transmission Circuit #1 b.6. BERTRAM5 (631092) 161.0 kV to BERTRAM7 (631020) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to MGS CT2 (629215) 18.0 kV Two Winding #1 b.2. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply Fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to PR CRK1G (629085) 34.5 kV Two Winding #2 b.2. PRAR CK7 (631017) 115.0 kV to PR CRK3G (630787) 13.2 kV Two Winding #1 b.3. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.4. PRAR CK7 (631017) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 b.5. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 b.6. SUTLIFF7 (631022) 115.0 kV to CALAMUS7 (631023) 115.0 kV Transmission Circuit #1 b.7. CALAMUS7 (631023) 115.0 kV to CALAMUS9 (629093) 34.5 kV Two Winding #1 b.8. CALAMUS7 (631023) 115.0 kV to E CALMS7 (631024) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on M-TOWN_W5 161.00 (631128) 161 kV Bus a. Apply Fault at the M-TOWN_W5 161.00 (631128) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBRCK5 (631082) 161.0 kV to M-TOWN_W5 (631128) 161.0 kV Transmission Circuit #1 b.2. M-TOWN_W5 (631128) 161.0 kV to STRY_CO5 (631156) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply Fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP8 (630341) 69.0 kV to IAFINDP5 (631029) 161.0 kV Two Winding #1 b.2. WELSBRG5 (631008) 161.0 kV to IAFINDP5 (631029) 161.0 kV Transmission Circuit #1 b.3. IAFINDP5 (631029) 161.0 kV to NUTHTCH5 (631166) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to MGS ST1 (629216) 18.0 kV Two Winding #1 b.2. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply Fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDYCN8 (630339) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 b.2. GRNDYCN8 (630339) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply Fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP8 (630341) 69.0 kV to IAFINDP5 (631029) 161.0 kV Two Winding #1 b.2. IAFINDP8 (630341) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on CONRAD 8 69.000 (630350) 69 kV Bus a. Apply Fault at the CONRAD 8 69.000 (630350) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONRAD 8 (630350) 69.0 kV to CONRAD8 (656275) 69.0 kV Transmission Circuit #1 b.2. CONRAD 8 (630350) 69.0 kV to MELRSTAP8 (656297) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply Fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTERCREEK8 (630839) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 b.2. OTTERCREEK8 (630839) 69.0 kV to HUBBRDPUMPT8 (630842) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply Fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 b.2. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply Fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMPTNW8 (636315) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 b.2. HAMPTNW8 (636315) 69.0 kV to LATIMER8 (636317) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SHEFFLD8 69.000 (636316) 69 kV Bus a. Apply Fault at the SHEFFLD8 69.000 (636316) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEFFLD8 (636316) 69.0 kV to MECSHDFT8 (656199) 69.0 kV Transmission Circuit #1 b.2. SHEFFLD8 (636316) 69.0 kV to HAMPTNW8 (636315) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on LATIMER8 69.000 (636317) 69 kV Bus a. Apply Fault at the LATIMER8 69.000 (636317) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LATIMER8 (636317) 69.0 kV to HAMPTNW8 (636315) 69.0 kV Transmission Circuit #1 b.2. LATIMER8 (636317) 69.0 kV to WB LATM 8 (636318) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on DUMONT8 69.000 (656021) 69 kV Bus a. Apply Fault at the DUMONT8 69.000 (656021) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUMONT8 (656021) 69.0 kV to GENEVA8 (656187) 69.0 kV Transmission Circuit #1 b.2. DUMONT8 (656021) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply Fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER8 (656149) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 b.2. BUCKNER8 (656149) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on DOWS8 69.000 (656181) 69 kV Bus a. Apply Fault at the DOWS8 69.000 (656181) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOWS8 (656181) 69.0 kV to HAMILTONT8 (656209) 69.0 kV Transmission Circuit #1 b.2. DOWS8 (656181) 69.0 kV to GALT8 (656859) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on ESHEFFTP8 69.000 (656185) 69 kV Bus a. Apply Fault at the ESHEFFTP8 69.000 (656185) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ESHEFFTP8 (656185) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 b.2. ESHEFFTP8 (656185) 69.0 kV to GLCOATNG8 (656189) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GENEVA8 69.000 (656187) 69 kV Bus a. Apply Fault at the GENEVA8 69.000 (656187) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA8 (656187) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 b.2. GENEVA8 (656187) 69.0 kV to DUMONT8 (656021) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GLCOATNG8 69.000 (656189) 69 kV Bus a. Apply Fault at the GLCOATNG8 69.000 (656189) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLCOATNG8 (656189) 69.0 kV to ESHEFFTP8 (656185) 69.0 kV Transmission Circuit #1 b.2. GLCOATNG8 (656189) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HAMPTON5 161.00 (656191) 161 kV Bus a. Apply Fault at the HAMPTON5 161.00 (656191) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMPTON8 (656193) 69.0 kV to HAMPTON5 (656191) 161.0 kV Two Winding #1 b.2. HAMPTON8 (656193) 69.0 kV to HAMPTNW8 (636315) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HAMILTONT8 69.000 (656209) 69 kV Bus a. Apply Fault at the HAMILTONT8 69.000 (656209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMILTONT8 (656209) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 b.2. HAMILTONT8 (656209) 69.0 kV to DOWS8 (656181) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MELRSTAP8 69.000 (656297) 69 kV Bus a. Apply Fault at the MELRSTAP8 69.000 (656297) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MELRSTAP8 (656297) 69.0 kV to CONRAD 8 (630350) 69.0 kV Transmission Circuit #1 b.2. MELRSTAP8 (656297) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG G (656301) 69.0 kV to WELSBRG5 (631008) 161.0 kV Two Winding #1 b.2. WELSBRG G (656301) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FERNTAP8 69.000 (656303) 69 kV Bus a. Apply Fault at the FERNTAP8 69.000 (656303) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FERNTAP8 (656303) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 b.2. FERNTAP8 (656303) 69.0 kV to APLNGTON8 (656271) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on ALDEN8 69.000 (656753) 69 kV Bus a. Apply Fault at the ALDEN8 69.000 (656753) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDEN8 (656753) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 b.2. ALDEN8 (656753) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on ALDENJCT8 69.000 (656755) 69 kV Bus a. Apply Fault at the ALDENJCT8 69.000 (656755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDENJCT8 (656755) 69.0 kV to BUCKNER8 (656149) 69.0 kV Transmission Circuit #1 b.2. ALDENJCT8 (656755) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BUCKEYE8 69.000 (656759) 69 kV Bus a. Apply Fault at the BUCKEYE8 69.000 (656759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKEYE8 (656759) 69.0 kV to PLEASANT8 (656781) 69.0 kV Transmission Circuit #1 b.2. BUCKEYE8 (656759) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FARM_TAP8 69.000 (656769) 69 kV Bus a. Apply Fault at the FARM_TAP8 69.000 (656769) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARM_TAP8 (656769) 69.0 kV to IAFINDP8 (630341) 69.0 kV Transmission Circuit #1 b.2. FARM_TAP8 (656769) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.2. WELSBRG5 (631008) 161.0 kV to WELSBRG G (656301) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply Fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP5 (631029) 161.0 kV to IAFINDP8 (630341) 69.0 kV Two Winding #1 b.2. IAFINDP5 (631029) 161.0 kV to WELSBRG5 (631008) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GRNDYMUNT8 69.000 (656305) 69 kV Bus a. Apply Fault at the GRNDYMUNT8 69.000 (656305) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDYMUNT8 (656305) 69.0 kV to GRNDYCTR8 (656289) 69.0 kV Transmission Circuit #1 b.2. GRNDYMUNT8 (656305) 69.0 kV to GRNDYCN8 (630339) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on IFE8 69.000 (656775) 69 kV Bus a. Apply Fault at the IFE8 69.000 (656775) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IFE8 (656775) 69.0 kV to IAFINDP8 (630341) 69.0 kV Transmission Circuit #1 b.2. IFE8 (656775) 69.0 kV to ALDEN8 (656753) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ELDORA8 69.000 (656761) 69 kV Bus a. Apply Fault at the ELDORA8 69.000 (656761) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELDORA8 (656761) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 b.2. ELDORA8 (656761) 69.0 kV to OTTERCREEK8 (630839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on ALDNRRLTP8 69.000 (656795) 69 kV Bus a. Apply Fault at the ALDNRRLTP8 69.000 (656795) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDNRRLTP8 (656795) 69.0 kV to ALDEN8 (656753) 69.0 kV Transmission Circuit #1 b.2. ALDNRRLTP8 (656795) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WELBRGEASTT869.000 (656309) 69 kV Bus a. Apply Fault at the WELBRGEASTT869.000 (656309) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELBRGEASTT8 (656309) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 b.2. WELBRGEASTT8 (656309) 69.0 kV to FERNTAP8 (656303) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SUTLIFF7 115.00 (631022) 115 kV Bus a. Apply Fault at the SUTLIFF7 115.00 (631022) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTLIFF7 (631022) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.2. SUTLIFF7 (631022) 115.0 kV to CALAMUS7 (631023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SQUARED7 115.00 (631032) 115 kV Bus a. Apply Fault at the SQUARED7 115.00 (631032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQUARED7 (631032) 115.0 kV to STON PT7 (631015) 115.0 kV Transmission Circuit #1 b.2. SQUARED7 (631032) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on MECSHDFT8 69.000 (656199) 69 kV Bus a. Apply Fault at the MECSHDFT8 69.000 (656199) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MECSHDFT8 (656199) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 b.2. MECSHDFT8 (656199) 69.0 kV to SHEFFLD8 (636316) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WB LATM 8 69.000 (636318) 69 kV Bus a. Apply Fault at the WB LATM 8 69.000 (636318) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WB LATM 8 (636318) 69.0 kV to LATIMER8 (636317) 69.0 kV Transmission Circuit #1 b.2. WB LATM 8 (636318) 69.0 kV to COULTR 8 (630357) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GALT8 69.000 (656859) 69 kV Bus a. Apply Fault at the GALT8 69.000 (656859) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GALT8 (656859) 69.0 kV to DOWS8 (656181) 69.0 kV Transmission Circuit #1 b.2. GALT8 (656859) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SHEFFLD5 161.00 (656201) 161 kV Bus a. Apply Fault at the SHEFFLD5 161.00 (656201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSHEFFLD8 (656205) 69.0 kV to SHEFFLD5 (656201) 161.0 kV Two Winding #1 b.2. WSHEFFLD8 (656205) 69.0 kV to MECSHDFT8 (656199) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on PLEASANT8 69.000 (656781) 69 kV Bus a. Apply Fault at the PLEASANT8 69.000 (656781) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLEASANT8 (656781) 69.0 kV to OTTERCREEK8 (630839) 69.0 kV Transmission Circuit #1 b.2. PLEASANT8 (656781) 69.0 kV to BUCKEYE8 (656759) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HAMILTONT8 (656209) 69 kV Bus a. Apply Fault at the HAMILTONT8 (656209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMILTONT8 (656209) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HAMPTNW8 (636315) 69 kV Bus a. Apply Fault at the HAMPTNW8 (636315) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMPTNW8 (636315) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WELSBRG5 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on FRANKLN5 (636230) 161 kV Bus a. Apply Fault at the FRANKLN5 (636230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLN5 (636230) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on ALDNRRLTP8 (656795) 69 kV Bus a. Apply Fault at the ALDNRRLTP8 (656795) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDNRRLTP8 (656795) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on IAFINDP8 (630341) 69 kV Bus a. Apply Fault at the IAFINDP8 (630341) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP8 (630341) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on MONoLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONoLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONoLITH 3 (640590) 345.0 kV to MONoLITH 7 (640591) 115.0 kV to MONoLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on G22-015-TAP 345.00 (767280) 345 kV Bus a. Apply Fault at the G22-015-TAP 345.00 (767280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on UNIONTP5 161.00 (636225) 161 kV Bus a. Apply fault at the UNIONTP5 161.00 (636225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKHAWK 5 (636200) 161.0 kV to UNIONTP5 (636225) 161.0 kV Transmission Circuit #1 b.2. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. UNIONTP5 (636225) 161.0 kV to UNIONCF5 (638030) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on WRIGHT 5 161.00 (636050) 161 kV Bus a. Apply fault at the WRIGHT 5 161.00 (636050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBSTER5 (636001) 161.0 kV to WRIGHT 5 (636050) 161.0 kV Transmission Circuit #1 b.2. WRIGHT 5 (636050) 161.0 kV to WRIGHT 8 (636051) 69.0 kV Two Winding #1 b.3. WRIGHT 5 (636050) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on WASHBRN5 161.00 (636210) 161 kV Bus a. Apply fault at the WASHBRN5 161.00 (636210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DYSART 5 (631086) 161.0 kV to WASHBRN5 (636210) 161.0 kV Transmission Circuit #1 b.2. WASHBRN5 (636210) 161.0 kV to WASHBRN8 (636211) 69.0 kV Two Winding #1 b.3. WASHBRN5 (636210) 161.0 kV to SHAULISRD5 (636215) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on TRAER 5 161.00 (631083) 161 kV Bus a. Apply fault at the TRAER 5 161.00 (631083) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1365 POI (43654) 161.0 kV to TRAER 5 (631083) 161.0 kV Transmission Circuit #1 b.2. TRAER 5 (631083) 161.0 kV to TRAER 8 (630027) 69.0 kV Two Winding #1 b.3. TRAER 5 (631083) 161.0 kV to DYSART 5 (631086) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on SQUARED7 115.00 (631032) 115 kV Bus a. Apply fault at the SQUARED7 115.00 (631032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT7 (631015) 115.0 kV to SQUARED7 (631032) 115.0 kV Transmission Circuit #1 b.2. PRAR CK7 (631017) 115.0 kV to SQUARED7 (631032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP5 (631029) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on ABBOTT 5 161.00 (631000) 161 kV Bus a. Apply fault at the ABBOTT 5 161.00 (631000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABBOTT 5 (631000) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on TOLEDO 5 161.00 (631001) 161 kV Bus a. Apply fault at the TOLEDO 5 161.00 (631001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLEDO 5 (631001) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips J2031 (50310). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on TOLEDO 5 161.00 (631001) 161 kV Bus a. Apply fault at the TOLEDO 5 161.00 (631001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLEDO 5 (631001) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips J2031 (50310). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on NEWHAL5 161.00 (631009) 161 kV Bus a. Apply fault at the NEWHAL5 161.00 (631009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHAL5 (631009) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP5 (631029) 161.0 kV to NUTHTCH5 (631166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on ROSEHLW5 161.00 (631034) 161 kV Bus a. Apply fault at the ROSEHLW5 161.00 (631034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHLW5 (631034) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY 5 (631048) 161.0 kV to CGORDO_5 (631049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY 5 (631048) 161.0 kV to COLBY5 (631202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on MT VERN5 161.00 (631073) 161 kV Bus a. Apply fault at the MT VERN5 161.00 (631073) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MT VERN5 (631073) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN 5 (631081) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on TIMBRCK5 161.00 (631082) 161 kV Bus a. Apply fault at the TIMBRCK5 161.00 (631082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRCK5 (631082) 161.0 kV to M-TOWN_W5 (631128) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on DYSART 5 161.00 (631086) 161 kV Bus a. Apply fault at the DYSART 5 161.00 (631086) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DYSART 5 (631086) 161.0 kV to VINTON 5 (631087) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on PCI 5 161.00 (631090) 161 kV Bus a. Apply fault at the PCI 5 161.00 (631090) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCI 5 (631090) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 5 (631107) 161.0 kV to NEWTON 5 (631119) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 5 (631107) 161.0 kV to NEANKNY5 (635710) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on M-TOWN_W5 161.00 (631128) 161 kV Bus a. Apply fault at the M-TOWN_W5 161.00 (631128) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN_W5 (631128) 161.0 kV to STRY_CO5 (631156) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on NUTHTCH5 161.00 (631166) 161 kV Bus a. Apply fault at the NUTHTCH5 161.00 (631166) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on JASPER 5 161.00 (631107) 161 kV Bus a. Apply fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JASPER 8 (630046) 69.0 kV to JASPER 5 (631107) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY S8 (630213) 69.0 kV to EMERY 5 (631048) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on EMERY 5 161.00 (631048) 161 kV Bus a. Apply fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY N8 (630214) 69.0 kV to EMERY 5 (631048) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV to IAFINDP5 (631029) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on TIMBRCK5 161.00 (631082) 161 kV Bus a. Apply fault at the TIMBRCK5 161.00 (631082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCREEK8 (630963) 69.0 kV to TIMBRCK5 (631082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV to WELSBRG G (656301) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on STON PT5 161.00 (631080) 161 kV Bus a. Apply fault at the STON PT5 161.00 (631080) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT5 (631080) 161.0 kV to STON PT7 (631015) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on KILLDEER3 345.00 (631199) 345 kV Bus a. Apply fault at the KILLDEER3 345.00 (631199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KILLDEER3 (631199) 345.0 kV to EMERY 5 (631048) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on STON PT7 115.00 (631015) 115 kV Bus a. Apply fault at the STON PT7 115.00 (631015) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT7 (631015) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on FRANKLN5 161.00 (636230) 161 kV Bus a. Apply fault at the FRANKLN5 161.00 (636230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on WALL LK5 161.00 (636235) 161 kV Bus a. Apply fault at the WALL LK5 161.00 (636235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LK5 (636235) 161.0 kV to WALL LK8 (636236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SHEFFLD5 161.00 (656201) 161 kV Bus a. Apply fault at the SHEFFLD5 161.00 (656201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERY 5 (631048) 161.0 kV to SHEFFLD5 (656201) 161.0 kV Transmission Circuit #1 b.2. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.3. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.4. SHEFFLD5 (656201) 161.0 kV to WSHEFFLD8 (656205) 69.0 kV Two Winding #1 b.5. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on LIME CK L2 5161.00 (631160) 161 kV Bus a. Apply fault at the LIME CK L2 5161.00 (631160) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIME CK L1 5 (631047) 161.0 kV to LIME CK L2 5 (631160) 161.0 kV Transmission Circuit #z b.2. EMERY 5 (631048) 161.0 kV to LIME CK L2 5 (631160) 161.0 kV Transmission Circuit #2 b.3. BARTON5 (631154) 161.0 kV to LIME CK L2 5 (631160) 161.0 kV Transmission Circuit #1 b.4. LIME CK L2 5 (631160) 161.0 kV to LIME CK J2 8 (630198) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G551-G1 (693756). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on HAMPTONTAP5 161.00 (656207) 161 kV Bus a. Apply fault at the HAMPTONTAP5 161.00 (656207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.2. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.3. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.4. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on ALDNRRLTP8 69.000 (656795) 69 kV Bus a. Apply fault at the ALDNRRLTP8 69.000 (656795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALDNBUCKEYE8 (630859) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 b.2. ALDEN8 (656753) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 b.3. ALDENJCT8 (656755) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on ESHEFFTP8 69.000 (656185) 69 kV Bus a. Apply fault at the ESHEFFTP8 69.000 (656185) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ESHEFFLD8 (656183) 69.0 kV to ESHEFFTP8 (656185) 69.0 kV Transmission Circuit #1 b.2. ESHEFFTP8 (656185) 69.0 kV to GLCOATNG8 (656189) 69.0 kV Transmission Circuit #1 b.3. ESHEFFTP8 (656185) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on FERNTAP8 69.000 (656303) 69 kV Bus a. Apply fault at the FERNTAP8 69.000 (656303) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APLNGTON8 (656271) 69.0 kV to FERNTAP8 (656303) 69.0 kV Transmission Circuit #1 b.2. FERN8 (656287) 69.0 kV to FERNTAP8 (656303) 69.0 kV Transmission Circuit #1 b.3. FERNTAP8 (656303) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on HICKSTAP 69.000 (656307) 69 kV Bus a. Apply fault at the HICKSTAP 69.000 (656307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REINBECK8 (630861) 69.0 kV to HICKSTAP (656307) 69.0 kV Transmission Circuit #1 b.2. DINSDALE8 (656281) 69.0 kV to HICKSTAP (656307) 69.0 kV Transmission Circuit #1 b.3. HICKS8 (656293) 69.0 kV to HICKSTAP (656307) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on MELRSTAP8 69.000 (656297) 69 kV Bus a. Apply fault at the MELRSTAP8 69.000 (656297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD 8 (630350) 69.0 kV to MELRSTAP8 (656297) 69.0 kV Transmission Circuit #1 b.2. MELROSE8 (656295) 69.0 kV to MELRSTAP8 (656297) 69.0 kV Transmission Circuit #1 b.3. MELRSTAP8 (656297) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on ROLANDTP8 69.000 (656790) 69 kV Bus a. Apply fault at the ROLANDTP8 69.000 (656790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLAND8 (656783) 69.0 kV to ROLANDTP8 (656790) 69.0 kV Transmission Circuit #1 b.2. GARDEN C8 (656789) 69.0 kV to ROLANDTP8 (656790) 69.0 kV Transmission Circuit #1 b.3. ROLANDTP8 (656790) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on TRAERTAP8 69.000 (656299) 69 kV Bus a. Apply fault at the TRAERTAP8 69.000 (656299) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TRAER 8 (630027) 69.0 kV to TRAERTAP8 (656299) 69.0 kV Transmission Circuit #1 b.2. CLUTIER8 (656273) 69.0 kV to TRAERTAP8 (656299) 69.0 kV Transmission Circuit #1 b.3. DINSDALE8 (656281) 69.0 kV to TRAERTAP8 (656299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on WALLLKTP8 69.000 (656899) 69 kV Bus a. Apply fault at the WALLLKTP8 69.000 (656899) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LAK8 (656897) 69.0 kV to WALLLKTP8 (656899) 69.0 kV Transmission Circuit #1 b.2. WALLLKTP8 (656899) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 b.3. WALLLKTP8 (656899) 69.0 kV to PRESTAGE8 (656915) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on BUTLER 5 161.00 (636240) 161 kV Bus a. Apply fault at the BUTLER 5 161.00 (636240) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.2. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. BUTLER 5 (636240) 161.0 kV to BUTLER 9 (636241) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on ELDORA8 69.000 (630841) 69 kV Bus a. Apply fault at the ELDORA8 69.000 (630841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORA8 (630841) 69.0 kV to UNION_CB8 (630921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on CONRAD8 69.000 (630923) 69 kV Bus a. Apply fault at the CONRAD8 69.000 (630923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD8 (630923) 69.0 kV to GREENMNTN8 (630925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on MARION K2 7 115.00 (631195) 115 kV Bus a. Apply fault at the MARION K2 7 115.00 (631195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARION J2 8 (630759) 69.0 kV to MARION K2 7 (631195) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on HUBBRDRURAL869.000 (630840) 69 kV Bus a. Apply fault at the HUBBRDRURAL869.000 (630840) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUBBRDRURAL8 (630840) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on LATIMER8 69.000 (636317) 69 kV Bus a. Apply fault at the LATIMER8 69.000 (636317) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LATIMER8 (636317) 69.0 kV to WB LATM 8 (636318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to HUBBRDPUMPT8 (630842) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on GREENMNTN8 69.000 (630925) 69 kV Bus a. Apply fault at the GREENMNTN8 69.000 (630925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREENMNTN8 (630925) 69.0 kV to FLETCHR J1 8 (630929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on SCOTTTAP8 69.000 (636086) 69 kV Bus a. Apply fault at the SCOTTTAP8 69.000 (636086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTTAP8 (636086) 69.0 kV to LKCORNL8 (656875) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on COULTR 8 69.000 (630357) 69 kV Bus a. Apply fault at the COULTR 8 69.000 (630357) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTR 8 (630357) 69.0 kV to WB LATM 8 (636318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on CALAMUS7 115.00 (631023) 115 kV Bus a. Apply fault at the CALAMUS7 115.00 (631023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTLIFF7 (631022) 115.0 kV to CALAMUS7 (631023) 115.0 kV Transmission Circuit #1 b.2. CALAMUS7 (631023) 115.0 kV to CALAMUS9 (629093) 34.5 kV Two Winding #1 b.3. CALAMUS7 (631023) 115.0 kV to E CALMS7 (631024) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTNW8 (636315) 69.0 kV to LATIMER8 (636317) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on STATECENTER869.000 (630961) 69 kV Bus a. Apply fault at the STATECENTER869.000 (630961) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATECENTER8 (630961) 69.0 kV to LAMOILLEREC8 (630962) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on BELMNDJ8 69.000 (630469) 69 kV Bus a. Apply fault at the BELMNDJ8 69.000 (630469) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELMNDJ8 (630469) 69.0 kV to EATNTAP8 (630470) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on COULTR 8 69.000 (630357) 69 kV Bus a. Apply fault at the COULTR 8 69.000 (630357) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COULTR 8 (630357) 69.0 kV to SCOTTTAP8 (636086) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on DIKEMORRISN869.000 (630860) 69 kV Bus a. Apply fault at the DIKEMORRISN869.000 (630860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIKEMORRISN8 (630860) 69.0 kV to REINBECK8 (630861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on IAFINDP8 69.000 (630341) 69 kV Bus a. Apply fault at the IAFINDP8 69.000 (630341) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTNW8 (636315) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on DIKEMORRISN869.000 (630860) 69 kV Bus a. Apply fault at the DIKEMORRISN869.000 (630860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIKEMORRISN8 (630860) 69.0 kV to GRNDYCTR8 (656289) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTNW8 (636315) 69.0 kV to SHEFFLD8 (636316) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on IAFINDP8 69.000 (630341) 69 kV Bus a. Apply fault at the IAFINDP8 69.000 (630341) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV to FARM_TAP8 (656769) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on NBELMDT8 69.000 (630467) 69 kV Bus a. Apply fault at the NBELMDT8 69.000 (630467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBELMDT8 (630467) 69.0 kV to BELMNDJ8 (630469) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on WELSBRGDIST869.000 (630862) 69 kV Bus a. Apply fault at the WELSBRGDIST869.000 (630862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRGDIST8 (630862) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to ELDORA8 (630841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on LAMOILLEREC869.000 (630962) 69 kV Bus a. Apply fault at the LAMOILLEREC869.000 (630962) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMOILLEREC8 (630962) 69.0 kV to TIMBERCREEK8 (630963) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on ACKLEY 5 161.00 (636229) 161 kV Bus a. Apply fault at the ACKLEY 5 161.00 (636229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on MEC WELSBRG5161.00 (636217) 161 kV Bus a. Apply fault at the MEC WELSBRG5161.00 (636217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEC WELSBRG5 (636217) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on BERTRAM5 161.00 (631092) 161 kV Bus a. Apply fault at the BERTRAM5 161.00 (631092) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.2. BERTRAM5 (631092) 161.0 kV to BERTRAM7 (631020) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG5 (631008) 161.0 kV to IAFINDP5 (631029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on J1365 POI 161.00 (43654) 161 kV Bus a. Apply fault at the J1365 POI 161.00 (43654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1365 POI (43654) 161.0 kV to ABBOTT 5 (631000) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on J1952 POI 161.00 (49524) 161 kV Bus a. Apply fault at the J1952 POI 161.00 (49524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1952 POI (49524) 161.0 kV to EMERY 5 (631048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips J1952 (49520). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCN8 (630339) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCN8 (630339) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on CONRAD 8 69.000 (630350) 69 kV Bus a. Apply fault at the CONRAD 8 69.000 (630350) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD 8 (630350) 69.0 kV to CONRAD8 (656275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on BELMNDJ8 69.000 (630469) 69 kV Bus a. Apply fault at the BELMNDJ8 69.000 (630469) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELMNDJ8 (630469) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTERCREEK8 (630839) 69.0 kV to PLEASANT8 (656781) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on FLETCHR J1 869.000 (630929) 69 kV Bus a. Apply fault at the FLETCHR J1 869.000 (630929) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR J1 8 (630929) 69.0 kV to FLETCHR J2 8 (630977) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on M-TOWN K2 7 115.00 (631004) 115 kV Bus a. Apply fault at the M-TOWN K2 7 115.00 (631004) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on STON PT7 115.00 (631015) 115 kV Bus a. Apply fault at the STON PT7 115.00 (631015) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STON PT7 (631015) 115.0 kV to 6 ST 7 (631016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAR CK7 (631017) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on MARION K1 7 115.00 (631019) 115 kV Bus a. Apply fault at the MARION K1 7 115.00 (631019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARION K1 7 (631019) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on W.BRCH 7 115.00 (631021) 115 kV Bus a. Apply fault at the W.BRCH 7 115.00 (631021) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BRCH 7 (631021) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on SCOTTTAP8 69.000 (636086) 69 kV Bus a. Apply fault at the SCOTTTAP8 69.000 (636086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTTAP8 (636086) 69.0 kV to SCOTT8 (656913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on WALL LK8 69.000 (636236) 69 kV Bus a. Apply fault at the WALL LK8 69.000 (636236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LK8 (636236) 69.0 kV to BLAIRSBU8 (656843) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on WALL LK8 69.000 (636236) 69 kV Bus a. Apply fault at the WALL LK8 69.000 (636236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALL LK8 (636236) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on DUMONT 8 69.000 (636249) 69 kV Bus a. Apply fault at the DUMONT 8 69.000 (636249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMONT 8 (636249) 69.0 kV to DUMONT8 (656021) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on SHEFFLD8 69.000 (636316) 69 kV Bus a. Apply fault at the SHEFFLD8 69.000 (636316) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFLD8 (636316) 69.0 kV to MECSHDFT8 (656199) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on ACKLEY 8 69.000 (636319) 69 kV Bus a. Apply fault at the ACKLEY 8 69.000 (636319) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACKLEY 8 (636319) 69.0 kV to ACKLYTAP8 (656751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on BEAVERCK8 69.000 (656007) 69 kV Bus a. Apply fault at the BEAVERCK8 69.000 (656007) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERCK8 (656007) 69.0 kV to APLGTNJC8 (656269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on BRISTOW8 69.000 (656011) 69 kV Bus a. Apply fault at the BRISTOW8 69.000 (656011) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW8 (656011) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on DUMONT8 69.000 (656021) 69 kV Bus a. Apply fault at the DUMONT8 69.000 (656021) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMONT8 (656021) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on DUMONT8 69.000 (656021) 69 kV Bus a. Apply fault at the DUMONT8 69.000 (656021) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMONT8 (656021) 69.0 kV to GENEVA8 (656187) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on KESLEY8 69.000 (656035) 69 kV Bus a. Apply fault at the KESLEY8 69.000 (656035) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KESLEY8 (656035) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on NEAL8 69.000 (656049) 69 kV Bus a. Apply fault at the NEAL8 69.000 (656049) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL8 (656049) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKNER8 (656149) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKNER8 (656149) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKNER8 (656149) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on ALEXANDR8 69.000 (656179) 69 kV Bus a. Apply fault at the ALEXANDR8 69.000 (656179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALEXANDR8 (656179) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on ALEXANDR8 69.000 (656179) 69 kV Bus a. Apply fault at the ALEXANDR8 69.000 (656179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALEXANDR8 (656179) 69.0 kV to BELMOND8 (656841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on DOWS8 69.000 (656181) 69 kV Bus a. Apply fault at the DOWS8 69.000 (656181) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOWS8 (656181) 69.0 kV to HAMILTONT8 (656209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on DOWS8 69.000 (656181) 69 kV Bus a. Apply fault at the DOWS8 69.000 (656181) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOWS8 (656181) 69.0 kV to GALT8 (656859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on GENEVA8 69.000 (656187) 69 kV Bus a. Apply fault at the GENEVA8 69.000 (656187) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA8 (656187) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on GLCOATNG8 69.000 (656189) 69 kV Bus a. Apply fault at the GLCOATNG8 69.000 (656189) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLCOATNG8 (656189) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on HAMPTON8 69.000 (656193) 69 kV Bus a. Apply fault at the HAMPTON8 69.000 (656193) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTON8 (656193) 69.0 kV to HAMILTONT8 (656209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on MECSHDFT8 69.000 (656199) 69 kV Bus a. Apply fault at the MECSHDFT8 69.000 (656199) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MECSHDFT8 (656199) 69.0 kV to SWALEDAL8 (656203) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on MECSHDFT8 69.000 (656199) 69 kV Bus a. Apply fault at the MECSHDFT8 69.000 (656199) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MECSHDFT8 (656199) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on HAMILTONT8 69.000 (656209) 69 kV Bus a. Apply fault at the HAMILTONT8 69.000 (656209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMILTONT8 (656209) 69.0 kV to HAMILTON8 (656211) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on APLGTNJC8 69.000 (656269) 69 kV Bus a. Apply fault at the APLGTNJC8 69.000 (656269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APLGTNJC8 (656269) 69.0 kV to APLNGTON8 (656271) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on CONRAD8 69.000 (656275) 69 kV Bus a. Apply fault at the CONRAD8 69.000 (656275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONRAD8 (656275) 69.0 kV to CRAMERJC8 (656279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on CRAMER8 69.000 (656277) 69 kV Bus a. Apply fault at the CRAMER8 69.000 (656277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAMER8 (656277) 69.0 kV to CRAMERJC8 (656279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on CRAMERJC8 69.000 (656279) 69 kV Bus a. Apply fault at the CRAMERJC8 69.000 (656279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAMERJC8 (656279) 69.0 kV to DINSDALE8 (656281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on GRNDYCTR8 69.000 (656289) 69 kV Bus a. Apply fault at the GRNDYCTR8 69.000 (656289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCTR8 (656289) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on WELSBRG G 69.000 (656301) 69 kV Bus a. Apply fault at the WELSBRG G 69.000 (656301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG G (656301) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on WELSBRG G 69.000 (656301) 69 kV Bus a. Apply fault at the WELSBRG G 69.000 (656301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG G (656301) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on ALDEN8 69.000 (656753) 69 kV Bus a. Apply fault at the ALDEN8 69.000 (656753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALDEN8 (656753) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on ALDENJCT8 69.000 (656755) 69 kV Bus a. Apply fault at the ALDENJCT8 69.000 (656755) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALDENJCT8 (656755) 69.0 kV to BUCKEYE8 (656759) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on BOONDOCK8 69.000 (656757) 69 kV Bus a. Apply fault at the BOONDOCK8 69.000 (656757) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONDOCK8 (656757) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BUCKEYE8 69.000 (656759) 69 kV Bus a. Apply fault at the BUCKEYE8 69.000 (656759) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE8 (656759) 69.0 kV to PLEASANT8 (656781) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on ELSWORTH8 69.000 (656763) 69 kV Bus a. Apply fault at the ELSWORTH8 69.000 (656763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELSWORTH8 (656763) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on JEWELL8 69.000 (656777) 69 kV Bus a. Apply fault at the JEWELL8 69.000 (656777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEWELL8 (656777) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on IESLYONT8 69.000 (656778) 69 kV Bus a. Apply fault at the IESLYONT8 69.000 (656778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IESLYONT8 (656778) 69.0 kV to WILLIAMS8 (656787) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on GALT8 69.000 (656859) 69 kV Bus a. Apply fault at the GALT8 69.000 (656859) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALT8 (656859) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on IAFINDP8 69.000 (630341) 69 kV Bus a. Apply fault at the IAFINDP8 69.000 (630341) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IAFINDP8 (630341) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on HAMPTON8 69.000 (656193) 69 kV Bus a. Apply fault at the HAMPTON8 69.000 (656193) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMPTON8 (656193) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on DINSDALE8 69.000 (656281) 69 kV Bus a. Apply fault at the DINSDALE8 69.000 (656281) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DINSDALE8 (656281) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on WELSBRG G 69.000 (656301) 69 kV Bus a. Apply fault at the WELSBRG G 69.000 (656301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSBRG G (656301) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514 and 541518) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858), G19-058 (763895), G19-063 (763926) and Voltage protection trips G22-065 (768284). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858), G19-058 (763895), G19-063 (763926) and Voltage protection trips G22-065 (768284). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514 and 541518) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514 and 541518) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514 and 541518) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Voltage protection trips G17-121 (761841 and 761844). 2. Power oscillations observed following the fault at the WCGS (532751) generating site. This issue is also observed in PQ case and is not impacted by the CQ unit. | 1. Protection disabled with No impact to stability. 2. No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FLTRDG-WG1 (539114). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514 and 541518) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020), ROCKCK (541514 and 541518) and OUTLAW (541546, 541549 and 541550). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BL.PLN.5 161.00 (631012) 161 kV Bus a. Apply Fault at the BL.PLN.5 161.00 (631012) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2031 SUB (50313) 161.0 kV to TOLEDO 5 (631001) 161.0 kV Transmission Circuit #1 b.2. TOLEDO 5 (631001) 161.0 kV to TOLEDO 9 (629101) 34.5 kV Two Winding #1 b.3. TOLEDO 5 (631001) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 b.4. TOLEDO 5 (631001) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.5. NEWHAL5 (631009) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 b.6. BL.PLN.5 (631012) 161.0 kV to BL.PLN.9 (629102) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on EMERY 5 161.00 (631048) 161 kV Bus a. Apply Fault at the EMERY 5 161.00 (631048) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERY 5 (631048) 161.0 kV to EMERYGT2 (629068) 18.0 kV Two Winding #1 b.2. EMERY 5 (631048) 161.0 kV to SHEFFLD5 (656201) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NUTHTCH5 161.00 (631166) 161 kV Bus a. Apply Fault at the NUTHTCH5 161.00 (631166) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP5 (631029) 161.0 kV to NUTHTCH5 (631166) 161.0 kV Transmission Circuit #1 b.2. NUTHTCH5 (631166) 161.0 kV to WHISWIL5 (631171) 161.0 kV Transmission Circuit #1 b.3. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MGS ST1 18.000 (629216) 18 kV Bus a. Apply Fault at the MGS ST1 18.000 (629216) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.2. MGS ST1 (629216) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MGS CT1 18.000 (629214) 18 kV Bus a. Apply Fault at the MGS CT1 18.000 (629214) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 b.2. MGS CT1 (629214) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WALL LK5 161.00 (636235) 161 kV Bus a. Apply Fault at the WALL LK5 161.00 (636235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRIGHT 5 (636050) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.2. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.3. WALL LK5 (636235) 161.0 kV to CENTURY B2 9 (636234) 34.5 kV Two Winding #2 b.4. WALL LK5 (636235) 161.0 kV to WALL LK8 (636236) 69.0 kV Two Winding #1 b.5. WALL LK5 (636235) 161.0 kV to CENTURY B1 9 (636237) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BUTLER 5 161.00 (636240) 161 kV Bus a. Apply Fault at the BUTLER 5 161.00 (636240) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.2. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.4. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.5. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.6. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.7. BUTLER 5 (636240) 161.0 kV to BUTLER 9 (636241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FRANKLN5 161.00 (636230) 161 kV Bus a. Apply Fault at the FRANKLN5 161.00 (636230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.2. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.3. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.4. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.5. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.6. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on BUTLER 5 161.00 (636240) 161 kV Bus a. Apply Fault at the BUTLER 5 161.00 (636240) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKHAWK 5 (636200) 161.0 kV to UNIONTP5 (636225) 161.0 kV Transmission Circuit #1 b.2. UNIONTP5 (636225) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.3. UNIONTP5 (636225) 161.0 kV to UNIONCF5 (638030) 161.0 kV Transmission Circuit #1 b.4. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 b.5. BUTLER 5 (636240) 161.0 kV to BUTLER 9 (636241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTHL CT3 (630773) 13.5 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 b.2. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2031 SUB (50313) 161.0 kV to TOLEDO 5 (631001) 161.0 kV Transmission Circuit #1 b.2. M-TOWN K1 7 (627026) 115.0 kV to M-TOWN K2 7 (631004) 115.0 kV Transmission Circuit #z b.3. TOLEDO 5 (631001) 161.0 kV to TOLEDO 9 (629101) 34.5 kV Two Winding #1 b.4. TOLEDO 5 (631001) 161.0 kV to BL.PLN.5 (631012) 161.0 kV Transmission Circuit #1 b.5. TOLEDO 5 (631001) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.6. M-TOWN K2 7 (631004) 115.0 kV to M-TOWN 9 (629105) 34.5 kV Two Winding #1 b.7. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.8. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ABBOTT 5 161.00 (631000) 161 kV Bus a. Apply Fault at the ABBOTT 5 161.00 (631000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1365 POI (43654) 161.0 kV to ABBOTT 5 (631000) 161.0 kV Transmission Circuit #1 b.2. M-TOWN K1 7 (627026) 115.0 kV to M-TOWN K2 7 (631004) 115.0 kV Transmission Circuit #z b.3. ABBOTT 5 (631000) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.4. M-TOWN K2 7 (631004) 115.0 kV to M-TOWN 9 (629105) 34.5 kV Two Winding #1 b.5. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.6. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 b.7. VIENNA B1 9 (636250) 34.5 kV to ABBOTT 5 (631000) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HAMPTONTAP5 161.00 (656207) 161 kV Bus a. Apply Fault at the HAMPTONTAP5 161.00 (656207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERY 5 (631048) 161.0 kV to SHEFFLD5 (656201) 161.0 kV Transmission Circuit #1 b.2. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.3. HAMPTON5 (656191) 161.0 kV to HAMPTON8 (656193) 69.0 kV Two Winding #1 b.4. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.5. SHEFFLD5 (656201) 161.0 kV to WSHEFFLD8 (656205) 69.0 kV Two Winding #1 b.6. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.2. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on JASPER 5 161.00 (631107) 161 kV Bus a. Apply Fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.2. JASPER 5 (631107) 161.0 kV to NEANKNY5 (635710) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on WRIGHT 5 161.00 (636050) 161 kV Bus a. Apply Fault at the WRIGHT 5 161.00 (636050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER5 (636001) 161.0 kV to WRIGHT 5 (636050) 161.0 kV Transmission Circuit #1 b.2. WRIGHT 5 (636050) 161.0 kV to WRIGHT 8 (636051) 69.0 kV Two Winding #1 b.3. WRIGHT 5 (636050) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on JASPER 5 161.00 (631107) 161 kV Bus a. Apply Fault at the JASPER 5 161.00 (631107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JASPER 8 (630046) 69.0 kV to JASPER 5 (631107) 161.0 kV Two Winding #1 b.2. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ACKLEY 5 161.00 (636229) 161 kV Bus a. Apply Fault at the ACKLEY 5 161.00 (636229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on TIMBRCK5 161.00 (631082) 161 kV Bus a. Apply Fault at the TIMBRCK5 161.00 (631082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TMBRCRK9 (629133) 34.5 kV to TIMBRCK5 (631082) 161.0 kV Two Winding #1 b.2. TIMBERCREEK8 (630963) 69.0 kV to TIMBRCK5 (631082) 161.0 kV Two Winding #1 b.3. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 b.4. TIMBRCK5 (631082) 161.0 kV to M-TOWN_W5 (631128) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply Fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to PR CRK4G (629066) 18.0 kV Two Winding #1 b.2. PRAR CK7 (631017) 115.0 kV to PR CRK1G (629085) 34.5 kV Two Winding #2 b.3. PRAR CK7 (631017) 115.0 kV to PR CRK3G (630787) 13.2 kV Two Winding #1 b.4. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.5. PRAR CK7 (631017) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 b.6. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to IAFINDP5 (631029) 161.0 kV Transmission Circuit #1 b.2. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.3. WELSBRG5 (631008) 161.0 kV to MEC WELSBRG5 (636217) 161.0 kV Transmission Circuit #1 b.4. WELSBRG5 (631008) 161.0 kV to WELSBRG G (656301) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREENMNTN8 (630925) 69.0 kV to FLETCHR J1 8 (630929) 69.0 kV Transmission Circuit #1 b.2. FLETCHR J1 8 (630929) 69.0 kV to FLETCHR J2 8 (630977) 69.0 kV Transmission Circuit #z b.3. FLETCHR J1 8 (630929) 69.0 kV to M-TOWN 5 (631081) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MARION K1 7 115.00 (631019) 115 kV Bus a. Apply Fault at the MARION K1 7 115.00 (631019) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARION J1 8 (629183) 69.0 kV to MARION K1 7 (631019) 115.0 kV Two Winding #1 b.2. MARION J2 8 (630759) 69.0 kV to MARION K2 7 (631195) 115.0 kV Two Winding #1 b.3. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 b.4. MARION K1 7 (631019) 115.0 kV to SWAMPFX7 (631027) 115.0 kV Transmission Circuit #1 b.5. MARION K1 7 (631019) 115.0 kV to OLDSETTLERS7 (631167) 115.0 kV Transmission Circuit #1 b.6. MARION K1 7 (631019) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FRANKLN5 161.00 (636230) 161 kV Bus a. Apply Fault at the FRANKLN5 161.00 (636230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUTHTCH5 (631166) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.2. ACKLEY 5 (636229) 161.0 kV to FRANKLN5 (636230) 161.0 kV Transmission Circuit #1 b.3. FRANKLN5 (636230) 161.0 kV to WALL LK5 (636235) 161.0 kV Transmission Circuit #1 b.4. FRANKLN5 (636230) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.5. HAMPTON5 (656191) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 b.6. SHEFFLD5 (656201) 161.0 kV to HAMPTONTAP5 (656207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ACKLEY 5 161.00 (636229) 161 kV Bus a. Apply Fault at the ACKLEY 5 161.00 (636229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ACKLEY 5 (636229) 161.0 kV to BUTLER 5 (636240) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN K1 7 (627026) 115.0 kV to SUTHL CT1 (630771) 13.5 kV Two Winding #1 b.2. M-TOWN K1 7 (627026) 115.0 kV to SUTHL CT2 (630772) 13.5 kV Two Winding #1 b.3. M-TOWN K1 7 (627026) 115.0 kV to M-TOWN K2 7 (631004) 115.0 kV Transmission Circuit #z b.4. M-TOWN K2 7 (631004) 115.0 kV to M-TOWN 9 (629105) 34.5 kV Two Winding #1 b.5. M-TOWN K2 7 (631004) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.6. M-TOWN 5 (631081) 161.0 kV to M-TOWN K2 7 (631004) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BERTRAM5 161.00 (631092) 161 kV Bus a. Apply Fault at the BERTRAM5 161.00 (631092) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.2. PCI 5 (631090) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 b.3. BERTRAM5 (631092) 161.0 kV to BERTRAM7 (631020) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LAUREL_5 161.00 (631186) 161 kV Bus a. Apply Fault at the LAUREL_5 161.00 (631186) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.2. JASPER 5 (631107) 161.0 kV to LAUREL_5 (631186) 161.0 kV Transmission Circuit #1 b.3. LAUREL B1 9 (635845) 34.5 kV to LAUREL_5 (631186) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on BERTRAM5 161.00 (631092) 161 kV Bus a. Apply Fault at the BERTRAM5 161.00 (631092) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1889 SUB (48893) 161.0 kV to MT VERN5 (631073) 161.0 kV Transmission Circuit #1 b.2. MT VERNoN 8 (629319) 69.0 kV to MT VERN5 (631073) 161.0 kV Two Winding #1 b.3. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.4. MT VERN5 (631073) 161.0 kV to BERTRAM5 (631092) 161.0 kV Transmission Circuit #1 b.5. MT VERN5 (631073) 161.0 kV to WYOMING5 (631099) 161.0 kV Transmission Circuit #1 b.6. BERTRAM5 (631092) 161.0 kV to BERTRAM7 (631020) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to MGS CT2 (629215) 18.0 kV Two Winding #1 b.2. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply Fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to PR CRK1G (629085) 34.5 kV Two Winding #2 b.2. PRAR CK7 (631017) 115.0 kV to PR CRK3G (630787) 13.2 kV Two Winding #1 b.3. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 b.4. PRAR CK7 (631017) 115.0 kV to SUTLIFF7 (631022) 115.0 kV Transmission Circuit #1 b.5. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 b.6. SUTLIFF7 (631022) 115.0 kV to CALAMUS7 (631023) 115.0 kV Transmission Circuit #1 b.7. CALAMUS7 (631023) 115.0 kV to CALAMUS9 (629093) 34.5 kV Two Winding #1 b.8. CALAMUS7 (631023) 115.0 kV to E CALMS7 (631024) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on M-TOWN_W5 161.00 (631128) 161 kV Bus a. Apply Fault at the M-TOWN_W5 161.00 (631128) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBRCK5 (631082) 161.0 kV to M-TOWN_W5 (631128) 161.0 kV Transmission Circuit #1 b.2. M-TOWN_W5 (631128) 161.0 kV to STRY_CO5 (631156) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply Fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP8 (630341) 69.0 kV to IAFINDP5 (631029) 161.0 kV Two Winding #1 b.2. WELSBRG5 (631008) 161.0 kV to IAFINDP5 (631029) 161.0 kV Transmission Circuit #1 b.3. IAFINDP5 (631029) 161.0 kV to NUTHTCH5 (631166) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on M-TOWN 5 161.00 (631081) 161 kV Bus a. Apply Fault at the M-TOWN 5 161.00 (631081) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. M-TOWN 5 (631081) 161.0 kV to MGS ST1 (629216) 18.0 kV Two Winding #1 b.2. M-TOWN 5 (631081) 161.0 kV to TIMBRCK5 (631082) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply Fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDYCN8 (630339) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 b.2. GRNDYCN8 (630339) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply Fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP8 (630341) 69.0 kV to IAFINDP5 (631029) 161.0 kV Two Winding #1 b.2. IAFINDP8 (630341) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on CONRAD 8 69.000 (630350) 69 kV Bus a. Apply Fault at the CONRAD 8 69.000 (630350) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONRAD 8 (630350) 69.0 kV to CONRAD8 (656275) 69.0 kV Transmission Circuit #1 b.2. CONRAD 8 (630350) 69.0 kV to MELRSTAP8 (656297) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OTTERCREEK8 69.000 (630839) 69 kV Bus a. Apply Fault at the OTTERCREEK8 69.000 (630839) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTERCREEK8 (630839) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 b.2. OTTERCREEK8 (630839) 69.0 kV to HUBBRDPUMPT8 (630842) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on PRAR CK7 115.00 (631017) 115 kV Bus a. Apply Fault at the PRAR CK7 115.00 (631017) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAR CK7 (631017) 115.0 kV to MARION K2 7 (631195) 115.0 kV Transmission Circuit #1 b.2. PRAR CK7 (631017) 115.0 kV to BERTRAM7 (631020) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HAMPTNW8 69.000 (636315) 69 kV Bus a. Apply Fault at the HAMPTNW8 69.000 (636315) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMPTNW8 (636315) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 b.2. HAMPTNW8 (636315) 69.0 kV to LATIMER8 (636317) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SHEFFLD8 69.000 (636316) 69 kV Bus a. Apply Fault at the SHEFFLD8 69.000 (636316) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEFFLD8 (636316) 69.0 kV to MECSHDFT8 (656199) 69.0 kV Transmission Circuit #1 b.2. SHEFFLD8 (636316) 69.0 kV to HAMPTNW8 (636315) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on LATIMER8 69.000 (636317) 69 kV Bus a. Apply Fault at the LATIMER8 69.000 (636317) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LATIMER8 (636317) 69.0 kV to HAMPTNW8 (636315) 69.0 kV Transmission Circuit #1 b.2. LATIMER8 (636317) 69.0 kV to WB LATM 8 (636318) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on DUMONT8 69.000 (656021) 69 kV Bus a. Apply Fault at the DUMONT8 69.000 (656021) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUMONT8 (656021) 69.0 kV to GENEVA8 (656187) 69.0 kV Transmission Circuit #1 b.2. DUMONT8 (656021) 69.0 kV to PRKSBRG8 (656065) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on BUCKNER8 69.000 (656149) 69 kV Bus a. Apply Fault at the BUCKNER8 69.000 (656149) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER8 (656149) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 b.2. BUCKNER8 (656149) 69.0 kV to RADCLIFF8 (656791) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on DOWS8 69.000 (656181) 69 kV Bus a. Apply Fault at the DOWS8 69.000 (656181) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOWS8 (656181) 69.0 kV to HAMILTONT8 (656209) 69.0 kV Transmission Circuit #1 b.2. DOWS8 (656181) 69.0 kV to GALT8 (656859) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on ESHEFFTP8 69.000 (656185) 69 kV Bus a. Apply Fault at the ESHEFFTP8 69.000 (656185) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ESHEFFTP8 (656185) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 b.2. ESHEFFTP8 (656185) 69.0 kV to GLCOATNG8 (656189) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GENEVA8 69.000 (656187) 69 kV Bus a. Apply Fault at the GENEVA8 69.000 (656187) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA8 (656187) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 b.2. GENEVA8 (656187) 69.0 kV to DUMONT8 (656021) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GLCOATNG8 69.000 (656189) 69 kV Bus a. Apply Fault at the GLCOATNG8 69.000 (656189) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLCOATNG8 (656189) 69.0 kV to ESHEFFTP8 (656185) 69.0 kV Transmission Circuit #1 b.2. GLCOATNG8 (656189) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HAMPTON5 161.00 (656191) 161 kV Bus a. Apply Fault at the HAMPTON5 161.00 (656191) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMPTON8 (656193) 69.0 kV to HAMPTON5 (656191) 161.0 kV Two Winding #1 b.2. HAMPTON8 (656193) 69.0 kV to HAMPTNW8 (636315) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HAMILTONT8 69.000 (656209) 69 kV Bus a. Apply Fault at the HAMILTONT8 69.000 (656209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMILTONT8 (656209) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 b.2. HAMILTONT8 (656209) 69.0 kV to DOWS8 (656181) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MELRSTAP8 69.000 (656297) 69 kV Bus a. Apply Fault at the MELRSTAP8 69.000 (656297) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MELRSTAP8 (656297) 69.0 kV to CONRAD 8 (630350) 69.0 kV Transmission Circuit #1 b.2. MELRSTAP8 (656297) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG G (656301) 69.0 kV to WELSBRG5 (631008) 161.0 kV Two Winding #1 b.2. WELSBRG G (656301) 69.0 kV to ELDORA8 (656761) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FERNTAP8 69.000 (656303) 69 kV Bus a. Apply Fault at the FERNTAP8 69.000 (656303) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FERNTAP8 (656303) 69.0 kV to WELBRGEASTT8 (656309) 69.0 kV Transmission Circuit #1 b.2. FERNTAP8 (656303) 69.0 kV to APLNGTON8 (656271) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on ALDEN8 69.000 (656753) 69 kV Bus a. Apply Fault at the ALDEN8 69.000 (656753) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDEN8 (656753) 69.0 kV to IFE8 (656775) 69.0 kV Transmission Circuit #1 b.2. ALDEN8 (656753) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on ALDENJCT8 69.000 (656755) 69 kV Bus a. Apply Fault at the ALDENJCT8 69.000 (656755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDENJCT8 (656755) 69.0 kV to BUCKNER8 (656149) 69.0 kV Transmission Circuit #1 b.2. ALDENJCT8 (656755) 69.0 kV to ALDNRRLTP8 (656795) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BUCKEYE8 69.000 (656759) 69 kV Bus a. Apply Fault at the BUCKEYE8 69.000 (656759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKEYE8 (656759) 69.0 kV to PLEASANT8 (656781) 69.0 kV Transmission Circuit #1 b.2. BUCKEYE8 (656759) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FARM_TAP8 69.000 (656769) 69 kV Bus a. Apply Fault at the FARM_TAP8 69.000 (656769) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARM_TAP8 (656769) 69.0 kV to IAFINDP8 (630341) 69.0 kV Transmission Circuit #1 b.2. FARM_TAP8 (656769) 69.0 kV to HAMPTON8 (656193) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WELSBRG5 161.00 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 161.00 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to M-TOWN 5 (631081) 161.0 kV Transmission Circuit #1 b.2. WELSBRG5 (631008) 161.0 kV to WELSBRG G (656301) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on IAFINDP5 161.00 (631029) 161 kV Bus a. Apply Fault at the IAFINDP5 161.00 (631029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP5 (631029) 161.0 kV to IAFINDP8 (630341) 69.0 kV Two Winding #1 b.2. IAFINDP5 (631029) 161.0 kV to WELSBRG5 (631008) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GRNDYMUNT8 69.000 (656305) 69 kV Bus a. Apply Fault at the GRNDYMUNT8 69.000 (656305) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDYMUNT8 (656305) 69.0 kV to GRNDYCTR8 (656289) 69.0 kV Transmission Circuit #1 b.2. GRNDYMUNT8 (656305) 69.0 kV to GRNDYCN8 (630339) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on IFE8 69.000 (656775) 69 kV Bus a. Apply Fault at the IFE8 69.000 (656775) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IFE8 (656775) 69.0 kV to IAFINDP8 (630341) 69.0 kV Transmission Circuit #1 b.2. IFE8 (656775) 69.0 kV to ALDEN8 (656753) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ELDORA8 69.000 (656761) 69 kV Bus a. Apply Fault at the ELDORA8 69.000 (656761) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELDORA8 (656761) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 b.2. ELDORA8 (656761) 69.0 kV to OTTERCREEK8 (630839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on ALDNRRLTP8 69.000 (656795) 69 kV Bus a. Apply Fault at the ALDNRRLTP8 69.000 (656795) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDNRRLTP8 (656795) 69.0 kV to ALDEN8 (656753) 69.0 kV Transmission Circuit #1 b.2. ALDNRRLTP8 (656795) 69.0 kV to ALDENJCT8 (656755) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WELBRGEASTT869.000 (656309) 69 kV Bus a. Apply Fault at the WELBRGEASTT869.000 (656309) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELBRGEASTT8 (656309) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 b.2. WELBRGEASTT8 (656309) 69.0 kV to FERNTAP8 (656303) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SUTLIFF7 115.00 (631022) 115 kV Bus a. Apply Fault at the SUTLIFF7 115.00 (631022) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTLIFF7 (631022) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 b.2. SUTLIFF7 (631022) 115.0 kV to CALAMUS7 (631023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SQUARED7 115.00 (631032) 115 kV Bus a. Apply Fault at the SQUARED7 115.00 (631032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQUARED7 (631032) 115.0 kV to STON PT7 (631015) 115.0 kV Transmission Circuit #1 b.2. SQUARED7 (631032) 115.0 kV to PRAR CK7 (631017) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on MECSHDFT8 69.000 (656199) 69 kV Bus a. Apply Fault at the MECSHDFT8 69.000 (656199) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MECSHDFT8 (656199) 69.0 kV to WSHEFFLD8 (656205) 69.0 kV Transmission Circuit #1 b.2. MECSHDFT8 (656199) 69.0 kV to SHEFFLD8 (636316) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WB LATM 8 69.000 (636318) 69 kV Bus a. Apply Fault at the WB LATM 8 69.000 (636318) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WB LATM 8 (636318) 69.0 kV to LATIMER8 (636317) 69.0 kV Transmission Circuit #1 b.2. WB LATM 8 (636318) 69.0 kV to COULTR 8 (630357) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GALT8 69.000 (656859) 69 kV Bus a. Apply Fault at the GALT8 69.000 (656859) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GALT8 (656859) 69.0 kV to DOWS8 (656181) 69.0 kV Transmission Circuit #1 b.2. GALT8 (656859) 69.0 kV to WILLEMSN8 (656903) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SHEFFLD5 161.00 (656201) 161 kV Bus a. Apply Fault at the SHEFFLD5 161.00 (656201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSHEFFLD8 (656205) 69.0 kV to SHEFFLD5 (656201) 161.0 kV Two Winding #1 b.2. WSHEFFLD8 (656205) 69.0 kV to MECSHDFT8 (656199) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on PLEASANT8 69.000 (656781) 69 kV Bus a. Apply Fault at the PLEASANT8 69.000 (656781) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLEASANT8 (656781) 69.0 kV to OTTERCREEK8 (630839) 69.0 kV Transmission Circuit #1 b.2. PLEASANT8 (656781) 69.0 kV to BUCKEYE8 (656759) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HAMILTONT8 (656209) 69 kV Bus a. Apply Fault at the HAMILTONT8 (656209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMILTONT8 (656209) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HAMPTNW8 (636315) 69 kV Bus a. Apply Fault at the HAMPTNW8 (636315) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAMPTNW8 (636315) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WELSBRG5 (631008) 161 kV Bus a. Apply Fault at the WELSBRG5 (631008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSBRG5 (631008) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on FRANKLN5 (636230) 161 kV Bus a. Apply Fault at the FRANKLN5 (636230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLN5 (636230) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on ALDNRRLTP8 (656795) 69 kV Bus a. Apply Fault at the ALDNRRLTP8 (656795) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALDNRRLTP8 (656795) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on IAFINDP8 (630341) 69 kV Bus a. Apply Fault at the IAFINDP8 (630341) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IAFINDP8 (630341) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on MONoLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONoLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONoLITH 3 (640590) 345.0 kV to MONoLITH 7 (640591) 115.0 kV to MONoLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. THISTLE7 (539801) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on G22-015-TAP 345.00 (767280) 345 kV Bus a. Apply Fault at the G22-015-TAP 345.00 (767280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | 2025 Annual Interim | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONoLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips FRMR CTY (635020). | Protection disabled with No impact to stability.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCN8 (630339) 69.0 kV to WELSBRG G (656301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the MGS ST (629216) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on GRNDYCN8 69.000 (630339) 69 kV Bus a. Apply fault at the GRNDYCN8 69.000 (630339) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCN8 (630339) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the MGS ST (629216) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on GRNDYCTR8 69.000 (656289) 69 kV Bus a. Apply fault at the GRNDYCTR8 69.000 (656289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDYCTR8 (656289) 69.0 kV to GRNDYMUNT8 (656305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the MGS ST (629216) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25S | Base | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
03 CENTRAL | 2025 Annual Interim | 25W | Base | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the WCGS (532751) generating site. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on MAGZREC5 161.00 (507195) 161 kV Bus a. Apply fault at the MAGZREC5 161.00 (507195) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DANVLE AR! (337902) 161.0 kV to MAGZREC5 (507195) 161.0 kV Transmission Circuit #1 b.2. NMAGZIN5 (507190) 161.0 kV to MAGZREC5 (507195) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on FITZHUGH 5 161.00 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 161.00 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 (503902) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on DARDANE5 161.00 (505508) 161 kV Bus a. Apply fault at the DARDANE5 161.00 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on OZARK H5 161.00 (505516) 161 kV Bus a. Apply fault at the OZARK H5 161.00 (505516) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 (505516) 161.0 kV to VAN BUR5 (505522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on NMAGZIN5 161.00 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 161.00 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 (507190) 161.0 kV to WBOONVL5 (507192) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on NMAGZIN5 161.00 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 161.00 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 (507190) 161.0 kV to BRANCH 5 (515316) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on DARDANE5 161.00 (505508) 161 kV Bus a. Apply fault at the DARDANE5 161.00 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit #1 b.2. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.3. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit #1 b.4. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on FITZHUGH 5 161.00 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 161.00 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on FIG_FIVE 2 69.000 (504185) 69 kV Bus a. Apply fault at the FIG_FIVE 2 69.000 (504185) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI_N 2 (504032) 69.0 kV to FIG_FIVE 2 (504185) 69.0 kV Transmission Circuit #1 b.2. FIG_FIVE 2 (504185) 69.0 kV to CEDARTP2 (506967) 69.0 kV Transmission Circuit #1 b.3. GREENLD2 (506936) 69.0 kV to STRICKR2 (506974) 69.0 kV Transmission Circuit #1 b.4. CEDARTP2 (506967) 69.0 kV to STRICKR2 (506974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on BOONVIL2 69.000 (507183) 69 kV Bus a. Apply fault at the BOONVIL2 69.000 (507183) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONVIL2 (507183) 69.0 kV to BRANCH 2 (515313) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on VBI_N 2 69.000 (504032) 69 kV Bus a. Apply fault at the VBI_N 2 69.000 (504032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI_N 2 (504032) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on BOONEVIL 2 69.000 (504172) 69 kV Bus a. Apply fault at the BOONEVIL 2 69.000 (504172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONEVIL 2 (504172) 69.0 kV to BOONVIL2 (507183) 69.0 kV Transmission Circuit #1 b.2. BOONEVIL 2 (504172) 69.0 kV to WBOONVL2 (507198) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on BRIGSKM 5 161.00 (513044) 161 kV Bus a. Apply fault at the BRIGSKM 5 161.00 (513044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BRIGGS (300767) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 b.2. TAHLQH 5 (512655) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 b.3. STIWEL5 (512704) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on 5CDRCRST 161.00 (301344) 161 kV Bus a. Apply fault at the 5CDRCRST 161.00 (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on 5PARK 161.00 (301307) 161 kV Bus a. Apply fault at the 5PARK 161.00 (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK (301307) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on 7CLANS 5 161.00 (515956) 161 kV Bus a. Apply fault at the 7CLANS 5 161.00 (515956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 (512655) 161.0 kV to 7CLANS 5 (515956) 161.0 kV Transmission Circuit #1 b.2. MUSKOGE5 (515222) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 b.3. 7CLANS 5 (515956) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on SUNSTCN5 161.00 (515254) 161 kV Bus a. Apply fault at the SUNSTCN5 161.00 (515254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 (505582) 161.0 kV to SUNSTCN5 (515254) 161.0 kV Transmission Circuit #1 b.2. SUNSTCN5 (515254) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.3. SUNSTCN5 (515254) 161.0 kV to SUNSTCR5 (521124) 161.0 kV Transmission Circuit #z1 b.4. TARBY 5 (515264) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.5. SHAD-PT5 (515265) 161.0 kV to SHADYPT5 (521062) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on QUANXTP5 161.00 (515310) 161 kV Bus a. Apply fault at the QUANXTP5 161.00 (515310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 (515300) 161.0 kV to QUANXTP5 (515310) 161.0 kV Transmission Circuit #1 b.2. QUANXTP5 (515310) 161.0 kV to BARLING5 (515311) 161.0 kV Transmission Circuit #1 b.3. QUANXTP5 (515310) 161.0 kV to QUANEXS5 (515474) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on CARNALL2 69.000 (515287) 69 kV Bus a. Apply fault at the CARNALL2 69.000 (515287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNALL2 (515287) 69.0 kV to MASSARD2 (515342) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on PARKVU 2 69.000 (515288) 69 kV Bus a. Apply fault at the PARKVU 2 69.000 (515288) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKVU 2 (515288) 69.0 kV to BELLAVE2 (515290) 69.0 kV Transmission Circuit #1 b.2. PARKVU 2 (515288) 69.0 kV to MASSARD2 (515342) 69.0 kV Transmission Circuit #1 b.3. BELLAVE2 (515290) 69.0 kV to 3RDST 2 (515307) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on VBAVEC 2 69.000 (515298) 69 kV Bus a. Apply fault at the VBAVEC 2 69.000 (515298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBAVEC 2 (515298) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on CHAFXING-TP5161.00 (504189) 161 kV Bus a. Apply fault at the CHAFXING-TP5161.00 (504189) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAFFEEXING5 (504187) 161.0 kV to CHAFXING-TP5 (504189) 161.0 kV Transmission Circuit #1 b.2. CHAFXING-TP5 (504189) 161.0 kV to RYEHILL5 (504190) 161.0 kV Transmission Circuit #1 b.3. CHAFXING-TP5 (504189) 161.0 kV to MCSTLTP5 (515876) 161.0 kV Transmission Circuit #1 b.4. FTSMTHE5 (515300) 161.0 kV to COLONY 5 (515345) 161.0 kV Transmission Circuit #1 b.5. MASSARD5 (515343) 161.0 kV to RYHLLTP5 (515523) 161.0 kV Transmission Circuit #1 b.6. COLONY 5 (515345) 161.0 kV to BATTLEF5 (515349) 161.0 kV Transmission Circuit #1 b.7. BATTLEF5 (515349) 161.0 kV to RYHLLTP5 (515523) 161.0 kV Transmission Circuit #1 b.8. RYHLLTP5 (515523) 161.0 kV to MCSTLTP5 (515876) 161.0 kV Transmission Circuit #1 b.9. MCSTL2 5 (515874) 161.0 kV to MCSTLTP5 (515876) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on BARLING5 161.00 (515311) 161 kV Bus a. Apply fault at the BARLING5 161.00 (515311) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 (515311) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on NITROTP5 161.00 (515329) 161 kV Bus a. Apply fault at the NITROTP5 161.00 (515329) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.2. NITROTP5 (515329) 161.0 kV to SIMMONS5 (515332) 161.0 kV Transmission Circuit #1 b.3. NITROTP5 (515329) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.4. NITROTP5 (515329) 161.0 kV to NITROUS5 (515350) 161.0 kV Transmission Circuit #1 b.5. SIMMONS5 (515332) 161.0 kV to DYER 5 (515333) 161.0 kV Transmission Circuit #1 b.6. DYER 5 (515333) 161.0 kV to ALMA 5 (515334) 161.0 kV Transmission Circuit #1 b.7. ALMA 5 (515334) 161.0 kV to RUDY 5 (515337) 161.0 kV Transmission Circuit #1 b.8. RUDY 5 (515337) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 b.9. VBI 5 (515339) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on ROLANTP2 69.000 (515277) 69 kV Bus a. Apply fault at the ROLANTP2 69.000 (515277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 b.2. ROLANTP2 (515277) 69.0 kV to KLGORE 2 (515335) 69.0 kV Transmission Circuit #1 b.3. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on OAKGROV5 161.00 (515340) 161 kV Bus a. Apply fault at the OAKGROV5 161.00 (515340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 (515339) 161.0 kV to OAKGROV5 (515340) 161.0 kV Transmission Circuit #1 b.2. OAKGROV5 (515340) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 b.3. WHITESD5 (515341) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SUBIACT5 161.00 (515440) 161 kV Bus a. Apply fault at the SUBIACT5 161.00 (515440) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 5 (515316) 161.0 kV to SHORTMT5 (515358) 161.0 kV Transmission Circuit #1 b.2. IGO 5 (515355) 161.0 kV to RAZRBAK5 (515357) 161.0 kV Transmission Circuit #1 b.3. RAZRBAK5 (515357) 161.0 kV to SUBIACT5 (515440) 161.0 kV Transmission Circuit #1 b.4. SHORTMT5 (515358) 161.0 kV to SUBIACT5 (515440) 161.0 kV Transmission Circuit #1 b.5. SUBIACT5 (515440) 161.0 kV to SUBIACO5 (515441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on ALTUS 161.00 (515352) 161 kV Bus a. Apply fault at the ALTUS 161.00 (515352) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 (503902) 161.0 kV to ALTUS (515352) 161.0 kV Transmission Circuit #1 b.2. ALTUS (515352) 161.0 kV to GLCARBN (515353) 161.0 kV Transmission Circuit #1 b.3. GLCARBN (515353) 161.0 kV to NoARK 5 (515354) 161.0 kV Transmission Circuit #1 b.4. NoARK 5 (515354) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on GRNDPRT5 161.00 (515524) 161 kV Bus a. Apply fault at the GRNDPRT5 161.00 (515524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 (504192) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.2. BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.3. VBI 5 (515339) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on HWY59TP5 161.00 (515527) 161 kV Bus a. Apply fault at the HWY59TP5 161.00 (515527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 (504191) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.2. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.3. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on COALHIL2 69.000 (515322) 69 kV Bus a. Apply fault at the COALHIL2 69.000 (515322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 (515320) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 b.2. COALHIL2 (515322) 69.0 kV to AVECOZK2 (515324) 69.0 kV Transmission Circuit #1 b.3. AVECOZK2 (515324) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on PENDER 2 69.000 (515317) 69 kV Bus a. Apply fault at the PENDER 2 69.000 (515317) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 2 (515313) 69.0 kV to PENDER 2 (515317) 69.0 kV Transmission Circuit #1 b.2. PENDER 2 (515317) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on JONSON 5 161.00 (515293) 161 kV Bus a. Apply fault at the JONSON 5 161.00 (515293) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 (515293) 161.0 kV to OAKPARK5 (515315) 161.0 kV Transmission Circuit #1 b.2. JONSON 5 (515293) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on HELBERG5 161.00 (515327) 161 kV Bus a. Apply fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on VBI 2 69.000 (515336) 69 kV Bus a. Apply fault at the VBI 2 69.000 (515336) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 (515336) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on BRANCH 2 69.000 (515313) 69 kV Bus a. Apply fault at the BRANCH 2 69.000 (515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 2 (515313) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on LSPADRA2 69.000 (515320) 69 kV Bus a. Apply fault at the LSPADRA2 69.000 (515320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 (515320) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on HELBERG2 69.000 (515325) 69 kV Bus a. Apply fault at the HELBERG2 69.000 (515325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG2 (515325) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on MASSARD2 69.000 (515342) 69 kV Bus a. Apply fault at the MASSARD2 69.000 (515342) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 (515342) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on 5LIBRTY 161.00 (300869) 161 kV Bus a. Apply fault at the 5LIBRTY 161.00 (300869) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LIBRTY (300869) 161.0 kV to 5LBRTYTKM (301557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on 5STIGLER 161.00 (301550) 161 kV Bus a. Apply fault at the 5STIGLER 161.00 (301550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on 5LBRTYTKM 161.00 (301557) 161 kV Bus a. Apply fault at the 5LBRTYTKM 161.00 (301557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM (301557) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on 5AKINSKM 161.00 (301558) 161 kV Bus a. Apply fault at the 5AKINSKM 161.00 (301558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5AKINSKM (301558) 161.0 kV to AKINS E5 (505526) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on 5AKINSKM 161.00 (301558) 161 kV Bus a. Apply fault at the 5AKINSKM 161.00 (301558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5AKINSKM (301558) 161.0 kV to AKINS W5 (505528) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 (505522) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on LIBERTY5 161.00 (505524) 161 kV Bus a. Apply fault at the LIBERTY5 161.00 (505524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 (505524) 161.0 kV to AKINS E5 (505526) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on AKINS E5 161.00 (505526) 161 kV Bus a. Apply fault at the AKINS E5 161.00 (505526) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKINS E5 (505526) 161.0 kV to AKINS W5 (505528) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on AKINS W5 161.00 (505528) 161 kV Bus a. Apply fault at the AKINS W5 161.00 (505528) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKINS W5 (505528) 161.0 kV to SALISAW5 (505550) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on SALISAW5 161.00 (505550) 161 kV Bus a. Apply fault at the SALISAW5 161.00 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 (505550) 161.0 kV to GORE 5 (505552) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on VBI 5 161.00 (515339) 161 kV Bus a. Apply fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 (515339) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on NALCOTP5 161.00 (515348) 161 kV Bus a. Apply fault at the NALCOTP5 161.00 (515348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 (515348) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV to CLK X1 1 (505513) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV to CLK X2 1 (505515) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SALISAW5 161.00 (505550) 161 kV Bus a. Apply fault at the SALISAW5 161.00 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 (505550) 161.0 kV to SALSWGR2 (512652) 69.0 kV to SALTER1 (512831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on SALISAW5 161.00 (505550) 161 kV Bus a. Apply fault at the SALISAW5 161.00 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 (505550) 161.0 kV to SALSWGR2 (512652) 69.0 kV to SALTER2 (512842) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 (512655) 161.0 kV to TAHLQH 2 (512647) 69.0 kV to TAHLQH1 (512851) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 (512655) 161.0 kV to TAHLQH 2 (512647) 69.0 kV to TAHLQH2 1 (512825) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on BRANCH 5 161.00 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 161.00 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 2 (515313) 69.0 kV to BRANCH 5 (515316) 161.0 kV to BRANCH21 (515708) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 (515320) 69.0 kV to LSPADRA5 (515319) 161.0 kV to LSPADR41 (515733) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on VBI 5 161.00 (515339) 161 kV Bus a. Apply fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 (515336) 69.0 kV to VBI 5 (515339) 161.0 kV to VBI 1 (515769) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on MASSARD5 161.00 (515343) 161 kV Bus a. Apply fault at the MASSARD5 161.00 (515343) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 (515342) 69.0 kV to MASSARD5 (515343) 161.0 kV to MASSARD1 (515735) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on BOONVIL2 69.000 (507183) 69 kV Bus a. Apply fault at the BOONVIL2 69.000 (507183) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONVIL2 (507183) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | No | Yes | 1. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC ( 511565), O.K.U.-7 (511456) rise above 1.2 pu threshold. This issue is also observed in base case and is not impacted by the CQ unit. 3. Post fault steady state voltages at GEN-2018-015 (762460), and G18-015-TAP (762467) rise above 1.1 pu threshold. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Sustained high reactive power output following the fault is observed at the G20-020 (764511, 76514) generating site, Mvar output remains high for more than 10 seconds following the fault and the high voltage relay trips the unit at bus 764511. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587953) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. There has been no observable impact from the CQ request under study to this issue. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | No | No | Yes | 1. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. 3. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), and O.K.U.-7 (511456) rise above 1.2pu threshold. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Post fault steady state voltages at GEN-2018-015 (762460) and G18-015-TAP (762467) remain below 0.9 pu threshold. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. There has been no observable impact from the CQ request under study to this issue. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 5RUSSELVL.E!161.00 (337905) 161 kV Bus a. Apply Fault at the 5RUSSELVL.E!161.00 (337905) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RUSSELVL.IN (337862) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit #1 b.2. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit #1 b.3. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.4. 5RUSSELVL.E! (337905) 161.0 kV to 5RUSSELVL.E_ (337916) 161.0 kV Transmission Circuit #r1 b.5. 5RUSSELVL.E! (337905) 161.0 kV to 5RUSSELVL.E_ (337916) 161.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on DARDANE5 161.00 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 161.00 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.4. DARDANE5 (505508) 161.0 kV to DAR1&2 1 (505510) 13.8 kV Two Winding #1 b.5. DARDANE5 (505508) 161.0 kV to DAR3&4 1 (505512) 13.8 kV Two Winding #1 b.6. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on OZARK H5 161.00 (505516) 161 kV Bus a. Apply Fault at the OZARK H5 161.00 (505516) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.3. OZARK H5 (505516) 161.0 kV to OZK1&2 1 (505518) 13.8 kV Two Winding #1 b.4. OZARK H5 (505516) 161.0 kV to OZK345 1 (505520) 13.8 kV Two Winding #1 b.5. OZARK H5 (505516) 161.0 kV to VAN BUR5 (505522) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.2. CLK X1 1 (505513) 12.5 kV to CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 b.2. CLK X2 1 (505515) 12.5 kV to CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RS KERR5 161.00 (505582) 161 kV Bus a. Apply Fault at the RS KERR5 161.00 (505582) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STIGLER (300877) 69.0 kV to 5STIGLER (301550) 161.0 kV Two Winding #1 b.2. 5STIGLER (301550) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 b.3. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.4. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.5. RS KERR5 (505582) 161.0 kV to RSK1&2 1 (505584) 13.8 kV Two Winding #1 b.6. RS KERR5 (505582) 161.0 kV to RSK3&4 1 (505586) 13.8 kV Two Winding #1 b.7. RS KERR5 (505582) 161.0 kV to SUNSTCN5 (515254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RS KERR5 161.00 (505582) 161 kV Bus a. Apply Fault at the RS KERR5 161.00 (505582) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.2. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.3. RS KERR5 (505582) 161.0 kV to RSK1&2 1 (505584) 13.8 kV Two Winding #1 b.4. RS KERR5 (505582) 161.0 kV to RSK3&4 1 (505586) 13.8 kV Two Winding #1 b.5. RS KERR5 (505582) 161.0 kV to SUNSTCN5 (515254) 161.0 kV Transmission Circuit #1 b.6. SUNSTCN5 (515254) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.7. SUNSTCN5 (515254) 161.0 kV to SUNSTCR5 (521124) 161.0 kV Transmission Circuit #z1 b.8. TARBY 5 (515264) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.9. SHAD-PT5 (515265) 161.0 kV to SHADYPT5 (521062) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply Fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HWY59 5 (504191) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.2. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.3. TAHLQH 5 (512655) 161.0 kV to 7CLANS 5 (515956) 161.0 kV Transmission Circuit #1 b.4. MUSKOGE5 (515222) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 b.5. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.6. 7CLANS 5 (515956) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 b.7. TAHLQH 2 (512647) 69.0 kV to TAHLQH 5 (512655) 161.0 kV to TAHLQH1 (512851) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on IGO 5 161.00 (515355) 161 kV Bus a. Apply Fault at the IGO 5 161.00 (515355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 b.2. NoARK 5 (515354) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 b.3. IGO 5 (515355) 161.0 kV to RAZRBAK5 (515357) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on VBI 2 69.000 (515336) 69 kV Bus a. Apply Fault at the VBI 2 69.000 (515336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI_N 2 (504032) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.2. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.3. VBI 2 (515336) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on VBI 2 69.000 (515336) 69 kV Bus a. Apply Fault at the VBI 2 69.000 (515336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBAVEC 2 (515298) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.2. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.3. VBI 2 (515336) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on 5QUITMAN! 161.00 (337926) 161 kV Bus a. Apply Fault at the 5QUITMAN! 161.00 (337926) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5QUITMAN! (337926) 161.0 kV to 5HEBER.S (338112) 161.0 kV Transmission Circuit #1 b.2. 5QUITMAN! (337926) 161.0 kV to 5BEE BRANCH# (338831) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to 5MARSHALL# (338517) 161.0 kV Transmission Circuit #1 b.4. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.5. 5HEBER.N# (338758) 161.0 kV to GREERSF5 (505422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on 5HILLTOP% 161.00 (338110) 161 kV Bus a. Apply Fault at the 5HILLTOP% 161.00 (338110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HILLTOP% (338110) 161.0 kV to 5MARSHALL# (338517) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.3. 5CLINTON.W# (338832) 161.0 kV to 5BOTKINBURG# (338834) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on 5DANVLE AR! 161.00 (337902) 161 kV Bus a. Apply Fault at the 5DANVLE AR! 161.00 (337902) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit #1 b.2. 5DANVLE AR! (337902) 161.0 kV to MAGZREC5 (507195) 161.0 kV Transmission Circuit #1 b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.4. 3DANVLE AR (337901) 115.0 kV to 5DANVLE AR! (337902) 161.0 kV to 1DANVLE AR (337944) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on 5HILLTOP% 161.00 (338110) 161 kV Bus a. Apply Fault at the 5HILLTOP% 161.00 (338110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply Fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LBRTYTKM (301557) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #z1 b.2. OZARK H5 (505516) 161.0 kV to VAN BUR5 (505522) 161.0 kV Transmission Circuit #1 b.3. VAN BUR5 (505522) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #1 b.4. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.5. VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #z1 b.6. LIBERTY5 (505524) 161.0 kV to AKINS E5 (505526) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on 5STIGLER 161.00 (301550) 161 kV Bus a. Apply Fault at the 5STIGLER 161.00 (301550) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STIGLER (300877) 69.0 kV to 5STIGLER (301550) 161.0 kV Two Winding #1 b.2. 5STIGLER (301550) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 b.3. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.4. GORE 5 (505552) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on EUFAULA5 161.00 (505570) 161 kV Bus a. Apply Fault at the EUFAULA5 161.00 (505570) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STIGLER (300877) 69.0 kV to 5STIGLER (301550) 161.0 kV Two Winding #1 b.2. 5STIGLER (301550) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 b.3. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.4. EUF #1 1 (505576) 13.8 kV to EUFAULA5 (505570) 161.0 kV to EUFAULA4 (505574) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply Fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PARK (301307) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 b.2. 5CDRCRST (301344) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 b.3. TAHLQH 5 (512655) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 b.4. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.5. TAHLQH 5 (512655) 161.0 kV to 7CLANS 5 (515956) 161.0 kV Transmission Circuit #1 b.6. TAHLQH 2 (512647) 69.0 kV to TAHLQH 5 (512655) 161.0 kV to TAHLQH2 1 (512825) 13.8 kV Three Winding #2 b.7. TAHLQH 2 (512647) 69.0 kV to TAHLQH 5 (512655) 161.0 kV to TAHLQH1 (512851) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BRANCH 5 161.00 (515316) 161 kV Bus a. Apply Fault at the BRANCH 5 161.00 (515316) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOONVIL2 (507183) 69.0 kV to BRANCH 2 (515313) 69.0 kV Transmission Circuit #1 b.2. NMAGZIN5 (507190) 161.0 kV to BRANCH 5 (515316) 161.0 kV Transmission Circuit #1 b.3. BRANCH 2 (515313) 69.0 kV to PENDER 2 (515317) 69.0 kV Transmission Circuit #1 b.4. BRANCH 5 (515316) 161.0 kV to SHORTMT5 (515358) 161.0 kV Transmission Circuit #1 b.5. BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.6. BRANCH 5 (515316) 161.0 kV to GEN-2017-231 (760221) 161.0 kV Transmission Circuit #1 b.7. BRANCH 5 (515316) 161.0 kV to GEN-2021-033 (765610) 161.0 kV Transmission Circuit #1 b.8. BRANCH 2 (515313) 69.0 kV to BRANCH 5 (515316) 161.0 kV to BRANCH21 (515708) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.2. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. PENDER 2 (515317) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 b.3. AVECOZK2 (515324) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 b.4. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.5. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LSPADRA2 69.000 (515320) 69 kV Bus a. Apply Fault at the LSPADRA2 69.000 (515320) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 b.2. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 b.3. LSPADRA2 (515320) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 b.4. LSPADRA5 (515319) 161.0 kV to LSPADRA2 (515320) 69.0 kV to LSPADR41 (515733) 13.8 kV Three Winding #1 b.6. LSPADRA2 (515320) 69.0 kV to LSPADR21 (515779) 34.5 kV to LSPADR31 (515780) 2.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on VBI 5 161.00 (515339) 161 kV Bus a. Apply Fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI_N 2 (504032) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.2. VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #z1 b.3. VBAVEC 2 (515298) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.4. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.5. VBI 5 (515339) 161.0 kV to OAKGROV5 (515340) 161.0 kV Transmission Circuit #1 b.6. VBI 5 (515339) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 b.7. VBI 5 (515339) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 b.8. VBI 5 (515339) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.9. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.10. VBI 2 (515336) 69.0 kV to VBI 5 (515339) 161.0 kV to VBI 1 (515769) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FITZHUGH 5 161.00 (503902) 161 kV Bus a. Apply Fault at the FITZHUGH 5 161.00 (503902) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. FITZHUGH 5 (503902) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on COALHIL2 69.000 (515322) 69 kV Bus a. Apply Fault at the COALHIL2 69.000 (515322) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COALHIL2 (515322) 69.0 kV to AVECOZK2 (515324) 69.0 kV Transmission Circuit #1 b.2. COALHIL2 (515322) 69.0 kV to LSPADRA2 (515320) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NITROTP5 161.00 (515329) 161 kV Bus a. Apply Fault at the NITROTP5 161.00 (515329) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NITROTP5 (515329) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.2. NITROTP5 (515329) 161.0 kV to SIMMONS5 (515332) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on SIMMONS5 161.00 (515332) 161 kV Bus a. Apply Fault at the SIMMONS5 161.00 (515332) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIMMONS5 (515332) 161.0 kV to NITROTP5 (515329) 161.0 kV Transmission Circuit #1 b.2. SIMMONS5 (515332) 161.0 kV to DYER 5 (515333) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RUDY 5 161.00 (515337) 161 kV Bus a. Apply Fault at the RUDY 5 161.00 (515337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUDY 5 (515337) 161.0 kV to ALMA 5 (515334) 161.0 kV Transmission Circuit #1 b.2. RUDY 5 (515337) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on OAKGROV5 161.00 (515340) 161 kV Bus a. Apply Fault at the OAKGROV5 161.00 (515340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGROV5 (515340) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 b.2. OAKGROV5 (515340) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on NALCOTP5 161.00 (515348) 161 kV Bus a. Apply Fault at the NALCOTP5 161.00 (515348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NALCOTP5 (515348) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 b.2. NALCOTP5 (515348) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ALTUS 161.00 (515352) 161 kV Bus a. Apply Fault at the ALTUS 161.00 (515352) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTUS (515352) 161.0 kV to FITZHUGH 5 (503902) 161.0 kV Transmission Circuit #1 b.2. ALTUS (515352) 161.0 kV to GLCARBN (515353) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GLCARBN 161.00 (515353) 161 kV Bus a. Apply Fault at the GLCARBN 161.00 (515353) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLCARBN (515353) 161.0 kV to ALTUS (515352) 161.0 kV Transmission Circuit #1 b.2. GLCARBN (515353) 161.0 kV to NoARK 5 (515354) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply Fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LSPADRA2 (515320) 69.0 kV to LSPADRA5 (515319) 161.0 kV to LSPADR41 (515733) 13.8 kV Three Winding #1 b.2. LSPADRA2 (515320) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 b.2. HELBERG2 (515325) 69.0 kV to AVECOZK2 (515324) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on VBI 5 161.00 (515339) 161 kV Bus a. Apply Fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI 2 (515336) 69.0 kV to VBI 5 (515339) 161.0 kV to VBI 1 (515769) 13.8 kV Three Winding #1 b.2. VBI 2 (515336) 69.0 kV to VBI_N 2 (504032) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRNDPRT5 161.00 (515524) 161 kV Bus a. Apply Fault at the GRNDPRT5 161.00 (515524) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDPRT5 (515524) 161.0 kV to BRANCH 5 (515316) 161.0 kV Transmission Circuit #1 b.2. GRNDPRT5 (515524) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on AVECOZK2 69.000 (515324) 69 kV Bus a. Apply Fault at the AVECOZK2 69.000 (515324) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVECOZK2 (515324) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 b.2. AVECOZK2 (515324) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on PUDDIN 5 161.00 (515346) 161 kV Bus a. Apply Fault at the PUDDIN 5 161.00 (515346) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUDDIN 5 (515346) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. PUDDIN 5 (515346) 161.0 kV to NITROTP5 (515329) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on DYER 5 161.00 (515333) 161 kV Bus a. Apply Fault at the DYER 5 161.00 (515333) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DYER 5 (515333) 161.0 kV to SIMMONS5 (515332) 161.0 kV Transmission Circuit #1 b.2. DYER 5 (515333) 161.0 kV to ALMA 5 (515334) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on TWNBRDG5 161.00 (515360) 161 kV Bus a. Apply Fault at the TWNBRDG5 161.00 (515360) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWNBRDG5 (515360) 161.0 kV to RUDY 5 (515337) 161.0 kV Transmission Circuit #1 b.2. TWNBRDG5 (515360) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WHITESD5 161.00 (515341) 161 kV Bus a. Apply Fault at the WHITESD5 161.00 (515341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITESD5 (515341) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 b.2. WHITESD5 (515341) 161.0 kV to OAKGROV5 (515340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on ADABELL5 161.00 (515406) 161 kV Bus a. Apply Fault at the ADABELL5 161.00 (515406) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ADABELL5 (515406) 161.0 kV to NALCOTP5 (515348) 161.0 kV Transmission Circuit #1 b.2. ADABELL5 (515406) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on NoARK 5 161.00 (515354) 161 kV Bus a. Apply Fault at the NoARK 5 161.00 (515354) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NoARK 5 (515354) 161.0 kV to GLCARBN (515353) 161.0 kV Transmission Circuit #1 b.2. NoARK 5 (515354) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRKSVL2 (505511) 69.0 kV to CLARKSV5 (505514) 161.0 kV to CLK X1 1 (505513) 12.5 kV Three Winding #1 b.2. CLRKSVL2 (505511) 69.0 kV to CLARKSV5 (505514) 161.0 kV to CLK X2 1 (505515) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply Fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LSPADRA5 (515319) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 b.2. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG5 (515327) 161.0 kV to FITZHUGH 5 (503902) 161.0 kV Transmission Circuit #1 b.2. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on VBI 5 161.00 (515339) 161 kV Bus a. Apply Fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI 5 (515339) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 b.2. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on VAN BUR5 (505522) 161 kV Bus a. Apply Fault at the VAN BUR5 (505522) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAN BUR5 (505522) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CLARKSV5 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on OZARK H5 (505516) 161 kV Bus a. Apply Fault at the OZARK H5 (505516) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OZARK H5 (505516) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HELBERG5 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG5 (515327) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on NITROTP5 (515329) 161 kV Bus a. Apply Fault at the NITROTP5 (515329) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NITROTP5 (515329) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NoRAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. 4. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), O.K.U.-7 (511456), GEN-2018-015 (762460), and G18-015-TAP (762467) rise above 1.2 pu threshold. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #2 | P4 | Yes | Yes | No | Yes | No | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. 4. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), O.K.U.-7 (511456), GEN-2018-015 (762460), and G18-015-TAP (762467) above 1.2 pu. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNoR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNoR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNoR 5 (512700) 161.0 kV to WAGNoR 2 (512697) 69.0 kV to WAGNoR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply Fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.3. J1519 POI (45194) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply Fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to 7ADNA (345015) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 8EL DORADO% 500.00 (337561) 500 kV Bus a. Apply Fault at the 8EL DORADO% 500.00 (337561) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. 8EL DORADO% (337561) 500.0 kV to 7EL DORADO (337562) 345.0 kV to 1EL DORADO2 (337565) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. 4. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), O.K.U.-7 (511456), GEN-2018-015 (762460), and G18-015-TAP (762467) rise above the 1.2 p.u. threshold. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NoVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NoVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NoVUS_WND 1 (523107) 4.2 kV to NoVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NoVUS1 1 (523109) 34.5 kV to NoVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NoVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NoVUS1_TR1 1 (523110) 13.8 kV to NoVUS1 7 (523112) 345.0 kV to NoVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NoVUS1 3 (523111) 115.0 kV to NoVUS1 7 (523112) 345.0 kV to NoVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANo% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FLINTCR5 161.00 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 161.00 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to TONTITN5 (506957) 161.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to GENTRY 5 (504201) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.2. LONGWD 4 (508808) 138.0 kV to LIEBERM4 (508806) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMTHW5 (515301) 161.0 kV to ARKOMA 5 (515306) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.2. FTSMITH7 (515302) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply Fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GEN-2018-050345.00 (762845) 345 kV Bus a. Apply Fault at the GEN-2018-050345.00 (762845) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-050 (762845) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-050 (762845) 345.0 kV to G18-050-XFM1 (762846) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on G22-176-TAP 345.00 (770500) 345 kV Bus a. Apply Fault at the G22-176-TAP 345.00 (770500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-176-TAP (770500) 345.0 kV to DELWARE7 (510380) 345.0 kV Transmission Circuit #1 b.2. G22-176-TAP (770500) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GEN-2017-033345.00 (588760) 345 kV Bus a. Apply Fault at the GEN-2017-033345.00 (588760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-033 (588760) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-033 (588760) 345.0 kV to G17-033XFMR2 (588765) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on G18-015-TAP 345.00 (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP 345.00 (762467) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-015-TAP (762467) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. G18-015-TAP (762467) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 14 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. There has been no observable impact from the CQ request under study to this issue. 2. Post fault steady state voltages at O.K.U.-7 (511456), OKLAUN HVDC (511565), GEN-2017-033 (588760) buses rise above the 1.1 p.u. threshold. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | No | No | Yes | Yes | 1. Post fault steady state voltages at G17-151-TAP (762216), GEN-2017-151 (762217), O.K.U.-7 (511456), OKLAUN HVDC (511565), GEN-2017-033 (588760), GEN-2018-015 (762460), and G18-015-TAP (762467) buses rise above the 1.2 p.u. threshold. This issue is also observed in base case and is not impacted by the CQ unit. 2. Post fault steady state voltages at BORDER 7 (515458) remains below 0.9 pu threshold. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANo% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_SWPA_FAULT_001 | Single Phase Fault with Stuck Breaker on Stigler (301550) 161 kV Bus a. Apply Fault at the Stigler (301550) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. EUFAULA5 (505570) 161.0 kV to 5STIGLER (301550) 161.0 kV Transmission Circuit #1 b.2. RS KERR5 (505582) 161.0 kV to 5STIGLER (301550) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25S | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on VBI 5 (515339) 161 kV Bus a. Apply Fault at the VBI 5 (515339) 161 kV Bus b. After 23.52 cycles trip VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 c. After 2.1 cycles trip OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 d. After 1.2 cycles trip MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 e. After 1.5 cycles trip HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 f. After 3.9 cycles trip BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 g. After 11.3 cycles close VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 h. After 2.1 cycles close OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 i. After 1.2 cycles close MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 j. After 1.5 cycles close HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 k. After 3.9 cycles close BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 l. After 1.6 cycles trip ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 m. After 9.2 cycles trip TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 n. After 4.0 cycles trip trip VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 o. After 4.2 cycles trip OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 p. After 2.4 cycles trip MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 q. After 0.2 cycles close ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 r. After 2.8 cycles trip HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 s. After 6.4 cycles close TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 t. After 1.4 cycles trip BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 u. After 19.4 cycles trip VBI 5 (515339) 161.0 kV to VBI 2 (515336) 69.0 kV to VBI 1 (515769) 13.8 kV Three Winding #2 v. After 23.8 cycles trip ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 w. Clear Fault after 18.4 cycles and trip the following elements: w.1. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 w.2. HWY59 5 (504191) 161.0 kV to Load #A1 w.3. GRANDPR5 (504192) 161.0 kV to Load #A1 w.4. SIMMONS5 (515332) 161.0 kV to Load #1 w.5. SIMMONS5 (515332) 161.0 kV to Load #A1 w.6. DYER 5 (515333) 161.0 kV to Load #A1 w.7. ALMA 5 (515334) 161.0 kV to Load #1 w.8. RUDY 5 (515337) 161.0 kV to Load #A1 w.9. OAKGROV5 (515340) 161.0 kV to Load #A1 w.10. WHITESD5 (515341) 161.0 kV to Load #1 w.11. PUDDIN 5 (515346) 161.0 kV to Load #A1 w.12. NITROUS5 (515350) 161.0 kV to Load #1 w.13. GERBER 5 (515351) 161.0 kV to Load #1 w.14. TWNBRDG5 (515360) 161.0 kV to Load #1 w.15. ADABELL5 (515406) 161.0 kV to Load #1 w.16. HWY59 5 (504191) 161.0 kV to remove bus # w.17. GRANDPR5 (504192) 161.0 kV to remove bus # w.18. GERBRTP5 (515326) 161.0 kV to remove bus # w.19. NITROTP5 (515329) 161.0 kV to remove bus # w.20. SIMMONS5 (515332) 161.0 kV to remove bus # w.21. DYER 5 (515333) 161.0 kV to remove bus # w.22. ALMA 5 (515334) 161.0 kV to remove bus # w.23. RUDY 5 (515337) 161.0 kV to remove bus # w.24. OAKGROV5 (515340) 161.0 kV to remove bus # w.25. WHITESD5 (515341) 161.0 kV to remove bus # w.26. PUDDIN 5 (515346) 161.0 kV to remove bus # w.27. NALCOTP5 (515348) 161.0 kV to remove bus # w.28. NITROUS5 (515350) 161.0 kV to remove bus # w.29. GERBER 5 (515351) 161.0 kV to remove bus # w.30. TWNBRDG5 (515360) 161.0 kV to remove bus # w.31. ADABELL5 (515406) 161.0 kV to remove bus # w.32. GRNDPRT5 (515524) 161.0 kV to remove bus # w.33. HWY59TP5 (515527) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on MAGZREC5 161.00 (507195) 161 kV Bus a. Apply fault at the MAGZREC5 161.00 (507195) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DANVLE AR! (337902) 161.0 kV to MAGZREC5 (507195) 161.0 kV Transmission Circuit #1 b.2. NMAGZIN5 (507190) 161.0 kV to MAGZREC5 (507195) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on FITZHUGH 5 161.00 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 161.00 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 (503902) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on DARDANE5 161.00 (505508) 161 kV Bus a. Apply fault at the DARDANE5 161.00 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on OZARK H5 161.00 (505516) 161 kV Bus a. Apply fault at the OZARK H5 161.00 (505516) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 (505516) 161.0 kV to VAN BUR5 (505522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on NMAGZIN5 161.00 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 161.00 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 (507190) 161.0 kV to WBOONVL5 (507192) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on NMAGZIN5 161.00 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 161.00 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 (507190) 161.0 kV to BRANCH 5 (515316) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on DARDANE5 161.00 (505508) 161 kV Bus a. Apply fault at the DARDANE5 161.00 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit #1 b.2. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.3. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit #1 b.4. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on FITZHUGH 5 161.00 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 161.00 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on FIG_FIVE 2 69.000 (504185) 69 kV Bus a. Apply fault at the FIG_FIVE 2 69.000 (504185) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI_N 2 (504032) 69.0 kV to FIG_FIVE 2 (504185) 69.0 kV Transmission Circuit #1 b.2. FIG_FIVE 2 (504185) 69.0 kV to CEDARTP2 (506967) 69.0 kV Transmission Circuit #1 b.3. GREENLD2 (506936) 69.0 kV to STRICKR2 (506974) 69.0 kV Transmission Circuit #1 b.4. CEDARTP2 (506967) 69.0 kV to STRICKR2 (506974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on BOONVIL2 69.000 (507183) 69 kV Bus a. Apply fault at the BOONVIL2 69.000 (507183) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONVIL2 (507183) 69.0 kV to BRANCH 2 (515313) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on VBI_N 2 69.000 (504032) 69 kV Bus a. Apply fault at the VBI_N 2 69.000 (504032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI_N 2 (504032) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on BOONEVIL 2 69.000 (504172) 69 kV Bus a. Apply fault at the BOONEVIL 2 69.000 (504172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONEVIL 2 (504172) 69.0 kV to BOONVIL2 (507183) 69.0 kV Transmission Circuit #1 b.2. BOONEVIL 2 (504172) 69.0 kV to WBOONVL2 (507198) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on BRIGSKM 5 161.00 (513044) 161 kV Bus a. Apply fault at the BRIGSKM 5 161.00 (513044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BRIGGS (300767) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 b.2. TAHLQH 5 (512655) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 b.3. STIWEL5 (512704) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on 5CDRCRST 161.00 (301344) 161 kV Bus a. Apply fault at the 5CDRCRST 161.00 (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on 5PARK 161.00 (301307) 161 kV Bus a. Apply fault at the 5PARK 161.00 (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK (301307) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on 7CLANS 5 161.00 (515956) 161 kV Bus a. Apply fault at the 7CLANS 5 161.00 (515956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 (512655) 161.0 kV to 7CLANS 5 (515956) 161.0 kV Transmission Circuit #1 b.2. MUSKOGE5 (515222) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 b.3. 7CLANS 5 (515956) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on SUNSTCN5 161.00 (515254) 161 kV Bus a. Apply fault at the SUNSTCN5 161.00 (515254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 (505582) 161.0 kV to SUNSTCN5 (515254) 161.0 kV Transmission Circuit #1 b.2. SUNSTCN5 (515254) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.3. SUNSTCN5 (515254) 161.0 kV to SUNSTCR5 (521124) 161.0 kV Transmission Circuit #z1 b.4. TARBY 5 (515264) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.5. SHAD-PT5 (515265) 161.0 kV to SHADYPT5 (521062) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on QUANXTP5 161.00 (515310) 161 kV Bus a. Apply fault at the QUANXTP5 161.00 (515310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 (515300) 161.0 kV to QUANXTP5 (515310) 161.0 kV Transmission Circuit #1 b.2. QUANXTP5 (515310) 161.0 kV to BARLING5 (515311) 161.0 kV Transmission Circuit #1 b.3. QUANXTP5 (515310) 161.0 kV to QUANEXS5 (515474) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on CARNALL2 69.000 (515287) 69 kV Bus a. Apply fault at the CARNALL2 69.000 (515287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNALL2 (515287) 69.0 kV to MASSARD2 (515342) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on PARKVU 2 69.000 (515288) 69 kV Bus a. Apply fault at the PARKVU 2 69.000 (515288) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKVU 2 (515288) 69.0 kV to BELLAVE2 (515290) 69.0 kV Transmission Circuit #1 b.2. PARKVU 2 (515288) 69.0 kV to MASSARD2 (515342) 69.0 kV Transmission Circuit #1 b.3. BELLAVE2 (515290) 69.0 kV to 3RDST 2 (515307) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on VBAVEC 2 69.000 (515298) 69 kV Bus a. Apply fault at the VBAVEC 2 69.000 (515298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBAVEC 2 (515298) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on CHAFXING-TP5161.00 (504189) 161 kV Bus a. Apply fault at the CHAFXING-TP5161.00 (504189) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAFFEEXING5 (504187) 161.0 kV to CHAFXING-TP5 (504189) 161.0 kV Transmission Circuit #1 b.2. CHAFXING-TP5 (504189) 161.0 kV to RYEHILL5 (504190) 161.0 kV Transmission Circuit #1 b.3. CHAFXING-TP5 (504189) 161.0 kV to MCSTLTP5 (515876) 161.0 kV Transmission Circuit #1 b.4. FTSMTHE5 (515300) 161.0 kV to COLONY 5 (515345) 161.0 kV Transmission Circuit #1 b.5. MASSARD5 (515343) 161.0 kV to RYHLLTP5 (515523) 161.0 kV Transmission Circuit #1 b.6. COLONY 5 (515345) 161.0 kV to BATTLEF5 (515349) 161.0 kV Transmission Circuit #1 b.7. BATTLEF5 (515349) 161.0 kV to RYHLLTP5 (515523) 161.0 kV Transmission Circuit #1 b.8. RYHLLTP5 (515523) 161.0 kV to MCSTLTP5 (515876) 161.0 kV Transmission Circuit #1 b.9. MCSTL2 5 (515874) 161.0 kV to MCSTLTP5 (515876) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on BARLING5 161.00 (515311) 161 kV Bus a. Apply fault at the BARLING5 161.00 (515311) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 (515311) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on NITROTP5 161.00 (515329) 161 kV Bus a. Apply fault at the NITROTP5 161.00 (515329) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.2. NITROTP5 (515329) 161.0 kV to SIMMONS5 (515332) 161.0 kV Transmission Circuit #1 b.3. NITROTP5 (515329) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.4. NITROTP5 (515329) 161.0 kV to NITROUS5 (515350) 161.0 kV Transmission Circuit #1 b.5. SIMMONS5 (515332) 161.0 kV to DYER 5 (515333) 161.0 kV Transmission Circuit #1 b.6. DYER 5 (515333) 161.0 kV to ALMA 5 (515334) 161.0 kV Transmission Circuit #1 b.7. ALMA 5 (515334) 161.0 kV to RUDY 5 (515337) 161.0 kV Transmission Circuit #1 b.8. RUDY 5 (515337) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 b.9. VBI 5 (515339) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on ROLANTP2 69.000 (515277) 69 kV Bus a. Apply fault at the ROLANTP2 69.000 (515277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 b.2. ROLANTP2 (515277) 69.0 kV to KLGORE 2 (515335) 69.0 kV Transmission Circuit #1 b.3. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on OAKGROV5 161.00 (515340) 161 kV Bus a. Apply fault at the OAKGROV5 161.00 (515340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 (515339) 161.0 kV to OAKGROV5 (515340) 161.0 kV Transmission Circuit #1 b.2. OAKGROV5 (515340) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 b.3. WHITESD5 (515341) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SUBIACT5 161.00 (515440) 161 kV Bus a. Apply fault at the SUBIACT5 161.00 (515440) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 5 (515316) 161.0 kV to SHORTMT5 (515358) 161.0 kV Transmission Circuit #1 b.2. IGO 5 (515355) 161.0 kV to RAZRBAK5 (515357) 161.0 kV Transmission Circuit #1 b.3. RAZRBAK5 (515357) 161.0 kV to SUBIACT5 (515440) 161.0 kV Transmission Circuit #1 b.4. SHORTMT5 (515358) 161.0 kV to SUBIACT5 (515440) 161.0 kV Transmission Circuit #1 b.5. SUBIACT5 (515440) 161.0 kV to SUBIACO5 (515441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on ALTUS 161.00 (515352) 161 kV Bus a. Apply fault at the ALTUS 161.00 (515352) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 (503902) 161.0 kV to ALTUS (515352) 161.0 kV Transmission Circuit #1 b.2. ALTUS (515352) 161.0 kV to GLCARBN (515353) 161.0 kV Transmission Circuit #1 b.3. GLCARBN (515353) 161.0 kV to NoARK 5 (515354) 161.0 kV Transmission Circuit #1 b.4. NoARK 5 (515354) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on GRNDPRT5 161.00 (515524) 161 kV Bus a. Apply fault at the GRNDPRT5 161.00 (515524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 (504192) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.2. BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.3. VBI 5 (515339) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on HWY59TP5 161.00 (515527) 161 kV Bus a. Apply fault at the HWY59TP5 161.00 (515527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 (504191) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.2. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.3. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on COALHIL2 69.000 (515322) 69 kV Bus a. Apply fault at the COALHIL2 69.000 (515322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 (515320) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 b.2. COALHIL2 (515322) 69.0 kV to AVECOZK2 (515324) 69.0 kV Transmission Circuit #1 b.3. AVECOZK2 (515324) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on PENDER 2 69.000 (515317) 69 kV Bus a. Apply fault at the PENDER 2 69.000 (515317) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 2 (515313) 69.0 kV to PENDER 2 (515317) 69.0 kV Transmission Circuit #1 b.2. PENDER 2 (515317) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on JONSON 5 161.00 (515293) 161 kV Bus a. Apply fault at the JONSON 5 161.00 (515293) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 (515293) 161.0 kV to OAKPARK5 (515315) 161.0 kV Transmission Circuit #1 b.2. JONSON 5 (515293) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on HELBERG5 161.00 (515327) 161 kV Bus a. Apply fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on VBI 2 69.000 (515336) 69 kV Bus a. Apply fault at the VBI 2 69.000 (515336) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 (515336) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on BRANCH 2 69.000 (515313) 69 kV Bus a. Apply fault at the BRANCH 2 69.000 (515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 2 (515313) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on LSPADRA2 69.000 (515320) 69 kV Bus a. Apply fault at the LSPADRA2 69.000 (515320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 (515320) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on HELBERG2 69.000 (515325) 69 kV Bus a. Apply fault at the HELBERG2 69.000 (515325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG2 (515325) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on MASSARD2 69.000 (515342) 69 kV Bus a. Apply fault at the MASSARD2 69.000 (515342) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 (515342) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on 5LIBRTY 161.00 (300869) 161 kV Bus a. Apply fault at the 5LIBRTY 161.00 (300869) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LIBRTY (300869) 161.0 kV to 5LBRTYTKM (301557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on 5STIGLER 161.00 (301550) 161 kV Bus a. Apply fault at the 5STIGLER 161.00 (301550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on 5LBRTYTKM 161.00 (301557) 161 kV Bus a. Apply fault at the 5LBRTYTKM 161.00 (301557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM (301557) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on 5AKINSKM 161.00 (301558) 161 kV Bus a. Apply fault at the 5AKINSKM 161.00 (301558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5AKINSKM (301558) 161.0 kV to AKINS E5 (505526) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on 5AKINSKM 161.00 (301558) 161 kV Bus a. Apply fault at the 5AKINSKM 161.00 (301558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5AKINSKM (301558) 161.0 kV to AKINS W5 (505528) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 (505522) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on LIBERTY5 161.00 (505524) 161 kV Bus a. Apply fault at the LIBERTY5 161.00 (505524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 (505524) 161.0 kV to AKINS E5 (505526) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on AKINS E5 161.00 (505526) 161 kV Bus a. Apply fault at the AKINS E5 161.00 (505526) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKINS E5 (505526) 161.0 kV to AKINS W5 (505528) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on AKINS W5 161.00 (505528) 161 kV Bus a. Apply fault at the AKINS W5 161.00 (505528) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKINS W5 (505528) 161.0 kV to SALISAW5 (505550) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on SALISAW5 161.00 (505550) 161 kV Bus a. Apply fault at the SALISAW5 161.00 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 (505550) 161.0 kV to GORE 5 (505552) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on VBI 5 161.00 (515339) 161 kV Bus a. Apply fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 (515339) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on NALCOTP5 161.00 (515348) 161 kV Bus a. Apply fault at the NALCOTP5 161.00 (515348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 (515348) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV to CLK X1 1 (505513) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV to CLK X2 1 (505515) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SALISAW5 161.00 (505550) 161 kV Bus a. Apply fault at the SALISAW5 161.00 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 (505550) 161.0 kV to SALSWGR2 (512652) 69.0 kV to SALTER1 (512831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on SALISAW5 161.00 (505550) 161 kV Bus a. Apply fault at the SALISAW5 161.00 (505550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALISAW5 (505550) 161.0 kV to SALSWGR2 (512652) 69.0 kV to SALTER2 (512842) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 (512655) 161.0 kV to TAHLQH 2 (512647) 69.0 kV to TAHLQH1 (512851) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 (512655) 161.0 kV to TAHLQH 2 (512647) 69.0 kV to TAHLQH2 1 (512825) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on BRANCH 5 161.00 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 161.00 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANCH 2 (515313) 69.0 kV to BRANCH 5 (515316) 161.0 kV to BRANCH21 (515708) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 (515320) 69.0 kV to LSPADRA5 (515319) 161.0 kV to LSPADR41 (515733) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on VBI 5 161.00 (515339) 161 kV Bus a. Apply fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 (515336) 69.0 kV to VBI 5 (515339) 161.0 kV to VBI 1 (515769) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on MASSARD5 161.00 (515343) 161 kV Bus a. Apply fault at the MASSARD5 161.00 (515343) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 (515342) 69.0 kV to MASSARD5 (515343) 161.0 kV to MASSARD1 (515735) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on BOONVIL2 69.000 (507183) 69 kV Bus a. Apply fault at the BOONVIL2 69.000 (507183) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONVIL2 (507183) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. There has been no observable impact from the CQ request under study to this issue. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Sustained high reactive power output following the fault is observed at the G20-020 (764511, 76514) generating site, Mvar output remains high for more than 10 seconds following the fault and the high voltage relay trips the unit at bus 764511. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips CB_WTG1 (585423). The protection was disabled with No impact to stability. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips CB_WTG1 (585423). The protection was disabled with No impact to stability. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. There has been no observable impact from the CQ request under study to this issue. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. This reduction is also required in the base case. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips CB_WTG1 (585423). The protection was disabled with No impact to stability. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. There has been no observable impact from the CQ request under study to this issue. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 5RUSSELVL.E!161.00 (337905) 161 kV Bus a. Apply Fault at the 5RUSSELVL.E!161.00 (337905) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RUSSELVL.IN (337862) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit #1 b.2. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit #1 b.3. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.4. 5RUSSELVL.E! (337905) 161.0 kV to 5RUSSELVL.E_ (337916) 161.0 kV Transmission Circuit #r1 b.5. 5RUSSELVL.E! (337905) 161.0 kV to 5RUSSELVL.E_ (337916) 161.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on DARDANE5 161.00 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 161.00 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.4. DARDANE5 (505508) 161.0 kV to DAR1&2 1 (505510) 13.8 kV Two Winding #1 b.5. DARDANE5 (505508) 161.0 kV to DAR3&4 1 (505512) 13.8 kV Two Winding #1 b.6. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on OZARK H5 161.00 (505516) 161 kV Bus a. Apply Fault at the OZARK H5 161.00 (505516) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.3. OZARK H5 (505516) 161.0 kV to OZK1&2 1 (505518) 13.8 kV Two Winding #1 b.4. OZARK H5 (505516) 161.0 kV to OZK345 1 (505520) 13.8 kV Two Winding #1 b.5. OZARK H5 (505516) 161.0 kV to VAN BUR5 (505522) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.2. CLK X1 1 (505513) 12.5 kV to CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 b.2. CLK X2 1 (505515) 12.5 kV to CLARKSV5 (505514) 161.0 kV to CLRKSVL2 (505511) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RS KERR5 161.00 (505582) 161 kV Bus a. Apply Fault at the RS KERR5 161.00 (505582) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STIGLER (300877) 69.0 kV to 5STIGLER (301550) 161.0 kV Two Winding #1 b.2. 5STIGLER (301550) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 b.3. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.4. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.5. RS KERR5 (505582) 161.0 kV to RSK1&2 1 (505584) 13.8 kV Two Winding #1 b.6. RS KERR5 (505582) 161.0 kV to RSK3&4 1 (505586) 13.8 kV Two Winding #1 b.7. RS KERR5 (505582) 161.0 kV to SUNSTCN5 (515254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RS KERR5 161.00 (505582) 161 kV Bus a. Apply Fault at the RS KERR5 161.00 (505582) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.2. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.3. RS KERR5 (505582) 161.0 kV to RSK1&2 1 (505584) 13.8 kV Two Winding #1 b.4. RS KERR5 (505582) 161.0 kV to RSK3&4 1 (505586) 13.8 kV Two Winding #1 b.5. RS KERR5 (505582) 161.0 kV to SUNSTCN5 (515254) 161.0 kV Transmission Circuit #1 b.6. SUNSTCN5 (515254) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.7. SUNSTCN5 (515254) 161.0 kV to SUNSTCR5 (521124) 161.0 kV Transmission Circuit #z1 b.8. TARBY 5 (515264) 161.0 kV to SHAD-PT5 (515265) 161.0 kV Transmission Circuit #1 b.9. SHAD-PT5 (515265) 161.0 kV to SHADYPT5 (521062) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply Fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HWY59 5 (504191) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.2. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.3. TAHLQH 5 (512655) 161.0 kV to 7CLANS 5 (515956) 161.0 kV Transmission Circuit #1 b.4. MUSKOGE5 (515222) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 b.5. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.6. 7CLANS 5 (515956) 161.0 kV to KETOWAH5 (516027) 161.0 kV Transmission Circuit #1 b.7. TAHLQH 2 (512647) 69.0 kV to TAHLQH 5 (512655) 161.0 kV to TAHLQH1 (512851) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on IGO 5 161.00 (515355) 161 kV Bus a. Apply Fault at the IGO 5 161.00 (515355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 b.2. NoARK 5 (515354) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 b.3. IGO 5 (515355) 161.0 kV to RAZRBAK5 (515357) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on VBI 2 69.000 (515336) 69 kV Bus a. Apply Fault at the VBI 2 69.000 (515336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI_N 2 (504032) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.2. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.3. VBI 2 (515336) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on VBI 2 69.000 (515336) 69 kV Bus a. Apply Fault at the VBI 2 69.000 (515336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBAVEC 2 (515298) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.2. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.3. VBI 2 (515336) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on 5QUITMAN! 161.00 (337926) 161 kV Bus a. Apply Fault at the 5QUITMAN! 161.00 (337926) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5QUITMAN! (337926) 161.0 kV to 5HEBER.S (338112) 161.0 kV Transmission Circuit #1 b.2. 5QUITMAN! (337926) 161.0 kV to 5BEE BRANCH# (338831) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to 5MARSHALL# (338517) 161.0 kV Transmission Circuit #1 b.4. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.5. 5HEBER.N# (338758) 161.0 kV to GREERSF5 (505422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on 5HILLTOP% 161.00 (338110) 161 kV Bus a. Apply Fault at the 5HILLTOP% 161.00 (338110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HILLTOP% (338110) 161.0 kV to 5MARSHALL# (338517) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.3. 5CLINTON.W# (338832) 161.0 kV to 5BOTKINBURG# (338834) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on 5DANVLE AR! 161.00 (337902) 161 kV Bus a. Apply Fault at the 5DANVLE AR! 161.00 (337902) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit #1 b.2. 5DANVLE AR! (337902) 161.0 kV to MAGZREC5 (507195) 161.0 kV Transmission Circuit #1 b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.4. 3DANVLE AR (337901) 115.0 kV to 5DANVLE AR! (337902) 161.0 kV to 1DANVLE AR (337944) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on 5HILLTOP% 161.00 (338110) 161 kV Bus a. Apply Fault at the 5HILLTOP% 161.00 (338110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on VAN BUR5 161.00 (505522) 161 kV Bus a. Apply Fault at the VAN BUR5 161.00 (505522) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LBRTYTKM (301557) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #z1 b.2. OZARK H5 (505516) 161.0 kV to VAN BUR5 (505522) 161.0 kV Transmission Circuit #1 b.3. VAN BUR5 (505522) 161.0 kV to LIBERTY5 (505524) 161.0 kV Transmission Circuit #1 b.4. VAN BUR5 (505522) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.5. VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #z1 b.6. LIBERTY5 (505524) 161.0 kV to AKINS E5 (505526) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on 5STIGLER 161.00 (301550) 161 kV Bus a. Apply Fault at the 5STIGLER 161.00 (301550) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STIGLER (300877) 69.0 kV to 5STIGLER (301550) 161.0 kV Two Winding #1 b.2. 5STIGLER (301550) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 b.3. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.4. GORE 5 (505552) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on EUFAULA5 161.00 (505570) 161 kV Bus a. Apply Fault at the EUFAULA5 161.00 (505570) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STIGLER (300877) 69.0 kV to 5STIGLER (301550) 161.0 kV Two Winding #1 b.2. 5STIGLER (301550) 161.0 kV to EUFAULA5 (505570) 161.0 kV Transmission Circuit #1 b.3. 5STIGLER (301550) 161.0 kV to RS KERR5 (505582) 161.0 kV Transmission Circuit #1 b.4. EUF #1 1 (505576) 13.8 kV to EUFAULA5 (505570) 161.0 kV to EUFAULA4 (505574) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on TAHLQH 5 161.00 (512655) 161 kV Bus a. Apply Fault at the TAHLQH 5 161.00 (512655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PARK (301307) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 b.2. 5CDRCRST (301344) 161.0 kV to TAHLQH 5 (512655) 161.0 kV Transmission Circuit #1 b.3. TAHLQH 5 (512655) 161.0 kV to BRIGSKM 5 (513044) 161.0 kV Transmission Circuit #1 b.4. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.5. TAHLQH 5 (512655) 161.0 kV to 7CLANS 5 (515956) 161.0 kV Transmission Circuit #1 b.6. TAHLQH 2 (512647) 69.0 kV to TAHLQH 5 (512655) 161.0 kV to TAHLQH2 1 (512825) 13.8 kV Three Winding #2 b.7. TAHLQH 2 (512647) 69.0 kV to TAHLQH 5 (512655) 161.0 kV to TAHLQH1 (512851) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BRANCH 5 161.00 (515316) 161 kV Bus a. Apply Fault at the BRANCH 5 161.00 (515316) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOONVIL2 (507183) 69.0 kV to BRANCH 2 (515313) 69.0 kV Transmission Circuit #1 b.2. NMAGZIN5 (507190) 161.0 kV to BRANCH 5 (515316) 161.0 kV Transmission Circuit #1 b.3. BRANCH 2 (515313) 69.0 kV to PENDER 2 (515317) 69.0 kV Transmission Circuit #1 b.4. BRANCH 5 (515316) 161.0 kV to SHORTMT5 (515358) 161.0 kV Transmission Circuit #1 b.5. BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.6. BRANCH 5 (515316) 161.0 kV to GEN-2017-231 (760221) 161.0 kV Transmission Circuit #1 b.7. BRANCH 5 (515316) 161.0 kV to GEN-2021-033 (765610) 161.0 kV Transmission Circuit #1 b.8. BRANCH 2 (515313) 69.0 kV to BRANCH 5 (515316) 161.0 kV to BRANCH21 (515708) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.2. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. PENDER 2 (515317) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 b.3. AVECOZK2 (515324) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 b.4. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.5. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LSPADRA2 69.000 (515320) 69 kV Bus a. Apply Fault at the LSPADRA2 69.000 (515320) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 b.2. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 b.3. LSPADRA2 (515320) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 b.4. LSPADRA5 (515319) 161.0 kV to LSPADRA2 (515320) 69.0 kV to LSPADR41 (515733) 13.8 kV Three Winding #1 b.6. LSPADRA2 (515320) 69.0 kV to LSPADR21 (515779) 34.5 kV to LSPADR31 (515780) 2.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on VBI 5 161.00 (515339) 161 kV Bus a. Apply Fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI_N 2 (504032) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.2. VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #z1 b.3. VBAVEC 2 (515298) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.4. KLGORE 2 (515335) 69.0 kV to VBI 2 (515336) 69.0 kV Transmission Circuit #1 b.5. VBI 5 (515339) 161.0 kV to OAKGROV5 (515340) 161.0 kV Transmission Circuit #1 b.6. VBI 5 (515339) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 b.7. VBI 5 (515339) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 b.8. VBI 5 (515339) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 b.9. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 b.10. VBI 2 (515336) 69.0 kV to VBI 5 (515339) 161.0 kV to VBI 1 (515769) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FITZHUGH 5 161.00 (503902) 161 kV Bus a. Apply Fault at the FITZHUGH 5 161.00 (503902) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FITZHUGH 5 (503902) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. FITZHUGH 5 (503902) 161.0 kV to OZARK H5 (505516) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on COALHIL2 69.000 (515322) 69 kV Bus a. Apply Fault at the COALHIL2 69.000 (515322) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COALHIL2 (515322) 69.0 kV to AVECOZK2 (515324) 69.0 kV Transmission Circuit #1 b.2. COALHIL2 (515322) 69.0 kV to LSPADRA2 (515320) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NITROTP5 161.00 (515329) 161 kV Bus a. Apply Fault at the NITROTP5 161.00 (515329) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NITROTP5 (515329) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 b.2. NITROTP5 (515329) 161.0 kV to SIMMONS5 (515332) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on SIMMONS5 161.00 (515332) 161 kV Bus a. Apply Fault at the SIMMONS5 161.00 (515332) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIMMONS5 (515332) 161.0 kV to NITROTP5 (515329) 161.0 kV Transmission Circuit #1 b.2. SIMMONS5 (515332) 161.0 kV to DYER 5 (515333) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RUDY 5 161.00 (515337) 161 kV Bus a. Apply Fault at the RUDY 5 161.00 (515337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUDY 5 (515337) 161.0 kV to ALMA 5 (515334) 161.0 kV Transmission Circuit #1 b.2. RUDY 5 (515337) 161.0 kV to TWNBRDG5 (515360) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on OAKGROV5 161.00 (515340) 161 kV Bus a. Apply Fault at the OAKGROV5 161.00 (515340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGROV5 (515340) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 b.2. OAKGROV5 (515340) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on NALCOTP5 161.00 (515348) 161 kV Bus a. Apply Fault at the NALCOTP5 161.00 (515348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NALCOTP5 (515348) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 b.2. NALCOTP5 (515348) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on ALTUS 161.00 (515352) 161 kV Bus a. Apply Fault at the ALTUS 161.00 (515352) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTUS (515352) 161.0 kV to FITZHUGH 5 (503902) 161.0 kV Transmission Circuit #1 b.2. ALTUS (515352) 161.0 kV to GLCARBN (515353) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GLCARBN 161.00 (515353) 161 kV Bus a. Apply Fault at the GLCARBN 161.00 (515353) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLCARBN (515353) 161.0 kV to ALTUS (515352) 161.0 kV Transmission Circuit #1 b.2. GLCARBN (515353) 161.0 kV to NoARK 5 (515354) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit #1 b.2. CLARKSV5 (505514) 161.0 kV to LSPADRA5 (515319) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply Fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LSPADRA2 (515320) 69.0 kV to LSPADRA5 (515319) 161.0 kV to LSPADR41 (515733) 13.8 kV Three Winding #1 b.2. LSPADRA2 (515320) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG2 (515325) 69.0 kV to HELBERG5 (515327) 161.0 kV to HELBERG1 (515730) 13.2 kV Three Winding #1 b.2. HELBERG2 (515325) 69.0 kV to AVECOZK2 (515324) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on VBI 5 161.00 (515339) 161 kV Bus a. Apply Fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI 2 (515336) 69.0 kV to VBI 5 (515339) 161.0 kV to VBI 1 (515769) 13.8 kV Three Winding #1 b.2. VBI 2 (515336) 69.0 kV to VBI_N 2 (504032) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRNDPRT5 161.00 (515524) 161 kV Bus a. Apply Fault at the GRNDPRT5 161.00 (515524) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDPRT5 (515524) 161.0 kV to BRANCH 5 (515316) 161.0 kV Transmission Circuit #1 b.2. GRNDPRT5 (515524) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on AVECOZK2 69.000 (515324) 69 kV Bus a. Apply Fault at the AVECOZK2 69.000 (515324) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVECOZK2 (515324) 69.0 kV to HELBERG2 (515325) 69.0 kV Transmission Circuit #1 b.2. AVECOZK2 (515324) 69.0 kV to COALHIL2 (515322) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on PUDDIN 5 161.00 (515346) 161 kV Bus a. Apply Fault at the PUDDIN 5 161.00 (515346) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUDDIN 5 (515346) 161.0 kV to HELBERG5 (515327) 161.0 kV Transmission Circuit #1 b.2. PUDDIN 5 (515346) 161.0 kV to NITROTP5 (515329) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on DYER 5 161.00 (515333) 161 kV Bus a. Apply Fault at the DYER 5 161.00 (515333) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DYER 5 (515333) 161.0 kV to SIMMONS5 (515332) 161.0 kV Transmission Circuit #1 b.2. DYER 5 (515333) 161.0 kV to ALMA 5 (515334) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on TWNBRDG5 161.00 (515360) 161 kV Bus a. Apply Fault at the TWNBRDG5 161.00 (515360) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWNBRDG5 (515360) 161.0 kV to RUDY 5 (515337) 161.0 kV Transmission Circuit #1 b.2. TWNBRDG5 (515360) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WHITESD5 161.00 (515341) 161 kV Bus a. Apply Fault at the WHITESD5 161.00 (515341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITESD5 (515341) 161.0 kV to MASSARD5 (515343) 161.0 kV Transmission Circuit #1 b.2. WHITESD5 (515341) 161.0 kV to OAKGROV5 (515340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on ADABELL5 161.00 (515406) 161 kV Bus a. Apply Fault at the ADABELL5 161.00 (515406) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ADABELL5 (515406) 161.0 kV to NALCOTP5 (515348) 161.0 kV Transmission Circuit #1 b.2. ADABELL5 (515406) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on NoARK 5 161.00 (515354) 161 kV Bus a. Apply Fault at the NoARK 5 161.00 (515354) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NoARK 5 (515354) 161.0 kV to GLCARBN (515353) 161.0 kV Transmission Circuit #1 b.2. NoARK 5 (515354) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CLARKSV5 161.00 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 161.00 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRKSVL2 (505511) 69.0 kV to CLARKSV5 (505514) 161.0 kV to CLK X1 1 (505513) 12.5 kV Three Winding #1 b.2. CLRKSVL2 (505511) 69.0 kV to CLARKSV5 (505514) 161.0 kV to CLK X2 1 (505515) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on LSPADRA5 161.00 (515319) 161 kV Bus a. Apply Fault at the LSPADRA5 161.00 (515319) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LSPADRA5 (515319) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit #1 b.2. LSPADRA5 (515319) 161.0 kV to IGO 5 (515355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HELBERG5 161.00 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 161.00 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG5 (515327) 161.0 kV to FITZHUGH 5 (503902) 161.0 kV Transmission Circuit #1 b.2. HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on VBI 5 161.00 (515339) 161 kV Bus a. Apply Fault at the VBI 5 161.00 (515339) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VBI 5 (515339) 161.0 kV to ADABELL5 (515406) 161.0 kV Transmission Circuit #1 b.2. VBI 5 (515339) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on VAN BUR5 (505522) 161 kV Bus a. Apply Fault at the VAN BUR5 (505522) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAN BUR5 (505522) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CLARKSV5 (505514) 161 kV Bus a. Apply Fault at the CLARKSV5 (505514) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV5 (505514) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on OZARK H5 (505516) 161 kV Bus a. Apply Fault at the OZARK H5 (505516) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OZARK H5 (505516) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HELBERG5 (515327) 161 kV Bus a. Apply Fault at the HELBERG5 (515327) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HELBERG5 (515327) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on NITROTP5 (515329) 161 kV Bus a. Apply Fault at the NITROTP5 (515329) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NITROTP5 (515329) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NoRAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNoR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNoR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNoR 5 (512700) 161.0 kV to WAGNoR 2 (512697) 69.0 kV to WAGNoR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply Fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.3. J1519 POI (45194) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply Fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to 7ADNA (345015) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 8EL DORADO% 500.00 (337561) 500 kV Bus a. Apply Fault at the 8EL DORADO% 500.00 (337561) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. 8EL DORADO% (337561) 500.0 kV to 7EL DORADO (337562) 345.0 kV to 1EL DORADO2 (337565) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NoVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NoVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NoVUS_WND 1 (523107) 4.2 kV to NoVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NoVUS1 1 (523109) 34.5 kV to NoVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NoVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NoVUS1_TR1 1 (523110) 13.8 kV to NoVUS1 7 (523112) 345.0 kV to NoVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NoVUS1 3 (523111) 115.0 kV to NoVUS1 7 (523112) 345.0 kV to NoVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANo% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FLINTCR5 161.00 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 161.00 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to TONTITN5 (506957) 161.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to GENTRY 5 (504201) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.2. LONGWD 4 (508808) 138.0 kV to LIEBERM4 (508806) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMTHW5 (515301) 161.0 kV to ARKOMA 5 (515306) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.2. FTSMITH7 (515302) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply Fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on GEN-2018-050345.00 (762845) 345 kV Bus a. Apply Fault at the GEN-2018-050345.00 (762845) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-050 (762845) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-050 (762845) 345.0 kV to G18-050-XFM1 (762846) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on G22-176-TAP 345.00 (770500) 345 kV Bus a. Apply Fault at the G22-176-TAP 345.00 (770500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-176-TAP (770500) 345.0 kV to DELWARE7 (510380) 345.0 kV Transmission Circuit #1 b.2. G22-176-TAP (770500) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GEN-2017-033345.00 (588760) 345 kV Bus a. Apply Fault at the GEN-2017-033345.00 (588760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-033 (588760) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-033 (588760) 345.0 kV to G17-033XFMR2 (588765) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on G18-015-TAP 345.00 (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP 345.00 (762467) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-015-TAP (762467) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. G18-015-TAP (762467) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | Steady state voltages following the fault at G17-151-TAP (762216), GEN-2017-151 (762217), O.K.U.-7 (511456), OKLAUN HVDC (511565), GEN-2017-033 (588760), GEN-2018-015 (762460), and G18-015-TAP (762467) buses rise above the 1.1 p.u. threshold. This issue is also observed in PQ case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANo% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_SWPA_FAULT_001 | Single Phase Fault with Stuck Breaker on Stigler (301550) 161 kV Bus a. Apply Fault at the Stigler (301550) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. EUFAULA5 (505570) 161.0 kV to 5STIGLER (301550) 161.0 kV Transmission Circuit #1 b.2. RS KERR5 (505582) 161.0 kV to 5STIGLER (301550) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | 2025 Annual Interim | 25W | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on VBI 5 (515339) 161 kV Bus a. Apply Fault at the VBI 5 (515339) 161 kV Bus b. After 23.52 cycles trip VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 c. After 2.1 cycles trip OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 d. After 1.2 cycles trip MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 e. After 1.5 cycles trip HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 f. After 3.9 cycles trip BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 g. After 11.3 cycles close VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 h. After 2.1 cycles close OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 i. After 1.2 cycles close MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 j. After 1.5 cycles close HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 k. After 3.9 cycles close BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 l. After 1.6 cycles trip ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 m. After 9.2 cycles trip TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 n. After 4.0 cycles trip trip VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 o. After 4.2 cycles trip OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 p. After 2.4 cycles trip MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 q. After 0.2 cycles close ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 r. After 2.8 cycles trip HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 s. After 6.4 cycles close TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 t. After 1.4 cycles trip BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 u. After 19.4 cycles trip VBI 5 (515339) 161.0 kV to VBI 2 (515336) 69.0 kV to VBI 1 (515769) 13.8 kV Three Winding #2 v. After 23.8 cycles trip ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 w. Clear Fault after 18.4 cycles and trip the following elements: w.1. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 w.2. HWY59 5 (504191) 161.0 kV to Load #A1 w.3. GRANDPR5 (504192) 161.0 kV to Load #A1 w.4. SIMMONS5 (515332) 161.0 kV to Load #1 w.5. SIMMONS5 (515332) 161.0 kV to Load #A1 w.6. DYER 5 (515333) 161.0 kV to Load #A1 w.7. ALMA 5 (515334) 161.0 kV to Load #1 w.8. RUDY 5 (515337) 161.0 kV to Load #A1 w.9. OAKGROV5 (515340) 161.0 kV to Load #A1 w.10. WHITESD5 (515341) 161.0 kV to Load #1 w.11. PUDDIN 5 (515346) 161.0 kV to Load #A1 w.12. NITROUS5 (515350) 161.0 kV to Load #1 w.13. GERBER 5 (515351) 161.0 kV to Load #1 w.14. TWNBRDG5 (515360) 161.0 kV to Load #1 w.15. ADABELL5 (515406) 161.0 kV to Load #1 w.16. HWY59 5 (504191) 161.0 kV to remove bus # w.17. GRANDPR5 (504192) 161.0 kV to remove bus # w.18. GERBRTP5 (515326) 161.0 kV to remove bus # w.19. NITROTP5 (515329) 161.0 kV to remove bus # w.20. SIMMONS5 (515332) 161.0 kV to remove bus # w.21. DYER 5 (515333) 161.0 kV to remove bus # w.22. ALMA 5 (515334) 161.0 kV to remove bus # w.23. RUDY 5 (515337) 161.0 kV to remove bus # w.24. OAKGROV5 (515340) 161.0 kV to remove bus # w.25. WHITESD5 (515341) 161.0 kV to remove bus # w.26. PUDDIN 5 (515346) 161.0 kV to remove bus # w.27. NALCOTP5 (515348) 161.0 kV to remove bus # w.28. NITROUS5 (515350) 161.0 kV to remove bus # w.29. GERBER 5 (515351) 161.0 kV to remove bus # w.30. TWNBRDG5 (515360) 161.0 kV to remove bus # w.31. ADABELL5 (515406) 161.0 kV to remove bus # w.32. GRNDPRT5 (515524) 161.0 kV to remove bus # w.33. HWY59TP5 (515527) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage oscillations observed following the fault at VBI 5 161 kV (515339). Voltage recovers above 0.9 pu at 11.3 seconds. This issue is also observed in base case and is not impacted by the CQ unit. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | No | Yes | 1. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC ( 511565), O.K.U.-7 (511456) rise above 1.2 pu threshold. 3. Post fault steady state voltages at GEN-2018-015 (762460), and G18-015-TAP (762467) rise above 1.1 pu threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Sustained high reactive power output following the fault is observed at the G20-020 (764511, 76514) generating site, Mvar output remains high for more than 10 seconds following the fault and the high voltage relay trips the unit at bus 764511. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587953) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | No | No | Yes | 1. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. 3. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), and O.K.U.-7 (511456) rise above 1.2pu threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Post fault steady state voltages at GEN-2018-015 (762460) and G18-015-TAP (762467) remain below 0.9 pu threshold. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 1.5 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. 4. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), O.K.U.-7 (511456), GEN-2018-015 (762460), and G18-015-TAP (762467) rise above 1.2 pu threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #2 | P4 | Yes | Yes | No | Yes | No | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. 4. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), O.K.U.-7 (511456), GEN-2018-015 (762460), and G18-015-TAP (762467) above 1.2 pu. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. 4. Post fault steady state voltages at GEN-2017-033 (588760), OKLAUN HVDC (511565), O.K.U.-7 (511456), GEN-2018-015 (762460), and G18-015-TAP (762467) rise above the 1.2 p.u. threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on G18-015-TAP 345.00 (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP 345.00 (762467) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-015-TAP (762467) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. G18-015-TAP (762467) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 14 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. 2. Post fault steady state voltages at O.K.U.-7 (511456), OKLAUN HVDC (511565), GEN-2017-033 (588760) buses rise above the 1.1 p.u. threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25S | Base | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | No | No | Yes | Yes | 1. Post fault steady state voltages at G17-151-TAP (762216), GEN-2017-151 (762217), O.K.U.-7 (511456), OKLAUN HVDC (511565), GEN-2017-033 (588760), GEN-2018-015 (762460), and G18-015-TAP (762467) buses rise above the 1.2 p.u. threshold. 2. Post fault steady state voltages at BORDER 7 (515458) remains below 0.9 pu threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Sustained high reactive power output following the fault is observed at the G20-020 (764511, 76514) generating site, Mvar output remains high for more than 10 seconds following the fault and the high voltage relay trips the unit at bus 764511. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 3 cycles resolves the issue. 2. No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. . | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips CB_WTG1 (585423). The protection was disabled with No impact to stability. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips CB_WTG1 (585423). The protection was disabled with No impact to stability. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 2 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | 1. Simulation crashes post fault due to Non-convergence. 2. Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | 1. Decreasing the clearing time from 6 cycles to 1.5 cycles resolves the issue. 2. No mitigation required
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-119 (587958 and 587953), G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | 1. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. This is followed by a large power jump resulting in power recovery starting at 18 seconds. This issue has been observed in both base and transfer cases as well as the original DISIS study attributed to the modelling of this request. 2. Power oscillations observed following the fault at the G16-097 (587793), G16-095 (587773), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | 1. Power oscillations observed following the fault at the G16-097 (587793), BLUCAN2 (599003, 920001, 920002, 920003 and 920004), G17-027 (588713, 588714, 588715 and 588716) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. 2. Voltage protection trips G16-095 (587773). The protection was disabled with no impact to stability. 3. Issues observed in the real power output G18-115 machines 1 and 2 (763321, 763324) where cessation of power is observed after 3 seconds following fault clearance. The power does not recover for the remaining simulation time, there is No indication recorded in the log file that these machines tripped. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-095 (587773) and nearby generating sites. The disabling of the mechanical dynamic models of this unit allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed following the fault at the G16-119 (587958 and 587953) and nearby generating sites. The disabling of the mechanical dynamic models of these units allowed the simulation to complete without any stability issues being observed. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | Steady state voltages following the fault at G17-151-TAP (762216), GEN-2017-151 (762217), O.K.U.-7 (511456), OKLAUN HVDC (511565), GEN-2017-033 (588760), GEN-2018-015 (762460), and G18-015-TAP (762467) buses rise above the 1.1 p.u. threshold. | No mitigation required.
04 SOUTHEAST | 2025 Annual Interim | 25W | Base | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on VBI 5 (515339) 161 kV Bus a. Apply Fault at the VBI 5 (515339) 161 kV Bus b. After 23.52 cycles trip VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 c. After 2.1 cycles trip OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 d. After 1.2 cycles trip MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 e. After 1.5 cycles trip HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 f. After 3.9 cycles trip BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 g. After 11.3 cycles close VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 h. After 2.1 cycles close OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 i. After 1.2 cycles close MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 j. After 1.5 cycles close HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 k. After 3.9 cycles close BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 l. After 1.6 cycles trip ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 m. After 9.2 cycles trip TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 n. After 4.0 cycles trip trip VAN BUR5 (505522) 161.0 kV to VBI 5 (515339) 161.0 kV Transmission Circuit #Z1 o. After 4.2 cycles trip OAKPARK5 (515315) 161.0 kV to GERBRTP5 (515326) 161.0 kV Transmission Circuit #1 p. After 2.4 cycles trip MASSARD5 (515343) 161.0 kV to WHITESD5 (515341) 161.0 kV Transmission Circuit #1 q. After 0.2 cycles close ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 r. After 2.8 cycles trip HELBERG5 (515327) 161.0 kV to PUDDIN 5 (515346) 161.0 kV Transmission Circuit #1 s. After 6.4 cycles close TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 t. After 1.4 cycles trip BRANCH 5 (515316) 161.0 kV to GRNDPRT5 (515524) 161.0 kV Transmission Circuit #1 u. After 19.4 cycles trip VBI 5 (515339) 161.0 kV to VBI 2 (515336) 69.0 kV to VBI 1 (515769) 13.8 kV Three Winding #2 v. After 23.8 cycles trip ROLANRD2 (515257) 69.0 kV to ROLANTP2 (515277) 69.0 kV Transmission Circuit #1 w. Clear Fault after 18.4 cycles and trip the following elements: w.1. TAHLQH 5 (512655) 161.0 kV to HWY59TP5 (515527) 161.0 kV Transmission Circuit #1 w.2. HWY59 5 (504191) 161.0 kV to Load #A1 w.3. GRANDPR5 (504192) 161.0 kV to Load #A1 w.4. SIMMONS5 (515332) 161.0 kV to Load #1 w.5. SIMMONS5 (515332) 161.0 kV to Load #A1 w.6. DYER 5 (515333) 161.0 kV to Load #A1 w.7. ALMA 5 (515334) 161.0 kV to Load #1 w.8. RUDY 5 (515337) 161.0 kV to Load #A1 w.9. OAKGROV5 (515340) 161.0 kV to Load #A1 w.10. WHITESD5 (515341) 161.0 kV to Load #1 w.11. PUDDIN 5 (515346) 161.0 kV to Load #A1 w.12. NITROUS5 (515350) 161.0 kV to Load #1 w.13. GERBER 5 (515351) 161.0 kV to Load #1 w.14. TWNBRDG5 (515360) 161.0 kV to Load #1 w.15. ADABELL5 (515406) 161.0 kV to Load #1 w.16. HWY59 5 (504191) 161.0 kV to remove bus # w.17. GRANDPR5 (504192) 161.0 kV to remove bus # w.18. GERBRTP5 (515326) 161.0 kV to remove bus # w.19. NITROTP5 (515329) 161.0 kV to remove bus # w.20. SIMMONS5 (515332) 161.0 kV to remove bus # w.21. DYER 5 (515333) 161.0 kV to remove bus # w.22. ALMA 5 (515334) 161.0 kV to remove bus # w.23. RUDY 5 (515337) 161.0 kV to remove bus # w.24. OAKGROV5 (515340) 161.0 kV to remove bus # w.25. WHITESD5 (515341) 161.0 kV to remove bus # w.26. PUDDIN 5 (515346) 161.0 kV to remove bus # w.27. NALCOTP5 (515348) 161.0 kV to remove bus # w.28. NITROUS5 (515350) 161.0 kV to remove bus # w.29. GERBER 5 (515351) 161.0 kV to remove bus # w.30. TWNBRDG5 (515360) 161.0 kV to remove bus # w.31. ADABELL5 (515406) 161.0 kV to remove bus # w.32. GRNDPRT5 (515524) 161.0 kV to remove bus # w.33. HWY59TP5 (515527) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage oscillations observed following the fault at VBI 5 161 kV (515339). Voltage recovers above 0.9 pu at 11.3 seconds. | No mitigation required.

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
ASGI-2024-001 | 03 CENTRAL | 50313 | J2031 SUB | 161 | 9.3289 | 9.3292 | 0.0003
ASGI-2024-001 | 03 CENTRAL | 627026 | M-TOWN K1 7 | 115 | 13.1733 | 13.174 | 0.0007
ASGI-2024-001 | 03 CENTRAL | 630339 | GRNDYCN8 | 69 | 5.8173 | 5.8186 | 0.0013
ASGI-2024-001 | 03 CENTRAL | 630341 | IAFINDP8 | 69 | 9.511 | 9.6657 | 0.1547
ASGI-2024-001 | 03 CENTRAL | 630357 | COULTR 8 | 69 | 3.2156 | 3.2167 | 0.0011
ASGI-2024-001 | 03 CENTRAL | 630859 | ALDNBUCKEYE8 | 69 | 5.0132 | 5.0396 | 0.0264
ASGI-2024-001 | 03 CENTRAL | 630862 | WELSBRGDIST8 | 69 | 6.9295 | 6.932 | 0.0025
ASGI-2024-001 | 03 CENTRAL | 630929 | FLETCHR J1 8 | 69 | 9.3227 | 9.3233 | 0.0006
ASGI-2024-001 | 03 CENTRAL | 630977 | FLETCHR J2 8 | 69 | 9.303 | 9.3036 | 0.0006
ASGI-2024-001 | 03 CENTRAL | 631000 | ABBOTT 5 | 161 | 12.6651 | 12.6659 | 0.0008
ASGI-2024-001 | 03 CENTRAL | 631001 | TOLEDO 5 | 161 | 9.3289 | 9.3292 | 0.0003
ASGI-2024-001 | 03 CENTRAL | 631004 | M-TOWN K2 7 | 115 | 13.1733 | 13.174 | 0.0007
ASGI-2024-001 | 03 CENTRAL | 631008 | WELSBRG5 | 161 | 9.8014 | 9.809 | 0.0076
ASGI-2024-001 | 03 CENTRAL | 631029 | IAFINDP5 | 161 | 11.9546 | 11.9859 | 0.0313
ASGI-2024-001 | 03 CENTRAL | 631048 | EMERY 5 | 161 | 28.332 | 28.3374 | 0.0054
ASGI-2024-001 | 03 CENTRAL | 631081 | M-TOWN 5 | 161 | 25.1087 | 25.1124 | 0.0037
ASGI-2024-001 | 03 CENTRAL | 631082 | TIMBRCK5 | 161 | 13.5496 | 13.5507 | 0.0011
ASGI-2024-001 | 03 CENTRAL | 631166 | NUTHTCH5 | 161 | 14.4414 | 14.4713 | 0.0299
ASGI-2024-001 | 03 CENTRAL | 631171 | WHISWIL5 | 161 | 11.6175 | 11.6305 | 0.013
ASGI-2024-001 | 03 CENTRAL | 631186 | LAUREL_5 | 161 | 14.2974 | 14.2981 | 0.0007
ASGI-2024-001 | 03 CENTRAL | 631225 | WHISWILLW E5 | 161 | 10.938 | 10.9493 | 0.0113
ASGI-2024-001 | 03 CENTRAL | 636217 | MEC WELSBRG5 | 161 | 9.7897 | 9.7972 | 0.0075
ASGI-2024-001 | 03 CENTRAL | 636229 | ACKLEY 5 | 161 | 8.4543 | 8.4598 | 0.0055
ASGI-2024-001 | 03 CENTRAL | 636230 | FRANKLN5 | 161 | 14.6917 | 14.7196 | 0.0279
ASGI-2024-001 | 03 CENTRAL | 636235 | WALL LK5 | 161 | 9.9883 | 9.9953 | 0.007
ASGI-2024-001 | 03 CENTRAL | 636249 | DUMONT 8 | 69 | 3.8025 | 3.8037 | 0.0012
ASGI-2024-001 | 03 CENTRAL | 636315 | HAMPTNW8 | 69 | 6.8346 | 6.8426 | 0.008
ASGI-2024-001 | 03 CENTRAL | 636316 | SHEFFLD8 | 69 | 5.5047 | 5.5082 | 0.0035
ASGI-2024-001 | 03 CENTRAL | 636317 | LATIMER8 | 69 | 3.567 | 3.5685 | 0.0015
ASGI-2024-001 | 03 CENTRAL | 636318 | WB LATM 8 | 69 | 3.3948 | 3.3961 | 0.0013
ASGI-2024-001 | 03 CENTRAL | 636319 | ACKLEY 8 | 69 | 3.1591 | 3.2751 | 0.116
ASGI-2024-001 | 03 CENTRAL | 656007 | BEAVERCK8 | 69 | 5.3728 | 5.3745 | 0.0017
ASGI-2024-001 | 03 CENTRAL | 656011 | BRISTOW8 | 69 | 4.2672 | 4.2679 | 0.0007
ASGI-2024-001 | 03 CENTRAL | 656021 | DUMONT8 | 69 | 5.5226 | 5.5252 | 0.0026
ASGI-2024-001 | 03 CENTRAL | 656035 | KESLEY8 | 69 | 5.5289 | 5.5307 | 0.0018
ASGI-2024-001 | 03 CENTRAL | 656049 | NEAL8 | 69 | 4.3767 | 4.3773 | 0.0006
ASGI-2024-001 | 03 CENTRAL | 656065 | PRKSBRG8 | 69 | 6.3649 | 6.3673 | 0.0024
ASGI-2024-001 | 03 CENTRAL | 656179 | ALEXANDR8 | 69 | 5.8282 | 5.8302 | 0.002
ASGI-2024-001 | 03 CENTRAL | 656181 | DOWS8 | 69 | 5.467 | 5.4709 | 0.0039
ASGI-2024-001 | 03 CENTRAL | 656183 | ESHEFFLD8 | 69 | 2.9833 | 2.9841 | 0.0008
ASGI-2024-001 | 03 CENTRAL | 656185 | ESHEFFTP8 | 69 | 8.7282 | 8.7354 | 0.0072
ASGI-2024-001 | 03 CENTRAL | 656187 | GENEVA8 | 69 | 5.62 | 5.6244 | 0.0044
ASGI-2024-001 | 03 CENTRAL | 656189 | GLCOATNG8 | 69 | 9.0798 | 9.0972 | 0.0174
ASGI-2024-001 | 03 CENTRAL | 656191 | HAMPTON5 | 161 | 8.7106 | 8.7215 | 0.0109
ASGI-2024-001 | 03 CENTRAL | 656193 | HAMPTON8 | 69 | 11.9356 | 11.9706 | 0.035
ASGI-2024-001 | 03 CENTRAL | 656199 | MECSHDFT8 | 69 | 6.4695 | 6.4735 | 0.004
ASGI-2024-001 | 03 CENTRAL | 656201 | SHEFFLD5 | 161 | 10.7933 | 10.8015 | 0.0082
ASGI-2024-001 | 03 CENTRAL | 656203 | SWALEDAL8 | 69 | 4.3204 | 4.3222 | 0.0018
ASGI-2024-001 | 03 CENTRAL | 656205 | WSHEFFLD8 | 69 | 9.9584 | 9.9665 | 0.0081
ASGI-2024-001 | 03 CENTRAL | 656207 | HAMPTONTAP5 | 161 | 10.8974 | 10.9123 | 0.0149
ASGI-2024-001 | 03 CENTRAL | 656209 | HAMILTONT8 | 69 | 8.0577 | 8.0715 | 0.0138
ASGI-2024-001 | 03 CENTRAL | 656211 | HAMILTON8 | 69 | 6.2758 | 6.2842 | 0.0084
ASGI-2024-001 | 03 CENTRAL | 656269 | APLGTNJC8 | 69 | 5.5179 | 5.5196 | 0.0017
ASGI-2024-001 | 03 CENTRAL | 656271 | APLNGTON8 | 69 | 5.6883 | 5.6901 | 0.0018
ASGI-2024-001 | 03 CENTRAL | 656295 | MELROSE8 | 69 | 9.0904 | 9.0945 | 0.0041
ASGI-2024-001 | 03 CENTRAL | 656297 | MELRSTAP8 | 69 | 9.9796 | 9.9845 | 0.0049
ASGI-2024-001 | 03 CENTRAL | 656301 | WELSBRG G | 69 | 11.7739 | 11.781 | 0.0071
ASGI-2024-001 | 03 CENTRAL | 656309 | WELBRGEASTT8 | 69 | 7.8497 | 7.853 | 0.0033
ASGI-2024-001 | 03 CENTRAL | 656749 | ACKLEY8 | 69 | 5.0302 | 5.1875 | 0.1573
ASGI-2024-001 | 03 CENTRAL | 656751 | ACKLYTAP8 | 69 | 3.6856 | 3.8418 | 0.1562
ASGI-2024-001 | 03 CENTRAL | 656753 | ALDEN8 | 69 | 7.3958 | 7.4636 | 0.0678
ASGI-2024-001 | 03 CENTRAL | 656755 | ALDENJCT8 | 69 | 7.2605 | 7.2851 | 0.0246
ASGI-2024-001 | 03 CENTRAL | 656761 | ELDORA8 | 69 | 7.759 | 7.7644 | 0.0054
ASGI-2024-001 | 03 CENTRAL | 656769 | FARM_TAP8 | 69 | 9.3132 | 9.4727 | 0.1595
ASGI-2024-001 | 03 CENTRAL | 656771 | FARMLAND8 | 69 | 8.5346 | 8.6937 | 0.1591
ASGI-2024-001 | 03 CENTRAL | 656775 | IFE8 | 69 | 8.4231 | 8.5311 | 0.108
ASGI-2024-001 | 03 CENTRAL | 656779 | PINELAKE8 | 69 | 2.6993 | 2.8565 | 0.1572
ASGI-2024-001 | 03 CENTRAL | 656795 | ALDNRRLTP8 | 69 | 7.0078 | 7.0595 | 0.0517
ASGI-2024-001 | 03 CENTRAL | 656859 | GALT8 | 69 | 6.7156 | 6.7187 | 0.0031
GEN-2024-003 | 04 SOUTHEAST | 300863 | 2GARLDTP | 69 | 3.3451 | 3.346 | 0.0009
GEN-2024-003 | 04 SOUTHEAST | 300865 | 2KEOTA | 69 | 2.3937 | 2.3942 | 0.0005
GEN-2024-003 | 04 SOUTHEAST | 300866 | 2KEOTATP | 69 | 5.1362 | 5.1383 | 0.0021
GEN-2024-003 | 04 SOUTHEAST | 300869 | 5LIBRTY | 161 | 8.4237 | 8.4816 | 0.0579
GEN-2024-003 | 04 SOUTHEAST | 300876 | 2STIGDST | 69 | 4.9642 | 4.9661 | 0.0019
GEN-2024-003 | 04 SOUTHEAST | 300877 | 2STIGLER | 69 | 5.8156 | 5.8183 | 0.0027
GEN-2024-003 | 04 SOUTHEAST | 301307 | 5PARK | 161 | 9.5633 | 9.5721 | 0.0088
GEN-2024-003 | 04 SOUTHEAST | 301550 | 5STIGLER | 161 | 6.9354 | 6.9466 | 0.0112
GEN-2024-003 | 04 SOUTHEAST | 301557 | 5LBRTYTKM | 161 | 9.0244 | 9.091 | 0.0666
GEN-2024-003 | 04 SOUTHEAST | 301558 | 5AKINSKM | 161 | 7.9043 | 7.9396 | 0.0353
GEN-2024-003 | 04 SOUTHEAST | 337862 | 5RUSSELVL.IN | 161 | 8.0233 | 8.0666 | 0.0433
GEN-2024-003 | 04 SOUTHEAST | 337902 | 5DANVLE AR! | 161 | 7.0156 | 7.0695 | 0.0539
GEN-2024-003 | 04 SOUTHEAST | 337903 | 5DARDANELLE | 161 | 9.1789 | 9.2603 | 0.0814
GEN-2024-003 | 04 SOUTHEAST | 337904 | 5RUSSELVL.S | 161 | 9.242 | 9.313 | 0.071
GEN-2024-003 | 04 SOUTHEAST | 337905 | 5RUSSELVL.E! | 161 | 8.7382 | 8.7896 | 0.0514
GEN-2024-003 | 04 SOUTHEAST | 337907 | 5ATKINS | 161 | 6.135 | 6.1603 | 0.0253
GEN-2024-003 | 04 SOUTHEAST | 338108 | 5ST JOE | 161 | 7.9428 | 7.9458 | 0.003
GEN-2024-003 | 04 SOUTHEAST | 338110 | 5HILLTOP% | 161 | 8.5502 | 8.5542 | 0.004
GEN-2024-003 | 04 SOUTHEAST | 338517 | 5MARSHALL# | 161 | 7.2659 | 7.2684 | 0.0025
GEN-2024-003 | 04 SOUTHEAST | 503902 | FITZHUGH 5 | 161 | 11.4148 | 12.8757 | 1.4609
GEN-2024-003 | 04 SOUTHEAST | 503908 | ELLIS 2 | 69 | 4.2336 | 4.2375 | 0.0039
GEN-2024-003 | 04 SOUTHEAST | 504032 | VBI_N 2 | 69 | 11.5685 | 11.6145 | 0.046
GEN-2024-003 | 04 SOUTHEAST | 504191 | HWY59 5 | 161 | 16.2534 | 16.5749 | 0.3215
GEN-2024-003 | 04 SOUTHEAST | 504192 | GRANDPR5 | 161 | 7.583 | 7.7114 | 0.1284
GEN-2024-003 | 04 SOUTHEAST | 505461 | BULL SH W5 | 161 | 8.7655 | 8.7662 | 0.0007
GEN-2024-003 | 04 SOUTHEAST | 505508 | DARDANE5 | 161 | 9.9127 | 10.0064 | 0.0937
GEN-2024-003 | 04 SOUTHEAST | 505511 | CLRKSVL2 | 69 | 6.7769 | 6.8863 | 0.1094
GEN-2024-003 | 04 SOUTHEAST | 505514 | CLARKSV5 | 161 | 7.7576 | 8.104 | 0.3464
GEN-2024-003 | 04 SOUTHEAST | 505516 | OZARK H5 | 161 | 11.1261 | 12.3939 | 1.2678
GEN-2024-003 | 04 SOUTHEAST | 505522 | VAN BUR5 | 161 | 19.057 | 19.5193 | 0.4623
GEN-2024-003 | 04 SOUTHEAST | 505524 | LIBERTY5 | 161 | 9.0461 | 9.113 | 0.0669
GEN-2024-003 | 04 SOUTHEAST | 505526 | AKINS E5 | 161 | 7.9126 | 7.948 | 0.0354
GEN-2024-003 | 04 SOUTHEAST | 505528 | AKINS W5 | 161 | 7.9126 | 7.948 | 0.0354
GEN-2024-003 | 04 SOUTHEAST | 505570 | EUFAULA5 | 161 | 8.1947 | 8.2047 | 0.01
GEN-2024-003 | 04 SOUTHEAST | 505582 | RS KERR5 | 161 | 9.2457 | 9.2807 | 0.035
GEN-2024-003 | 04 SOUTHEAST | 507183 | BOONVIL2 | 69 | 5.6413 | 5.6684 | 0.0271
GEN-2024-003 | 04 SOUTHEAST | 512655 | TAHLQH 5 | 161 | 10.7624 | 10.7735 | 0.0111
GEN-2024-003 | 04 SOUTHEAST | 515254 | SUNSTCN5 | 161 | 8.2825 | 8.3078 | 0.0253
GEN-2024-003 | 04 SOUTHEAST | 515265 | SHAD-PT5 | 161 | 9.6121 | 9.64 | 0.0279
GEN-2024-003 | 04 SOUTHEAST | 515298 | VBAVEC 2 | 69 | 9.3378 | 9.368 | 0.0302
GEN-2024-003 | 04 SOUTHEAST | 515313 | BRANCH 2 | 69 | 8.0172 | 8.1056 | 0.0884
GEN-2024-003 | 04 SOUTHEAST | 515316 | BRANCH 5 | 161 | 8.3502 | 8.5195 | 0.1693
GEN-2024-003 | 04 SOUTHEAST | 515317 | PENDER 2 | 69 | 6.8084 | 6.9061 | 0.0977
GEN-2024-003 | 04 SOUTHEAST | 515319 | LSPADRA5 | 161 | 7.6822 | 8.0456 | 0.3634
GEN-2024-003 | 04 SOUTHEAST | 515320 | LSPADRA2 | 69 | 7.7273 | 7.8839 | 0.1566
GEN-2024-003 | 04 SOUTHEAST | 515322 | COALHIL2 | 69 | 6.1781 | 6.2835 | 0.1054
GEN-2024-003 | 04 SOUTHEAST | 515324 | AVECOZK2 | 69 | 9.1996 | 9.4393 | 0.2397
GEN-2024-003 | 04 SOUTHEAST | 515325 | HELBERG2 | 69 | 9.8579 | 10.1338 | 0.2759
GEN-2024-003 | 04 SOUTHEAST | 515327 | HELBERG5 | 161 | 9.8409 | 10.6897 | 0.8488
GEN-2024-003 | 04 SOUTHEAST | 515329 | NITROTP5 | 161 | 8.8328 | 9.1518 | 0.319
GEN-2024-003 | 04 SOUTHEAST | 515332 | SIMMONS5 | 161 | 9.3546 | 9.6512 | 0.2966
GEN-2024-003 | 04 SOUTHEAST | 515333 | DYER 5 | 161 | 9.9559 | 10.2457 | 0.2898
GEN-2024-003 | 04 SOUTHEAST | 515335 | KLGORE 2 | 69 | 7.4109 | 7.4286 | 0.0177
GEN-2024-003 | 04 SOUTHEAST | 515336 | VBI 2 | 69 | 11.646 | 11.6929 | 0.0469
GEN-2024-003 | 04 SOUTHEAST | 515337 | RUDY 5 | 161 | 11.7056 | 12.0067 | 0.3011
GEN-2024-003 | 04 SOUTHEAST | 515339 | VBI 5 | 161 | 19.2839 | 19.7547 | 0.4708
GEN-2024-003 | 04 SOUTHEAST | 515340 | OAKGROV5 | 161 | 16.1169 | 16.3838 | 0.2669
GEN-2024-003 | 04 SOUTHEAST | 515341 | WHITESD5 | 161 | 15.994 | 16.2493 | 0.2553
GEN-2024-003 | 04 SOUTHEAST | 515346 | PUDDIN 5 | 161 | 9.4435 | 10.1738 | 0.7303
GEN-2024-003 | 04 SOUTHEAST | 515348 | NALCOTP5 | 161 | 17.0786 | 17.3429 | 0.2643
GEN-2024-003 | 04 SOUTHEAST | 515350 | NITROUS5 | 161 | 8.3635 | 8.6491 | 0.2856
GEN-2024-003 | 04 SOUTHEAST | 515352 | ALTUS | 161 | 10.1762 | 11.2499 | 1.0737
GEN-2024-003 | 04 SOUTHEAST | 515353 | GLCARBN | 161 | 9.4581 | 10.3291 | 0.871
GEN-2024-003 | 04 SOUTHEAST | 515354 | NOARK 5 | 161 | 8.992 | 9.7372 | 0.7452
GEN-2024-003 | 04 SOUTHEAST | 515355 | IGO 5 | 161 | 8.2813 | 8.7368 | 0.4555
GEN-2024-003 | 04 SOUTHEAST | 515357 | RAZRBAK5 | 161 | 6.7882 | 7.0244 | 0.2362
GEN-2024-003 | 04 SOUTHEAST | 515360 | TWNBRDG5 | 161 | 13.8792 | 14.2167 | 0.3375
GEN-2024-003 | 04 SOUTHEAST | 515406 | ADABELL5 | 161 | 17.2937 | 17.6146 | 0.3209
GEN-2024-003 | 04 SOUTHEAST | 515524 | GRNDPRT5 | 161 | 7.7766 | 7.9117 | 0.1351
GEN-2024-003 | 04 SOUTHEAST | 515527 | HWY59TP5 | 161 | 16.4589 | 16.7887 | 0.3298
GEN-2024-003 | 04 SOUTHEAST | 521062 | SHADYPT5 | 161 | 9.6121 | 9.64 | 0.0279
GEN-2024-003 | 04 SOUTHEAST | 521124 | SUNSTCR5 | 161 | 8.2825 | 8.3078 | 0.0253
GEN-2024-003 | 04 SOUTHEAST | 760221 | GEN-2017-231 | 161 | 8.0985 | 8.2576 | 0.1591
GEN-2024-003 | 04 SOUTHEAST | 765610 | GEN-2021-033 | 161 | 8.3224 | 8.4905 | 0.1681
GEN-2024-003 | 04 SOUTHEAST | 999104 | FITZHUGH_HV | 161 | 11.0106 | 12.4783 | 1.4677