## Executive Summary
Executive Summary: ERAS-2025-001 of Power Flow and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Expedited Resource Adequacy Study (ERAS) for generation interconnection requests received during the ERAS Queue Cluster Window which closed on October 2, 2025. The primary objective of this ERAS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this ERAS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. ERAS-2025-001 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest )
DISIS Manual Version 4.4
https://spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
This ERAS analyzes the impact of interconnecting new generation for total of:
13,262.06 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $784,546,773.71 Steady State Network Upgrade $337,892,742.32 Interconnection Costs: $446,654,031.39
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
By: SPP Generator Interconnection Department
Published: 4/3/2026
Costs for Solar/Battery Requests were allocated using the 29SP (summer peak) model.
Costs for Wind Requests were allocated using the 29L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
For CQ projects sharing a generation interconnection line, the Reactive Compensation required for the line was split proportionally based on MW between all connected CQ projects.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4607100% | SPP | Draft Report
4607600% | SPP | Final Report
4609700% | SPP | Final Report Revision 1
4611500% | SPP | Final Report Revision 2

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4607600% | Requests | 3 | Requests | Updated a typo regarding fuel type for ERAS-2025-033 and update POI location typo for ERAS-2025-019
4607600% | Network Upgrades | 6,7,8,9,10 | Constraints Summary/Assigned Upgrade Costs/Upgrade Summary/Contingent Upgrades - Screening/All Thermal | Updated SPS Network Upgrade descriptions and cost estimates due to additional TO feedback.
4607600% | Network Upgrades | 1,6,7,8,9,10 | Executive Summary/Constraints Summary/Assigned Upgrade Costs/Upgrade Summary/Contingent Upgrades - Screening/All Thermal | Removed the MOORE_CNTY to MCDWL_CRK 230 kV Line Rebuild due to additional TO feedback
4607600% | Seasonal LOIS | 3,4 | Requests/Seasonal LOIS | Updated the Seasonal LOIS values and the limited elements for ERAS-2025-008, ERAS-2025-015 and ERAS-2025-017
4607600% | SCRCCT Results | 13,14,15 | SCRCCT Results/SCRCCT/WSCR | Included the SCRCCT results
4609700% | Network Upgrades | 6,7,8,11 | Constraints Summary/Assigned Upgrade Costs/Upgrade Summary/All Voltage | Per TO and customer feedback, updated the Network Upgrade at Kummer Ridge 345 kV to a capacitor bank solution.
4609700% | Network Upgrades | 6,7,8,9,10 | Constraints Summary/Assigned Upgrade Costs/Upgrade Summary/Contingent Upgrades - Screening/All Thermal | Removed Potter County to Tolk 345 kV Line as a contingent upgrade due to withdrawals in DISIS-2020-001. Updated report to reflect removal of this contingent upgrade.
4611500% | JTIQ Upgrades | 4,9,16 | Requests/Contingent Upgrades - Screening/JTIQ Participant Summary | Added the results for the JTIQ participant groups and JTIQ contingent facility screening Added JTIQ Participant Summary tab
4611500% | JTIQ Expanded Scope | 6,10 | Constraints Summary/All Thermal | Added results of the JTIQ Expanded Scope Analysis

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status | JTIQ Particpant
ERAS-2025-011 | 01 NORTH | 23 | ERAS-2025-001 | Thermal | 750 | 0 | 0 | 750 | 750 | 0 | 0 | 0 | 0 | 0 | ER/NR | BEPC | Leland Olds 345kV Substation | ERAS | Yes
ERAS-2025-012 | 01 NORTH | 23 | ERAS-2025-001 | Thermal | 750 | 0 | 0 | 750 | 750 | 0 | 0 | 0 | 0 | 0 | ER/NR | BEPC | Leland Olds 345kV Substation | ERAS | Yes
ERAS-2025-035 | 01 NORTH | 23 | ERAS-2025-001 | Thermal | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 0 | ER/NR | NWPS | Siebrecht 115 kV Substation | ERAS | Yes
ERAS-2025-001 | 02 NEBRASKA | 23 | ERAS-2025-001 | Thermal | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 0 | ER/NR | LES | 84th & Bluff 115kV Substation | ERAS | Yes
ERAS-2025-006 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 717.8 | 690 | 690 | 690 | 690 | 690 | 690 | 717.8 | 717.8 | 0 | ER/NR | WERE | Reno County 345 kV Substation #1443 | ERAS | No
ERAS-2025-007 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 450.6 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 450.6 | 450.6 | 0 | ER/NR | WERE | Mullin Creek 345 kV Substation | ERAS | Yes
ERAS-2025-008 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 721.1 | 693.2 | 638.0394 | 693.2 | 638.0394 | 693.2 | 638.0394 | 721.1 | 721.1 | 0 | ER/NR | WERE | Viola 345 kV Substation | ERAS | No
ERAS-2025-013 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 450.6 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 450.6 | 450.6 | 0 | ER/NR | WERE | Mullin Creek 345 kV Substation | ERAS | Yes
ERAS-2025-015 | 03 CENTRAL | 23 | ERAS-2025-001 | Hybrid | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | -5.5 | ER/NR | SEPC | Holcomb 345 kV Substation | ERAS | No
ERAS-2025-017 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 600 | 600 | 481.9803 | 600 | 481.9803 | 600 | 481.9803 | 600 | 600 | 0 | ER/NR | SEPC | Holcomb 345 kV Substation | ERAS | No
ERAS-2025-019 | 03 CENTRAL | 23 | ERAS-2025-001 | Solar | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0.2 | ER/NR | MIDW | Kinsley 115 kV Substation | ERAS | No
ERAS-2025-029 | 03 CENTRAL | 23 | ERAS-2025-001 | Battery/Storage | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | -0.11296 | ER/NR | KACY | Nearman 161 kV Substation | ERAS | Yes
ERAS-2025-031 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | ER/NR | KACY | Quindaro 161kV Substation | ERAS | Yes
ERAS-2025-032 | 03 CENTRAL | 23 | ERAS-2025-001 | Hybrid | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -1 | ER/NR | SEPC | St. John 115 kV Substation | ERAS | No
ERAS-2025-033 | 03 CENTRAL | 23 | ERAS-2025-001 | Battery/Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -0.6 | ER/NR | SEPC | Fort Dodge 115 kV Substation | ERAS | No
ERAS-2025-034 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 250 | 205.1928 | 78.8246 | 205.1928 | 78.8246 | 205.1928 | 78.8246 | 250 | 250 | 0 | ER/NR | EMDE | State Line 439 161 kV Substation | ERAS | Yes
ERAS-2025-003 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 0 | ER/NR | OGE | Redbud 345kV Substation | ERAS | Yes
ERAS-2025-004 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 763 | 763 | 763 | 763 | 763 | 763 | 763 | 763 | 763 | 0 | ER/NR | OGE | Horseshoe Lake 138kV Substation | ERAS | Yes
ERAS-2025-005 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Hybrid | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -0.77 | ER/NR | AEP | Danville - Magazine 161kV Line | ERAS | Yes
ERAS-2025-009 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 0 | ER/NR | GRDA | Grec #1 Interconnect 161kV Substation | ERAS | Yes
ERAS-2025-010 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 496 | 496 | 496 | 496 | 496 | 496 | 496 | 496 | 496 | 0 | ER/NR | OGE | Horseshoe Lake 138kV Substation | ERAS | Yes
ERAS-2025-022 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Battery/Storage | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | -0.1 | ER/NR | PEC | Monte Vista 138 kV Substation | ERAS | Yes
ERAS-2025-023 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 510 | 505 | 505 | 505 | 505 | 505 | 505 | 510 | 510 | 0 | ER/NR | AEP | Northeastern 345 kV Substation | ERAS | Yes
ERAS-2025-024 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 744 | 404.4588 | 542.437 | 404.4588 | 542.437 | 404.4588 | 542.437 | 744 | 744 | 0 | ER/NR | AEP | Comanche 138kV Substation | ERAS | No
ERAS-2025-025 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Solar | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | -1.34 | ER/NR | WFEC | Washita 138kV Substation | ERAS | No
ERAS-2025-002 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 217 | 0 | 208 | 0 | 208 | 0 | 208 | 217 | 217 | 0 | ER/NR | SPS | Xcel Tuco 345kV Substation | ERAS | No
ERAS-2025-014 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 159.5 | 0 | 120.5 | 0 | 120.5 | 0 | 120.5 | 159.5 | 159.5 | 0 | ER/NR | SPS | Hobbs-Andrews 345kV Line | ERAS | No
ERAS-2025-016 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 232.5 | 0 | 224.7 | 0 | 224.7 | 0 | 224.7 | 232.5 | 232.5 | 0 | ER/NR | SPS | Tolk 230kV Substation | ERAS | No
ERAS-2025-018 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Hybrid | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 256 | -8.89 | ER/NR | SPS | Oasis 230kV Substation | ERAS | No
ERAS-2025-020 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Hybrid | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.42 | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | ERAS | No
ERAS-2025-021 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Wind | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | -22.57 | ER/NR | SPS | Border-Tuco 345kV Line | ERAS | No
ERAS-2025-026 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 744 | 0 | 665 | 0 | 665 | 0 | 665 | 744 | 744 | 0 | ER/NR | AEP | Oklaunion-Lawton East Side 345kV Line | ERAS | No
ERAS-2025-027 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 250 | -0.23 | ER/NR | SPS | Mahoney 230kV Substation | ERAS | No
ERAS-2025-028 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Solar | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 384 | -5.6 | ER/NR | SPS | Tuco-Yoakum 345kV Line | ERAS | No
ERAS-2025-030 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Hybrid | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 350 | -22.18 | ER/NR | SPS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS | No
ERAS-2025-036 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Battery/Storage | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 140 | -0.27 | ER/NR | SPS | Newhart - Potter 230 kV Line | ERAS | No
GEN-2023-SR4 | 01 NORTH | 22.5 | SURPLUS | Battery/Storage | 170.02 | [9 empty] | ER | BEPC |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR1 | 02 NEBRASKA | 22.5 | SURPLUS | THERMAL | 21.9 | [9 empty] | ER/NR | NPPD |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-SR8 | 03 CENTRAL | 22.5 | SURPLUS | Solar | 42 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-SR9 | 03 CENTRAL | 22.5 | SURPLUS | Solar | 10 | [9 empty] | ER/NR | KCPL |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-SR28 | 03 CENTRAL | 22.5 | SURPLUS | Solar | 150 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-SR2 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-GR1 | 04 SOUTHEAST | 22.5 | REPLACEMENT | THERMAL | 513 | [9 empty] | ER | AEPW |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR1 | 04 SOUTHEAST | 22.5 | REPLACEMENT | THERMAL | 97.488 | [9 empty] | ER | WFEC |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR2 | 04 SOUTHEAST | 22.5 | REPLACEMENT | THERMAL | 94.242 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR13 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 70 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-SR16 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 70 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR18 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 80 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-SR5 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 85.01 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2024-SR2 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 72.774 | [9 empty] | ER/NR | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2024-SR3 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 72.766 | [9 empty] | ER/NR | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2024-SR5 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 176.9 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR3 | 05 SOUTHWEST | 22.5 | REPLACEMENT | Wind | 80 | [9 empty] | ER/NR | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 22.5 | REPLACEMENT | Solar | 72 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR5 | 05 SOUTHWEST | 22.5 | REPLACEMENT | Solar | 150 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR12 | 05 SOUTHWEST | 22.5 | SURPLUS | Battery/Storage | 120 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR8 | 05 SOUTHWEST | 22.5 | SURPLUS | Battery/Storage | 200 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR9 | 05 SOUTHWEST | 22.5 | SURPLUS | Battery/Storage | 50 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [9 empty] | ER/NR | BEPC | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | [9 empty] | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | FACILITY STUDY STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Patent Gate Substation 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [9 empty] | ER | OPPD | 6846 Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [9 empty] | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 35 | [9 empty] | ER | KCPL
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 35 | [9 empty] | ER | KCPL
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Russell 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 21 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [9 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [9 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | FACILITY STUDY STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [9 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | FACILITY STUDY STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | FACILITY STUDY STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | FACILITY STUDY STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | FACILITY STUDY STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | FACILITY STUDY STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | FACILITY STUDY STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | BEPC-SPP | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [9 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid: Storage and Wind | 110 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA PENDING
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | WITHDRAWN
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA PENDING
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA PENDING
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA PENDING
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA PENDING
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA PENDING
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 400 | [9 empty] | ER/NR | OTP
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 40 | [9 empty] | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-106 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 350.08 | [9 empty] | ER/NR | AECI
GIA-107 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 250 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | BEPC-SPP | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [9 empty] | ER | WERE | Neosho 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [9 empty] | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | Done
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | Done
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | Done
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | Done
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Done
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | Done
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | Done
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Done
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Done
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Done
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | Done
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | Done
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Done
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Done
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | Done
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | Done
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | Done
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 120 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | Done
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Pipestone to Split Rock 115kV | Done
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Done
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Done
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | [9 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Done
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | [9 empty] | ER/NR | DPC | Barron 161 kV | Done
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL | Adams 345kV Substation | Done
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 170 | [9 empty] | ER | OTP
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 130 | [9 empty] | ER | OTP
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | [9 empty] | ER/NR | OTP
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | [9 empty] | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 300 | [9 empty] | ER/NR | OTP
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Done
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW | Traer 161-kV Substation | Done
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Done
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | Done
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Done
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Done
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Done
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | Done
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Done
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Done
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Done
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | [9 empty] | ER | AECI
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | Done
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | Done
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | Done
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Done
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Done
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Done
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | Done
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES | Goos Ferry | Done
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Done
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Done
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Done
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Done
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Done
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Done
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Done
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Done
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | Done
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Done
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | Done
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Done
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Done
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | Done
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Done
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | Done
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [9 empty] | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation | Done: Phase 3
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation | Done: Phase 3
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Done: Phase 3
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: Phase 3
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: Phase 3
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: Phase 3
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation | Done: Phase 3
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: Phase 3
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | WIND | 7.5 | [9 empty] | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | Done: GIA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | Done: GIA
NPPDSPRINGVIEW | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | WIND | 3 | [9 empty] | ER | NPPD
SPSLEACOUNTY | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | SOLAR | 5.5 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | WIND | 100 | [9 empty] | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | WIND | 246 | [9 empty] | ER/NR | AMMO
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC-SPP | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | [9 empty] | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 16 | [9 empty] | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 200 | [9 empty] | ER/NR | BEPC-SPP
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 34 | [9 empty] | ER/NR | BEPC-SPP
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Hybrid: Solar and Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Hybrid: Solar and Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | WIND | 11.5 | [9 empty] | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LLANOESTACADOWHITEDEER | 05 SOUTHWEST | 8 | PQ | WIND | 80 | [9 empty] | ER | SPS
SPSCARSON | 05 SOUTHWEST | 8 | PQ | WIND | 10 | [9 empty] | ER | SPS
SPSDUMAS19THST | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSETTER | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSMOOREE | 05 SOUTHWEST | 8 | PQ | WIND | 17.5 | [9 empty] | ER | SPS
SPSSHERMAN | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SUNRAY | 05 SOUTHWEST | 8 | PQ | WIND | 34.5 | [9 empty] | ER | SPS
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | WIND | 19.8 | [9 empty] | ER | SPS
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 20 | [9 empty] | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 10 | [9 empty] | ER | SPS
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | [9 empty] | ER | NPPD |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OGE | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | [9 empty] | ER | MIDW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 197.8 | [9 empty] | ER | OGE | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | [9 empty] | ER | OGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | 05 SOUTHWEST | 4 | DIS-10-1 | Thermal | 205 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 75 | [9 empty] | ER | NPPD | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 131.1 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | MKEC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.5 | [9 empty] | ER | MIDW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 3 | DIS-09-1 | Thermal | 675 | [9 empty] | ER | MIPU |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEP |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 25SP | Stability 25WP
ERAS-2025-001 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 104 | 104 | none | none | N/A | 104 | N/A | 104 | N/A | 104 | N/A | 104 | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 104 | 104 | none | none | 104 | N/A | N/A | 104 | 104 | N/A | N/A | 104 | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 104 | 104 | none | none | N/A | N/A | N/A | 104 | N/A | N/A | N/A | 104 | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 104 | 104 | none | none | N/A | N/A | N/A | 104 | N/A | N/A | N/A | 104 | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 104 | 104 | none | none | N/A | 104 | N/A | N/A | N/A | 104 | N/A | N/A | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 104 | 104 | none | none | 104 | N/A | N/A | N/A | 104 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 104 | 104 | none | none | N/A | 104 | N/A | 104 | N/A | 104 | N/A | 104 | N/A | N/A
ERAS-2025-001 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 104 | 104 | none | none | 104 | N/A | N/A | 104 | 104 | N/A | N/A | 104 | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 208 | 208 | none | none | N/A | 180.442 | N/A | 217 | N/A | 217 | N/A | 217 | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 208 | 0 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Line - Crawfish Draw - Phantom 765 kV New Line | 217 | N/A | N/A | 217 | 0 | N/A | N/A | 217 | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 217 | 217 | none | none | N/A | N/A | N/A | 217 | N/A | N/A | N/A | 217 | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 217 | 217 | none | none | N/A | N/A | N/A | 217 | N/A | N/A | N/A | 217 | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 208 | 208 | none | none | N/A | 180.442 | N/A | N/A | N/A | 217 | N/A | N/A | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 208 | 0 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Line - Crawfish Draw - Phantom 765 kV New Line | 217 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 208 | 208 | none | none | N/A | 180.442 | N/A | 217 | N/A | 217 | N/A | 217 | N/A | N/A
ERAS-2025-002 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 208 | 0 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Line - Crawfish Draw - Phantom 765 kV New Line | 217 | N/A | N/A | 217 | 0 | N/A | N/A | 217 | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 186 | 186 | none | none | N/A | 154.6645 | N/A | 186 | N/A | 186 | N/A | 186 | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 186 | 186 | none | none | 186 | N/A | N/A | 186 | 186 | N/A | N/A | 186 | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 186 | 186 | none | none | N/A | N/A | N/A | 186 | N/A | N/A | N/A | 186 | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 186 | 186 | none | none | N/A | N/A | N/A | 186 | N/A | N/A | N/A | 186 | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 186 | 186 | none | none | N/A | 154.6645 | N/A | N/A | N/A | 186 | N/A | N/A | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 186 | 186 | none | none | 186 | N/A | N/A | N/A | 186 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 186 | 186 | none | none | N/A | 154.6645 | N/A | 186 | N/A | 186 | N/A | 186 | N/A | N/A
ERAS-2025-003 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 186 | 186 | none | none | 186 | N/A | N/A | 186 | 186 | N/A | N/A | 186 | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 763 | 763 | none | none | N/A | 434.1696 | N/A | 585.5532 | N/A | 763 | N/A | 763 | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 763 | 763 | none | none | 488.0506 | N/A | N/A | 585.5532 | 763 | N/A | N/A | 763 | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 763 | 763 | none | none | N/A | N/A | N/A | 585.5532 | N/A | N/A | N/A | 763 | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 763 | 763 | none | none | N/A | N/A | N/A | 585.5532 | N/A | N/A | N/A | 763 | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 763 | 763 | none | none | N/A | 434.1696 | N/A | N/A | N/A | 763 | N/A | N/A | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 763 | 763 | none | none | 488.0506 | N/A | N/A | N/A | 763 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 763 | 763 | none | none | N/A | 434.1696 | N/A | 585.5532 | N/A | 763 | N/A | 763 | N/A | N/A
ERAS-2025-004 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 763 | 763 | none | none | 488.0506 | N/A | N/A | 585.5532 | 763 | N/A | N/A | 763 | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Long Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Near Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | N/A | N/A
ERAS-2025-005 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 690 | 690 | none | none | N/A | 717.8 | N/A | 717.8 | N/A | 635.1195 | N/A | 717.8 | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 690 | 690 | none | none | 717.8 | N/A | N/A | 717.8 | 635.9438 | N/A | N/A | 717.8 | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 717.8 | 717.8 | none | none | N/A | N/A | N/A | 717.8 | N/A | N/A | N/A | 717.8 | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 717.8 | 717.8 | none | none | N/A | N/A | N/A | 717.8 | N/A | N/A | N/A | 717.8 | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 690 | 690 | none | none | N/A | 717.8 | N/A | N/A | N/A | 635.1195 | N/A | N/A | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 690 | 690 | none | none | 717.8 | N/A | N/A | N/A | 635.9438 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 690 | 690 | none | none | N/A | 717.8 | N/A | 717.8 | N/A | 635.1195 | N/A | 717.8 | N/A | N/A
ERAS-2025-006 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 690 | 690 | none | none | 717.8 | N/A | N/A | 717.8 | 635.9438 | N/A | N/A | 717.8 | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 425.1 | 425.1 | none | none | N/A | 450.6 | N/A | 450.6 | N/A | 280.7766 | N/A | 450.6 | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 425.1 | 425.1 | none | none | 450.6 | N/A | N/A | 450.6 | 362.4699 | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 450.6 | 450.6 | none | none | N/A | N/A | N/A | 450.6 | N/A | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 450.6 | 450.6 | none | none | N/A | N/A | N/A | 450.6 | N/A | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 425.1 | 425.1 | none | none | N/A | 450.6 | N/A | N/A | N/A | 280.7766 | N/A | N/A | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 425.1 | 425.1 | none | none | 450.6 | N/A | N/A | N/A | 362.4699 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 425.1 | 425.1 | none | none | N/A | 450.6 | N/A | 450.6 | N/A | 280.7766 | N/A | 450.6 | N/A | N/A
ERAS-2025-007 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 425.1 | 425.1 | none | none | 450.6 | N/A | N/A | 450.6 | 362.4699 | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 693.2 | 638.0394 | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 ftlo POI 531449_4 | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | N/A | 599.6161 | N/A | 721.1 | N/A | 638.0394 | N/A | 721.1 | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 693.2 | 693.2 | none | none | 721.1 | N/A | N/A | 721.1 | 537.9791 | N/A | N/A | 721.1 | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 721.1 | 721.1 | none | none | N/A | N/A | N/A | 721.1 | N/A | N/A | N/A | 721.1 | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 721.1 | 721.1 | none | none | N/A | N/A | N/A | 721.1 | N/A | N/A | N/A | 721.1 | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 693.2 | 638.0394 | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 ftlo POI 531449_4 | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | N/A | 599.6161 | N/A | N/A | N/A | 638.0394 | N/A | N/A | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 693.2 | 693.2 | none | none | 721.1 | N/A | N/A | N/A | 537.9791 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 693.2 | 599.6161 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 ftlo System Intact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | N/A | 599.6161 | N/A | 721.1 | N/A | 638.0394 | N/A | 721.1 | N/A | N/A
ERAS-2025-008 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 693.2 | 693.2 | none | none | 721.1 | N/A | N/A | 721.1 | 537.9791 | N/A | N/A | 721.1 | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 450 | 450 | none | none | N/A | 450 | N/A | 450 | N/A | 450 | N/A | 450 | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 450 | 450 | none | none | 450 | N/A | N/A | 450 | 450 | N/A | N/A | 450 | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 450 | 450 | none | none | N/A | N/A | N/A | 450 | N/A | N/A | N/A | 450 | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 450 | 450 | none | none | N/A | N/A | N/A | 450 | N/A | N/A | N/A | 450 | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 450 | 450 | none | none | N/A | 450 | N/A | N/A | N/A | 450 | N/A | N/A | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 450 | 450 | none | none | 450 | N/A | N/A | N/A | 450 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 450 | 450 | none | none | N/A | 450 | N/A | 450 | N/A | 450 | N/A | 450 | N/A | N/A
ERAS-2025-009 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 450 | 450 | none | none | 450 | N/A | N/A | 450 | 450 | N/A | N/A | 450 | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 496 | 496 | none | none | N/A | 319.1803 | N/A | 264.4966 | N/A | 496 | N/A | 496 | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 496 | 496 | none | none | 317.2649 | N/A | N/A | 264.4966 | 496 | N/A | N/A | 496 | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 496 | 496 | none | none | N/A | N/A | N/A | 264.4966 | N/A | N/A | N/A | 496 | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 496 | 496 | none | none | N/A | N/A | N/A | 264.4966 | N/A | N/A | N/A | 496 | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 496 | 496 | none | none | N/A | 319.1803 | N/A | N/A | N/A | 496 | N/A | N/A | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 496 | 496 | none | none | 317.2649 | N/A | N/A | N/A | 496 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 496 | 496 | none | none | N/A | 319.1803 | N/A | 264.4966 | N/A | 496 | N/A | 496 | N/A | N/A
ERAS-2025-010 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 496 | 496 | none | none | 317.2649 | N/A | N/A | 264.4966 | 496 | N/A | N/A | 496 | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | 750 | N/A | 0 | N/A | 750 | N/A | 750 | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | 750 | N/A | N/A | 0 | 555.5561 | N/A | N/A | 750 | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 750 | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 750 | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 750 | 750 | none | none | N/A | 750 | N/A | N/A | N/A | 750 | N/A | N/A | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 750 | 750 | none | none | 750 | N/A | N/A | N/A | 555.5561 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | 750 | N/A | 0 | N/A | 750 | N/A | 750 | N/A | N/A
ERAS-2025-011 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | 750 | N/A | N/A | 0 | 555.5561 | N/A | N/A | 750 | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | 750 | N/A | 0 | N/A | 555.5561 | N/A | 750 | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | 750 | N/A | N/A | 0 | 750 | N/A | N/A | 750 | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 750 | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 750 | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 750 | 750 | none | none | N/A | 750 | N/A | N/A | N/A | 555.5561 | N/A | N/A | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 750 | 750 | none | none | 750 | N/A | N/A | N/A | 750 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | N/A | 750 | N/A | 0 | N/A | 555.5561 | N/A | 750 | N/A | N/A
ERAS-2025-012 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 750 | 0 | Voltage violation due to POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank | 750 | N/A | N/A | 0 | 750 | N/A | N/A | 750 | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 425.1 | 425.1 | none | none | N/A | 450.6 | N/A | 450.6 | N/A | 280.7766 | N/A | 450.6 | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 425.1 | 425.1 | none | none | 450.6 | N/A | N/A | 450.6 | 362.4699 | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 450.6 | 450.6 | none | none | N/A | N/A | N/A | 450.6 | N/A | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 450.6 | 450.6 | none | none | N/A | N/A | N/A | 450.6 | N/A | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 425.1 | 425.1 | none | none | N/A | 450.6 | N/A | N/A | N/A | 280.7766 | N/A | N/A | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 425.1 | 425.1 | none | none | 450.6 | N/A | N/A | N/A | 362.4699 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 425.1 | 425.1 | none | none | N/A | 450.6 | N/A | 450.6 | N/A | 280.7766 | N/A | 450.6 | N/A | N/A
ERAS-2025-013 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 425.1 | 425.1 | none | none | 450.6 | N/A | N/A | 450.6 | 362.4699 | N/A | N/A | 450.6 | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 120.5 | 120.5 | none | none | N/A | 0 | N/A | 71.2298 | N/A | 120.5 | N/A | 159.5 | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 120.5 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 159.5 | N/A | N/A | 71.2298 | 0 | N/A | N/A | 159.5 | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 159.5 | 159.5 | none | none | N/A | N/A | N/A | 71.2298 | N/A | N/A | N/A | 159.5 | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 159.5 | 159.5 | none | none | N/A | N/A | N/A | 71.2298 | N/A | N/A | N/A | 159.5 | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 120.5 | 120.5 | none | none | N/A | 0 | N/A | N/A | N/A | 120.5 | N/A | N/A | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 120.5 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 159.5 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 120.5 | 120.5 | none | none | N/A | 0 | N/A | 71.2298 | N/A | 120.5 | N/A | 159.5 | N/A | N/A
ERAS-2025-014 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 120.5 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 159.5 | N/A | N/A | 71.2298 | 0 | N/A | N/A | 159.5 | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | April 1 - May 31 (Long Term) | 400 | 400 | none | none | N/A | 400 | N/A | 400 | N/A | 321.3202 | N/A | 400 | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | April 1 - May 31 (Near Term) | 400 | 400 | none | none | 400 | N/A | N/A | 400 | 0 | N/A | N/A | 400 | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Long Term) | 400 | 400 | none | none | N/A | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Near Term) | 400 | 400 | none | none | N/A | N/A | N/A | 400 | N/A | N/A | N/A | 400 | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Long Term) | 400 | 400 | none | none | N/A | 400 | N/A | N/A | N/A | 321.3202 | N/A | N/A | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Near Term) | 400 | 400 | none | none | 400 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Long Term) | 400 | 400 | none | none | N/A | 400 | N/A | 400 | N/A | 321.3202 | N/A | 400 | N/A | N/A
ERAS-2025-015 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Near Term) | 400 | 400 | none | none | 400 | N/A | N/A | 400 | 0 | N/A | N/A | 400 | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 224.7 | 224.7 | none | none | N/A | 193.3307 | N/A | 232.5 | N/A | 232.5 | N/A | 232.5 | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 224.7 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 232.5 | N/A | N/A | 232.5 | 0 | N/A | N/A | 232.5 | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 232.5 | 232.5 | none | none | N/A | N/A | N/A | 232.5 | N/A | N/A | N/A | 232.5 | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 232.5 | 232.5 | none | none | N/A | N/A | N/A | 232.5 | N/A | N/A | N/A | 232.5 | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 224.7 | 224.7 | none | none | N/A | 193.3307 | N/A | N/A | N/A | 232.5 | N/A | N/A | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 224.7 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 232.5 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 224.7 | 224.7 | none | none | N/A | 193.3307 | N/A | 232.5 | N/A | 232.5 | N/A | 232.5 | N/A | N/A
ERAS-2025-016 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 224.7 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 232.5 | N/A | N/A | 232.5 | 0 | N/A | N/A | 232.5 | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 600 | 481.9803 | 531419 DOBSON 3 115 531493 GANO 3 115 1 ftlo POI 531449_4 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | N/A | 374.3483 | N/A | 600 | N/A | 481.9803 | N/A | 600 | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 600 | 600 | none | none | 600 | N/A | N/A | 600 | 0 | N/A | N/A | 600 | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 600 | 600 | none | none | N/A | N/A | N/A | 600 | N/A | N/A | N/A | 600 | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 600 | 600 | none | none | N/A | N/A | N/A | 600 | N/A | N/A | N/A | 600 | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 600 | 481.9803 | 531419 DOBSON 3 115 531493 GANO 3 115 1 ftlo POI 531449_4 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | N/A | 374.3483 | N/A | N/A | N/A | 481.9803 | N/A | N/A | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 600 | 600 | none | none | 600 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 600 | 481.9803 | 531419 DOBSON 3 115 531493 GANO 3 115 1 ftlo POI 531449_4 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | N/A | 374.3483 | N/A | 600 | N/A | 481.9803 | N/A | 600 | N/A | N/A
ERAS-2025-017 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 600 | 600 | none | none | 600 | N/A | N/A | 600 | 0 | N/A | N/A | 600 | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | April 1 - May 31 (Long Term) | 256 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 256 | N/A | 256 | N/A | 256 | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | April 1 - May 31 (Near Term) | 256 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 256 | N/A | N/A | 256 | 0 | N/A | N/A | 256 | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | Dec 1 - March 31 (Long Term) | 256 | 256 | none | none | N/A | N/A | N/A | 256 | N/A | N/A | N/A | 256 | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | Dec 1 - March 31 (Near Term) | 256 | 256 | none | none | N/A | N/A | N/A | 256 | N/A | N/A | N/A | 256 | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | June 1 - Sept 30 (Long Term) | 256 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 256 | N/A | N/A | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | June 1 - Sept 30 (Near Term) | 256 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 256 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | Oct 1 - Nov 30 (Long Term) | 256 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 256 | N/A | 256 | N/A | 256 | N/A | N/A
ERAS-2025-018 | 05 SOUTHWEST | Hybrid | Oct 1 - Nov 30 (Near Term) | 256 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 256 | N/A | N/A | 256 | 0 | N/A | N/A | 256 | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 80 | 80 | none | none | N/A | 80 | N/A | 80 | N/A | 64.6957 | N/A | 80 | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 80 | 80 | none | none | 80 | N/A | N/A | 80 | 59.5014 | N/A | N/A | 80 | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 80 | 80 | none | none | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 80 | 80 | none | none | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 80 | 80 | none | none | N/A | 80 | N/A | N/A | N/A | 64.6957 | N/A | N/A | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 80 | 80 | none | none | 80 | N/A | N/A | N/A | 59.5014 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 80 | 80 | none | none | N/A | 80 | N/A | 80 | N/A | 64.6957 | N/A | 80 | N/A | N/A
ERAS-2025-019 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 80 | 80 | none | none | 80 | N/A | N/A | 80 | 59.5014 | N/A | N/A | 80 | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | April 1 - May 31 (Long Term) | 400 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 0 | N/A | 400 | N/A | 400 | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | April 1 - May 31 (Near Term) | 400 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | 400 | N/A | N/A | 0 | 0 | N/A | N/A | 400 | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | Dec 1 - March 31 (Long Term) | 400 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 400 | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | Dec 1 - March 31 (Near Term) | 400 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 400 | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | June 1 - Sept 30 (Long Term) | 400 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 400 | N/A | N/A | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | June 1 - Sept 30 (Near Term) | 400 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 400 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | Oct 1 - Nov 30 (Long Term) | 400 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 0 | N/A | 400 | N/A | 400 | N/A | N/A
ERAS-2025-020 | 05 SOUTHWEST | Hybrid | Oct 1 - Nov 30 (Near Term) | 400 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | 400 | N/A | N/A | 0 | 0 | N/A | N/A | 400 | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 500 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | 0 | N/A | N/A | N/A | 500 | N/A | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 500 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | 0 | N/A | N/A | N/A | 500 | N/A | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 500 | 500 | none | none | N/A | N/A | N/A | 500 | N/A | N/A | N/A | 500 | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 500 | 500 | none | none | N/A | N/A | N/A | 500 | N/A | N/A | N/A | 500 | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 500 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 500 | N/A | N/A | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 500 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 500 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 500 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | 0 | N/A | N/A | N/A | 500 | N/A | N/A | N/A
ERAS-2025-021 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 500 | 0 | Non-Converged: P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | 0 | N/A | N/A | N/A | 500 | N/A | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 123 | 123 | none | none | N/A | 123 | N/A | 123 | N/A | 123 | N/A | 123 | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 123 | 123 | none | none | 123 | N/A | N/A | 123 | 123 | N/A | N/A | 123 | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 123 | 123 | none | none | N/A | N/A | N/A | 123 | N/A | N/A | N/A | 123 | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 123 | 123 | none | none | N/A | N/A | N/A | 123 | N/A | N/A | N/A | 123 | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 123 | 123 | none | none | N/A | 123 | N/A | N/A | N/A | 123 | N/A | N/A | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 123 | 123 | none | none | 123 | N/A | N/A | N/A | 123 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 123 | 123 | none | none | N/A | 123 | N/A | 123 | N/A | 123 | N/A | 123 | N/A | N/A
ERAS-2025-022 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 123 | 123 | none | none | 123 | N/A | N/A | 123 | 123 | N/A | N/A | 123 | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 505 | 505 | none | none | N/A | 510 | N/A | 510 | N/A | 510 | N/A | 510 | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 505 | 505 | none | none | 510 | N/A | N/A | 510 | 510 | N/A | N/A | 510 | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 510 | 510 | none | none | N/A | N/A | N/A | 510 | N/A | N/A | N/A | 510 | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 510 | 510 | none | none | N/A | N/A | N/A | 510 | N/A | N/A | N/A | 510 | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 505 | 505 | none | none | N/A | 510 | N/A | N/A | N/A | 510 | N/A | N/A | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 505 | 505 | none | none | 510 | N/A | N/A | N/A | 510 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 505 | 505 | none | none | N/A | 510 | N/A | 510 | N/A | 510 | N/A | 510 | N/A | N/A
ERAS-2025-023 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 505 | 505 | none | none | 510 | N/A | N/A | 510 | 510 | N/A | N/A | 510 | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 665 | 542.437 | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 ftlo 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | N/A | 330.5216 | N/A | 274.7068 | N/A | 542.437 | N/A | 744 | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 665 | 404.4588 | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 ftlo 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | 326.0897 | N/A | N/A | 274.7068 | 404.4588 | N/A | N/A | 744 | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 744 | 744 | none | none | N/A | N/A | N/A | 274.7068 | N/A | N/A | N/A | 744 | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 744 | 744 | none | none | N/A | N/A | N/A | 274.7068 | N/A | N/A | N/A | 744 | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 665 | 542.437 | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 ftlo 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | N/A | 330.5216 | N/A | N/A | N/A | 542.437 | N/A | N/A | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 665 | 404.4588 | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 ftlo 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | 326.0897 | N/A | N/A | N/A | 404.4588 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 665 | 542.437 | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 ftlo 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | N/A | 330.5216 | N/A | 274.7068 | N/A | 542.437 | N/A | 744 | N/A | N/A
ERAS-2025-024 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 665 | 404.4588 | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 ftlo 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | 326.0897 | N/A | N/A | 274.7068 | 404.4588 | N/A | N/A | 744 | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 175 | 175 | none | none | N/A | 175 | N/A | 175 | N/A | 175 | N/A | 175 | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 175 | 175 | none | none | 175 | N/A | N/A | 175 | 162.6555 | N/A | N/A | 175 | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 175 | 175 | none | none | N/A | N/A | N/A | 175 | N/A | N/A | N/A | 175 | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 175 | 175 | none | none | N/A | N/A | N/A | 175 | N/A | N/A | N/A | 175 | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 175 | 175 | none | none | N/A | 175 | N/A | N/A | N/A | 175 | N/A | N/A | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 175 | 175 | none | none | 175 | N/A | N/A | N/A | 162.6555 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 175 | 175 | none | none | N/A | 175 | N/A | 175 | N/A | 175 | N/A | 175 | N/A | N/A
ERAS-2025-025 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 175 | 175 | none | none | 175 | N/A | N/A | 175 | 162.6555 | N/A | N/A | 175 | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 665 | 665 | none | none | N/A | 435.7265 | N/A | 744 | N/A | 744 | N/A | 744 | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 665 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 385.1256 | N/A | N/A | 744 | 0 | N/A | N/A | 744 | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 744 | 744 | none | none | N/A | N/A | N/A | 744 | N/A | N/A | N/A | 744 | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 744 | 744 | none | none | N/A | N/A | N/A | 744 | N/A | N/A | N/A | 744 | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 665 | 665 | none | none | N/A | 435.7265 | N/A | N/A | N/A | 744 | N/A | N/A | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 665 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 385.1256 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 665 | 665 | none | none | N/A | 435.7265 | N/A | 744 | N/A | 744 | N/A | 744 | N/A | N/A
ERAS-2025-026 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 665 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 385.1256 | N/A | N/A | 744 | 0 | N/A | N/A | 744 | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 179.6797 | N/A | 250 | N/A | 250 | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 107.158 | N/A | N/A | 179.6797 | 0 | N/A | N/A | 250 | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 250 | 250 | none | none | N/A | N/A | N/A | 179.6797 | N/A | N/A | N/A | 250 | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 250 | 250 | none | none | N/A | N/A | N/A | 179.6797 | N/A | N/A | N/A | 250 | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 107.158 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 179.6797 | N/A | 250 | N/A | 250 | N/A | N/A
ERAS-2025-027 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 107.158 | N/A | N/A | 179.6797 | 0 | N/A | N/A | 250 | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 384 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 384 | N/A | 384 | N/A | 384 | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 384 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 384 | N/A | N/A | 384 | 0 | N/A | N/A | 384 | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 384 | 384 | none | none | N/A | N/A | N/A | 384 | N/A | N/A | N/A | 384 | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 384 | 384 | none | none | N/A | N/A | N/A | 384 | N/A | N/A | N/A | 384 | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 384 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 384 | N/A | N/A | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 384 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 384 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 384 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 384 | N/A | 384 | N/A | 384 | N/A | N/A
ERAS-2025-028 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 384 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 384 | N/A | N/A | 384 | 0 | N/A | N/A | 384 | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 170 | 170 | none | none | N/A | 170 | N/A | 170 | N/A | 150.4184 | N/A | 170 | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 170 | 170 | none | none | 170 | N/A | N/A | 170 | 151.2156 | N/A | N/A | 170 | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 170 | 170 | none | none | N/A | N/A | N/A | 170 | N/A | N/A | N/A | 170 | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 170 | 170 | none | none | N/A | N/A | N/A | 170 | N/A | N/A | N/A | 170 | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 170 | 170 | none | none | N/A | 170 | N/A | N/A | N/A | 150.4184 | N/A | N/A | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 170 | 170 | none | none | 170 | N/A | N/A | N/A | 151.2156 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 170 | 170 | none | none | N/A | 170 | N/A | 170 | N/A | 150.4184 | N/A | 170 | N/A | N/A
ERAS-2025-029 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 170 | 170 | none | none | 170 | N/A | N/A | 170 | 151.2156 | N/A | N/A | 170 | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | April 1 - May 31 (Long Term) | 350 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 350 | N/A | 350 | N/A | 350 | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | April 1 - May 31 (Near Term) | 350 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 350 | N/A | N/A | 350 | 0 | N/A | N/A | 350 | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | Dec 1 - March 31 (Long Term) | 350 | 350 | none | none | N/A | N/A | N/A | 350 | N/A | N/A | N/A | 350 | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | Dec 1 - March 31 (Near Term) | 350 | 350 | none | none | N/A | N/A | N/A | 350 | N/A | N/A | N/A | 350 | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | June 1 - Sept 30 (Long Term) | 350 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 350 | N/A | N/A | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | June 1 - Sept 30 (Near Term) | 350 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 350 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | Oct 1 - Nov 30 (Long Term) | 350 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 350 | N/A | 350 | N/A | 350 | N/A | N/A
ERAS-2025-030 | 05 SOUTHWEST | Hybrid | Oct 1 - Nov 30 (Near Term) | 350 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 350 | N/A | N/A | 350 | 0 | N/A | N/A | 350 | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 132.7221 | N/A | 150 | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 133.4255 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | N/A | N/A | 132.7221 | N/A | N/A | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | N/A | 133.4255 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 132.7221 | N/A | 150 | N/A | N/A
ERAS-2025-031 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 133.4255 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | April 1 - May 31 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 121.3045 | N/A | 150 | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | April 1 - May 31 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 111.5651 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Long Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Near Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | N/A | N/A | 121.3045 | N/A | N/A | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | N/A | 111.5651 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 121.3045 | N/A | 150 | N/A | N/A
ERAS-2025-032 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 111.5651 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 121.3045 | N/A | 150 | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 111.908 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 150 | none | none | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | N/A | N/A | 121.3045 | N/A | N/A | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | N/A | 111.908 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 150 | none | none | N/A | 150 | N/A | 150 | N/A | 121.3045 | N/A | 150 | N/A | N/A
ERAS-2025-033 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 150 | none | none | 150 | N/A | N/A | 150 | 111.908 | N/A | N/A | 150 | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 250 | 78.8246 | 505488 CARTHAG5 161 997570 CRG X1 69.0 1 ftlo 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | N/A | 17.2722 | N/A | 250 | N/A | 78.8246 | N/A | 250 | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 250 | 205.1928 | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 ftlo P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | 84.3315 | N/A | N/A | 250 | 205.1928 | N/A | N/A | 250 | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 250 | 250 | none | none | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 250 | 250 | none | none | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 250 | 78.8246 | 505488 CARTHAG5 161 997570 CRG X1 69.0 1 ftlo 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | N/A | 17.2722 | N/A | N/A | N/A | 78.8246 | N/A | N/A | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 250 | 205.1928 | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 ftlo P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | 84.3315 | N/A | N/A | N/A | 205.1928 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 250 | 78.8246 | 505488 CARTHAG5 161 997570 CRG X1 69.0 1 ftlo 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | N/A | 17.2722 | N/A | 250 | N/A | 78.8246 | N/A | 250 | N/A | N/A
ERAS-2025-034 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 250 | 205.1928 | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 ftlo P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | 84.3315 | N/A | N/A | 250 | 205.1928 | N/A | N/A | 250 | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 137.96 | 137.96 | none | none | N/A | 137.96 | N/A | 137.96 | N/A | 137.96 | N/A | 137.96 | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 137.96 | 137.96 | none | none | 137.96 | N/A | N/A | 137.96 | 137.96 | N/A | N/A | 137.96 | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 137.96 | 137.96 | none | none | N/A | N/A | N/A | 137.96 | N/A | N/A | N/A | 137.96 | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 137.96 | 137.96 | none | none | N/A | N/A | N/A | 137.96 | N/A | N/A | N/A | 137.96 | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 137.96 | 137.96 | none | none | N/A | 137.96 | N/A | N/A | N/A | 137.96 | N/A | N/A | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 137.96 | 137.96 | none | none | 137.96 | N/A | N/A | N/A | 137.96 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 137.96 | 137.96 | none | none | N/A | 137.96 | N/A | 137.96 | N/A | 137.96 | N/A | 137.96 | N/A | N/A
ERAS-2025-035 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 137.96 | 137.96 | none | none | 137.96 | N/A | N/A | 137.96 | 137.96 | N/A | N/A | 137.96 | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 140 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 140 | N/A | 140 | N/A | 140 | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 140 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 140 | N/A | N/A | 140 | 0 | N/A | N/A | 140 | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 140 | 140 | none | none | N/A | N/A | N/A | 140 | N/A | N/A | N/A | 140 | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 140 | 140 | none | none | N/A | N/A | N/A | 140 | N/A | N/A | N/A | 140 | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 140 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | N/A | N/A | 140 | N/A | N/A | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 140 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 140 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 140 | 0 | Non-Converged: 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Potter to Beckham 345 kV Line (2024 ITP) | N/A | 0 | N/A | 140 | N/A | 140 | N/A | 140 | N/A | N/A
ERAS-2025-036 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 140 | 0 | Non-Converged: POI 511468_4 | Line - Crawfish Draw - Phantom 765 kV New Line | 140 | N/A | N/A | 140 | 0 | N/A | N/A | 140 | N/A | N/A

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01NR | ERAS-2025-001 | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
02NR | ERAS-2025-001 | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
03NR | ERAS-2025-001 | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
04NR | ERAS-2025-001 | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
05ALL | ERAS-2025-001 | ERIS | Non-Converged | Non-Converged | 26SP | None | [7 empty] | None
05ALL | ERAS-2025-001 | ERIS | Non-Converged | Non-Converged | 29L, 29SP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
05ALL | ERAS-2025-001 | ERIS | Non-Converged | Non-Converged | 29SP | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | [7 empty] | Potter to Beckham 345 kV Line (2024 ITP)
05ALL | ERAS-2025-001 | ERIS | Non-Converged | Non-Converged | 29L, 29SP, 29WP | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | [7 empty] | Build New Andrews to Road Runner 345 kV Line
05NR | ERAS-2025-001 | NRIS | Non-Converged | None | 29L | None | [7 empty] | None
01NR | ERAS-2025-001 CF | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
02NR | ERAS-2025-001 CF | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
03NR | ERAS-2025-001 CF | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
04NR | ERAS-2025-001 CF | NRIS | Non-Converged | N/A | 29L | N/A | [7 empty] | N/A
05ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05NR | ERAS-2025-001 CF | NRIS | Non-Converged | None | 29L | None | [7 empty] | None
01NR | ERAS-2025-001 | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
02NR | ERAS-2025-001 | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
03NR | ERAS-2025-001 | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
04NR | ERAS-2025-001 | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
05ALL | ERAS-2025-001 | ERIS | Thermal | None | 29L | None | [7 empty] | None
05ALL | ERAS-2025-001 | ERIS | Thermal | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 29SP | System Intact | 1011 |  | <90% | 106.19 |  |  |  | COMANC7 TAP to LES 345 kV Line Rebuild
05ALL | ERAS-2025-001 | ERIS | Thermal | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 29SP | System Intact | 1011 |  | <90% | 106.39 |  |  |  | COMANC7 TAP to OKU 345 kV Line Rebuild
05ALL | ERAS-2025-001 | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 29SP | System Intact | 279 |  | <90% | 104.06 |  |  |  | ELKCITY 230/138 kV Transformer Replacement
05ALL | ERAS-2025-001 | ERIS | Thermal | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 26SP, 29SP, 29WP | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 353 | <90% | 123.24 |  |  |  | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
05ALL | ERAS-2025-001 | ERIS | Thermal | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 29SP | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: |  | 318.7 | <90% | 118.61 |  |  |  | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
05ALL | ERAS-2025-001 | ERIS | Thermal | 525549 TOLK 7 345 3WXFMR ABBXNL844501 230 1 | 29SP | 525549 TOLK 7 345 3WXFMR ABB XNL8445-01 2 |  | 556 | 93.36 | 104.59 |  |  |  | Tolk 345/230 kV CKT 1 Transformer Replacement
05ALL | ERAS-2025-001 | ERIS | Thermal | 526784 AMOCOWASSON6 230 527011 XTO_MAHONEY6 230 1 | 26SP, 29SP | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: |  | 498 | <90% | 109.19 |  |  |  | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade
05ALL | ERAS-2025-001 | ERIS | Thermal | 526784 AMOCOWASSON6 230 527149 MUSTANG 6 230 1 | 26SP, 29SP | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: |  | 498 | <90% | 105.04 |  |  |  | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade
05ALL | ERAS-2025-001 | ERIS | Thermal | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 | 26SP, 29SP | System Intact | 470 |  | <90% | 101.91 |  |  |  | YOAKUM to BRU SUB 230 kV Line Rebuild
05ALL | ERAS-2025-001 | ERIS | Thermal | 526935 YOAKUM 6 230 527149 MUSTANG 6 230 1 | 29SP | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: |  | 447 | 96.05 | 126.06 |  |  |  | YOAKUM to MUSTANG 230 kV Line Rebuild
05ALL | ERAS-2025-001 | ERIS | Thermal | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 | 26SP, 29SP, 29WP | System Intact | 399 |  | <90% | 123.28 |  |  |  | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
05NR | ERAS-2025-001 | NRIS | Thermal | None | 29L | None | [7 empty] | None
01NR | ERAS-2025-001 CF | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
02NR | ERAS-2025-001 CF | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
03NR | ERAS-2025-001 CF | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
04NR | ERAS-2025-001 CF | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
05ALL | ERAS-2025-001 CF | ERIS | Thermal | None | 26SP, 29L, 29WP | None | [7 empty] | None
05ALL | ERAS-2025-001 | ERIS | Thermal | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 29SP | P12:345:OKGE:BKRBKR4290:::EHV: |  | 1176 | <90 % | 117.77 |  |  |  | COMANC7 TAP to LES 345 kV Line Rebuild
05ALL | ERAS-2025-001 | ERIS | Thermal | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 29SP | P12:345:OKGE:BKRBKR4290:::EHV: |  | 1176 | <90 % | 117.99 |  |  |  | COMANC7 TAP to OKU 345 kV Line Rebuild
05NR | ERAS-2025-001 CF | NRIS | Thermal | None | 29L | None | [7 empty] | None
01NR | ERAS-2025-001 | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
02NR | ERAS-2025-001 | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
03NR | ERAS-2025-001 | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
04NR | ERAS-2025-001 | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
05ALL | ERAS-2025-001 | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05NR | ERAS-2025-001 | NRIS | Voltage | None | 29L | None | [7 empty] | None
01NR | ERAS-2025-001 CF | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
02NR | ERAS-2025-001 CF | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
03NR | ERAS-2025-001 CF | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
04NR | ERAS-2025-001 CF | NRIS | Voltage | N/A | 29L | N/A | [7 empty] | N/A
05ALL | ERAS-2025-001 CF | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
05NR | ERAS-2025-001 CF | NRIS | Voltage | None | 29L | None | [7 empty] | None
04ALL | ERAS-2025-001 | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | ERAS-2025-001 | ERIS | Thermal | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | ERAS-2025-001 CF | ERIS | Thermal | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | ERAS-2025-001 | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | ERAS-2025-001 CF | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
00ALL | ERAS-2025-001 | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 26SP, 29SP, 29WP | System Intact | 237 |  | <90 % | 143.17 |  |  |  | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 26SP, 29SP, 29WP | System Intact | 237 |  | <90 % | 143.17 |  |  |  | Comanche 345 kV New Substation
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 26SP, 29SP, 29WP | System Intact | 237 |  | <90 % | 143.17 |  |  |  | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 26SP, 29SP | System Intact | 237 |  | <90 % | 143.17 |  |  |  | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 237 |  | <90 % | 153.26 |  |  |  | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 237 |  | <90 % | 153.26 |  |  |  | Comanche 345 kV New Substation
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 237 |  | <90 % | 153.26 |  |  |  | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP | System Intact | 237 |  | <90 % | 153.26 |  |  |  | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 202 |  | <90 % | 122.64 |  |  |  | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
00ALL | ERAS-2025-001 | ERIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 202 |  | <90 % | 122.64 |  |  |  | Comanche 345 kV New Substation
00ALL | ERAS-2025-001 | ERIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 202 |  | <90 % | 122.64 |  |  |  | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP | System Intact | 202 |  | <90 % | 122.64 |  |  |  | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 26SP, 29SP | System Intact | 121 |  | <90 % | 134.16 |  |  |  | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 26SP, 29SP | System Intact | 121 |  | <90 % | 134.36 |  |  |  | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 514840 JONESTP4 138 514941 HSL 4 138 1 | 26SP | P12:138:OKGE:BKRBKR1770:::HV: |  | 382 | <90 % | 100.98 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 26SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 |  | 382 | <90 % | 106.11 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 26SP | System Intact | 287 |  | <90 % | 102.5 |  |  |  | Dunjee-Reno 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 26SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 |  | 287 | <90 % | 109.53 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 514941 HSL 4 138 514987 DALE 4 138 1 | 26SP, 29SP, 29WP | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 191 | <90 % | 124.94 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 26SP, 29WP | System Intact | 213 |  | <90 % | 111.92 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 514963 TROSPER4 138 514973 RENO 4 138 1 | 26SP | System Intact | 191 |  | <90 % | 113.21 |  |  |  | Trosper-Reno 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 26SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 |  | 287 | <90 % | 108.12 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 26SP | P12:138:OKGE-WFEC:BKRBKR1800:::HV: |  | 267 | <90 % | 107.92 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 | ERIS | Thermal | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 26SP | P12:138:OKGE-WFEC:BKRBKR1800:::HV: |  | 267 | <90 % | 107.92 |  |  |  | ERAS-2025-004 and ERAS-2025-010 Model Correction
00ALL | ERAS-2025-001 | ERIS | Thermal | 528526 TEAGUE 3 115 528547 S_JAL 3 115 1 | 29SP | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: |  | 154 | 134.77 | 106.2 |  |  |  | Build New Andrews to Road Runner 345 kV Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1 | 29SP | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: |  | 175 | 140.33 | 108.05 |  |  |  | Build New Andrews to Road Runner 345 kV Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 528602 ANDREWS 345/115/34.5 kV Transformer | 29SP | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: |  | 448 | 140.96 | 115.61 |  |  |  | Build New Andrews to Road Runner 345 kV Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 528602 ANDREWS 3 115 528603 NA_ENRICH 3 115 1 | 29SP, 29WP | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: |  | 309 | 208.68 | 167.14 |  |  |  | Build New Andrews to Road Runner 345 kV Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 531419 DOBSON3 115 531493 GANO 3 115 1 | 29SP | P23:345:SUNC:HLC_BRK282:::EHV: |  | 228.5 | <90 % | 109.19 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 29SP | P23:345:SUNC:HLC_BRK282:::EHV: |  | 228.5 | <90 % | 106.82 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 531432 PILE 3 115 531493 GANO 3 115 1 | 29SP | P23:345:SUNC:HLC_BRK282:::EHV: |  | 228.5 | <90 % | 108.27 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00ALL | ERAS-2025-001 | ERIS | Thermal | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 29SP | System Intact | 1183 |  | <90 % | 102.15 |  |  |  | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 | ERIS | Thermal | 547470 JOP145 5 161 547498 STL439 5 161 1 | 26SP, 29SP | 547467 ORO110 5 161 547469 RIV4525 161 1 |  | 290 | 104.8 | 120.85 |  |  |  | Joplin West 7th - Stateline 161 kV Line (Model Correction)
00ALL | ERAS-2025-001 | ERIS | Thermal | 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 | 29WP | POI 659105_7 - Potential P4 Event |  | 1195 | <90 % | 115.48 |  |  |  | Replacement of two disconnect switches at Antelope Valley Station
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 26SP, 29SP | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: |  | 106 | <90 % | 132.15 |  |  |  | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 26SP, 29SP | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: |  | 106 | <90 % | 125.01 |  |  |  | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 26SP, 29SP | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: |  | 106 | <90 % | 115.56 |  |  |  | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 29SP, 29WP | System Intact | 287 |  | <90 % | 102.42 |  |  |  | Dunjee-Reno 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 29SP, 29WP | System Intact | 67 |  | <90 % | 115.19 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 29SP, 29WP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 |  | 287 | <90 % | 109.52 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514941 HSL 4 138 514987 DALE 4 138 1 | 29SP, 29WP | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 191 | <90 % | 122.32 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 29SP, 29WP | System Intact | 213 |  | <90 % | 109.64 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514963 TROSPER4 138 514973 RENO 4 138 1 | 29SP, 29WP | System Intact | 191 |  | <90 % | 114.61 |  |  |  | Trosper-Reno 138 kV Ckt 1 Rebuild
00ALL | ERAS-2025-001 CF | ERIS | Thermal | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 29SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 |  | 287 | <90 % | 109.84 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 | NRIS | Thermal | 505488 CARTHAG5 161 997569 CRG X2 69.0 1 | 29SP | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 | 84 | 84 | 106.19 | 106.26 |  |  |  | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
00NR | ERAS-2025-001 | NRIS | Thermal | 505488 CARTHAG5 161 997570 CRG X1 69.0 1 | 29SP | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | 84 | 84 | 106.83 | 106.9 |  |  |  | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
00NR | ERAS-2025-001 | NRIS | Thermal | 505488 CARTHAG5 161 997643 CRG X2 69.0 1 | 26SP | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 | 84 | 84 | 100.86 | 101.14 |  |  |  | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
00NR | ERAS-2025-001 | NRIS | Thermal | 505488 CARTHAG5 161 997644 CRG X1 69.0 1 | 26SP | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | 84 | 84 | 101.46 | 101.74 |  |  |  | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
00NR | ERAS-2025-001 | NRIS | Thermal | 505490 CARTHG 2 69.0 997569 CRG X2 69.0 1 | 29SP | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 | 84 | 84 | 101.75 | 101.54 |  |  |  | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
00NR | ERAS-2025-001 | NRIS | Thermal | 505490 CARTHG 2 69.0 997570 CRG X1 69.0 1 | 29SP | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | 84 | 84 | 102.43 | 102.22 |  |  |  | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
00NR | ERAS-2025-001 | NRIS | Thermal | 530565 SEWARD 2 69.0 996957 SEWARD T1 69.0 1 | 29SP | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 40 | 44.8 | <90% | 106.62 |  |  |  | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1
00NR | ERAS-2025-001 | NRIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 26SP, 29SP, 29WP | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 40 | 40 | <90% | 119.3 |  |  |  | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
00NR | ERAS-2025-001 | NRIS | Thermal | 530679 SEWRDMW3 115 996957 SEWARD T1 69.0 1 | 29SP | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 40 | 44.8 | <90% | 104.98 |  |  |  | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1
00NR | ERAS-2025-001 | NRIS | Thermal | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 29SP | POI 531449_4 | 336 | 358.5 | <90% | 111.52 |  |  |  | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
00NR | ERAS-2025-001 | NRIS | Thermal | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 26SP | POI 531449_4 | 336 | 358.5 | <90% | 112.01 |  |  |  | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
00NR | ERAS-2025-001 | NRIS | Thermal | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 29SP | POI 531449_4 | 336 | 358.5 | <90% | 113.75 |  |  |  | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
00NR | ERAS-2025-001 | NRIS | Thermal | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 26SP | POI 531449_4 | 336 | 358.5 | <90% | 114.2 |  |  |  | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
00NR | ERAS-2025-001 | NRIS | Thermal | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 26SP | P23:345:WERE:WICH-345-50:EHV: | 369 | 382 | <90% | 102.63 |  |  |  | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 | NRIS | Thermal | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | 26SP | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1 | 89.8 | 89.8 | <90% | 103.76 |  |  |  | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade
00NR | ERAS-2025-001 | NRIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 26SP, 29SP | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | 101 | 101 | <90% | 107.67 |  |  |  | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
00NR | ERAS-2025-001 | NRIS | Thermal | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 29SP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | 400 | 440 | <90% | 113.08 |  |  |  | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
00NR | ERAS-2025-001 | NRIS | Thermal | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 26SP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | 400 | 440 | <90% | 111.87 |  |  |  | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
00NR | ERAS-2025-001 | NRIS | Thermal | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 29SP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | 400 | 440 | <90% | 112.01 |  |  |  | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
00NR | ERAS-2025-001 | NRIS | Thermal | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 26SP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | 400 | 440 | <90% | 111.38 |  |  |  | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
00NR | ERAS-2025-001 | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 26SP | P12:345:OTP:JAMESTN3:CENTER3:1 | 341 | 341 | <90% | 104.84 |  |  |  | Fargo 230 kV Terminal Upgrade
00NR | ERAS-2025-001 | NRIS | Thermal | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 29WP | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | 956 | 956 | <90% | 102.68 |  |  |  | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
00NR | ERAS-2025-001 | NRIS | Thermal | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 26SP, 29SP | POI 514801_3 | 136 | 136 | <90% | 125.21 |  |  |  | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
00NR | ERAS-2025-001 | NRIS | Thermal | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 26SP | POI 514801_3 | 241 | 283 | <90% | 105.16 |  |  |  | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
00NR | ERAS-2025-001 | NRIS | Thermal | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | 29SP, 29WP | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | 435 | 435 | 107.19 | 110.39 |  |  |  | Roadrunner 345/115 kV transformer #3 Model Correction
00NR | ERAS-2025-001 | NRIS | Thermal | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | 29SP, 29WP | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | 435 | 435 | 107.19 | 110.39 |  |  |  | Roadrunner 345/115 kV transformer #2 Model Correction
00NR | ERAS-2025-001 | NRIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00NR | ERAS-2025-001 | NRIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
01ALL | ERAS-2025-001 | ERIS | Thermal | N/A | 26SP, 29SP, 29WP | N/A | [7 empty] | N/A
01ALL | ERAS-2025-001 | ERIS | Voltage | N/A | 26SP, 29SP, 29WP | N/A | [7 empty] | N/A
01ALL | ERAS-2025-001 | ERIS | Non-Converged | N/A | 26SP, 29SP, 29WP | N/A | [7 empty] | N/A
02ALL | ERAS-2025-001 | ERIS | Thermal | N/A | 26SP, 29SP, 29WP | N/A | [7 empty] | N/A
02ALL | ERAS-2025-001 | ERIS | Voltage | N/A | 26SP, 29SP, 29WP | N/A | [7 empty] | N/A
02ALL | ERAS-2025-001 | ERIS | Non-Converged | N/A | 26SP, 29SP, 29WP | N/A | [7 empty] | N/A
03ALL | ERAS-2025-001 | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
03ALL | ERAS-2025-001 | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
03ALL | ERAS-2025-001 | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00NR | ERAS-2025-001 CF | NRIS | Thermal | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 26SP | P12:345:OKGE:BKRBKR4290:::EHV: | 1011 | 1176 | <90% | 124.4 |  |  |  | COMANC7 TAP to LES 345 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 29SP | POI 531449_4 | 211.7 | 228.5 | <90% | 113.41 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | ERAS-2025-001 CF | NRIS | Thermal | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 29SP | POI 531449_4 | 98.4 | 98.4 | <90% | 100.41 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | ERAS-2025-001 CF | NRIS | Thermal | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 29SP | POI 531449_4 | 211.7 | 228.5 | <90% | 111.04 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | ERAS-2025-001 CF | NRIS | Thermal | 531432 PILE 3 115 531493 GANO 3 115 1 | 29SP | POI 531449_4 | 211.7 | 228.5 | <90% | 112.49 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | ERAS-2025-001 CF | NRIS | Thermal | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 29SP | POI 531449_4 | 195.4 | 195.4 | <90% | 104.66 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | ERAS-2025-001 CF | NRIS | Thermal | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 26SP | System Intact | 1011 | 1176 | <90% | 112.67 |  |  |  | COMANC7 TAP to LES 345 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 26SP | P12:345:OKGE:BKRBKR4290:::EHV: | 1011 | 1176 | <90% | 124.4 |  |  |  | COMANC7 TAP to LES 345 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 26SP, 29SP, 29WP | System Intact | 202 | 235 | <90% | 151.49 |  |  |  | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 26SP, 29SP, 29WP | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | <90% | 250 |  |  |  | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 202 | 235 | <90% | 166.09 |  |  |  | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | P12:138:AEPW:COMANC-4:L.E.S.-4::: | 237 | 265 | <90% | 251.91 |  |  |  | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 29SP | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 71 | 72 | <90% | 104.82 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 26SP | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 71 | 72 | <90% | 110.96 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 26SP, 29SP | System Intact | 106 | 106 | <90% | 110.72 |  |  |  | Duncan - Duncan Tap 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 26SP, 29SP, 29WP | P42:345:OKGE:SB_GRNT7313:::EHV: | 106 | 106 | <90% | 144.39 |  |  |  | Duncan - Duncan Tap 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 26SP, 29SP, 29WP | System Intact | 121 | 171 | <90% | 142.91 |  |  |  | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 26SP, 29SP, 29WP | POI 511568_3 | 121 | 171 | <90% | 129.9 |  |  |  | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 29SP | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 71 | 72 | <90% | 105.34 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 26SP | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 71 | 72 | <90% | 111.5 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 26SP | System Intact | 106 | 106 | <90% | 103.7 |  |  |  | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 26SP, 29SP, 29WP | P42:345:OKGE:SB_GRNT7313:::EHV: | 106 | 106 | <90% | 137.3 |  |  |  | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 26SP, 29SP, 29WP | P42:345:OKGE:SB_GRNT7313:::EHV: | 106 | 106 | <90% | 127.8 |  |  |  | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 188 | 202 | <90% | 121.99 |  |  |  | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP, 29SP, 29WP | P12:138:AEPW:COMANC-4:L.E.S.-4::: | 188 | 202 | <90% | 255.02 |  |  |  | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 26SP, 29SP, 29WP | System Intact | 121 | 171 | <90% | 143.11 |  |  |  | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 26SP, 29SP, 29WP | POI 511568_3 | 121 | 171 | <90% | 130 |  |  |  | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514840 138 514941 HSL 4 138 1 | 26SP | P12:138:OKGE:BKRBKR1770:::HV: | 379 | 382 | <90% | 100.4 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514840 JONESTP4 138 514941 HSL 4 138 1 | 26SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | 379 | 382 | <90% | 100.29 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 26SP | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | 382 | 382 | <90% | 105.7 |  |  |  | Comanche 345 kV New Substation
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 29SP | System Intact | 287 | 287 | <90% | 101.64 |  |  |  | Dunjee - Reno 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 26SP, 29SP, 29WP | P12:138:OKGE:BKRBKR1093:::HV: | 287 | 287 | <90% | 126.92 |  |  |  | Dunjee - Reno 138 kV Ckt 1 Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 26SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | 67 | 76 | <90% | 116.12 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 29SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | 67 | 76 | <90% | 114.43 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 29SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | 268 | 287 | <90% | 108.04 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 26SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | 268 | 287 | <90% | 105.28 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514941 HSL 4 138 514987 DALE 4 138 1 | 26SP, 29SP, 29WP | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 191 | 191 | <90% | 115.63 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 26SP, 29SP, 29WP | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | 213 | 266 | <90% | 109.39 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 26SP, 29SP, 29WP | System Intact | 213 | 266 | <90% | 109.56 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514963 TROSPER4 138 514973 RENO 4 138 1 | 26SP, 29SP, 29WP | P12:138:OKGE:BKRBKR4260:::HV: | 191 | 239 | <90% | 123.39 |  |  |  | Trosper - Reno 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514963 TROSPER4 138 514973 RENO 4 138 1 | 26SP, 29SP, 29WP | System Intact | 191 | 239 | <90% | 109.79 |  |  |  | Trosper - Reno 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 26SP, 29SP | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | 268 | 287 | <90% | 112.1 |  |  |  | NE 10th - Reno 138 kV Line Rebuild
00NR | ERAS-2025-001 CF | NRIS | Thermal | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 29SP | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | 233 | 267 | <90% | 101.92 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 26SP | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | 233 | 267 | <90% | 105.59 |  |  |  | Multi - Horseshoe Lake Reconfiguration
00NR | ERAS-2025-001 CF | NRIS | Thermal | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 26SP | POI 511468_3 | 96 | 106 | <90% | 100.67 |  |  |  | Comanche 345 kV New Substation
00ALL | ERAS-2025-001 CF | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00NR | ERAS-2025-001 CF | NRIS | Thermal | None | 29WP | None | [7 empty] | None
01ALL | ERAS-2025-001 CF | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
02ALL | ERAS-2025-001 CF | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
03ALL | ERAS-2025-001 CF | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00ALL | ERAS-2025-001 CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00NR | ERAS-2025-001 CF | NRIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
01ALL | ERAS-2025-001 CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
02ALL | ERAS-2025-001 CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
03ALL | ERAS-2025-001 CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00NR | ERAS-2025-001 CF | NRIS | Non-Converged | Non-Converged | 26SP | POI 511468_4 | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
00NR | ERAS-2025-001 CF | NRIS | Non-Converged | Non-Converged | 26SP | POI 511468_0 | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
00NR | ERAS-2025-001 CF | NRIS | Non-Converged | Non-Converged | 26SP | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
00NR | ERAS-2025-001 CF | NRIS | Non-Converged | Non-Converged | 26SP | POI 511468_3 | [7 empty] | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
00ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00NR | ERAS-2025-001 CF | NRIS | Non-Converged | None | 29SP, 29WP | None | [7 empty] | None
01ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
02ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
03ALL | ERAS-2025-001 CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
00ALL | ERAS-2025-001 | ERIS | Voltage | 655857 MOCCASIN-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.7905 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655831 J12_____-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8037 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655851 BIGGULCH-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.815 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655852 L11_____-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8181 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655854 SANDCREK-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8266 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655896 KEENECRN-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8274 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655859 CHARLSON-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8276 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655866 SNDCRKTP-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8277 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655830 MOUNTAIN-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8284 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655847 SWENSON -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8284 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655885 NRTHFORK-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8295 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655837 ELMTREE -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8307 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655886 KEENE -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.832 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655858 TABLEBUT-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8327 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655848 BERG -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8357 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655874 BBCMPRSS-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.846 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655836 OAKDALE -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8464 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655873 BBCOMPTP-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8465 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655884 DEMCKSLK-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8572 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655864 GRAIL -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8624 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655865 STATION8-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8624 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655853 BEARCREK-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8638 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655832 BLUEBUTE-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.866 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655883 GALAXY -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8689 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655882 GALAXYTP-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8697 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655849 VEEDER -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8697 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655897 COYOTCHR-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8712 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655880 SCHAFR_T-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8717 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655890 WERNER -MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8719 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655894 HALLIDAY-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.872 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655899 FNCYBTAP-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8722 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655893 DUNNCNTR-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8736 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655881 DAP_____-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8755 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 659388 KUMMERDG-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8758 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 659385 ROUNDUP_-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8791 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 659143 BLAISDEL-BE4 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8856 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655891 KILLDEER-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8862 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 652419 KILDEER7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8867 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 659387 KUMMERDG-BE3 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8891 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655662 ROSEGLEN-CP7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8954 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655663 RAUB TAP-CP7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8959 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655870 TBGARDEN-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8974 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 659384 ROUNDUP_-BE3 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8979 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655869 TWINVLLY-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8984 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 659248 HALLIDAY-UM7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8899 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | ERAS-2025-001 | ERIS | Voltage | 655867 TWNVLYTP-MK7 | 29WP | POI 659105_7 -Potential P4 Event |  |  |  |  | 0.8989 | 0.9 | 1.05 | Kummer Ridge 345 kV Capacitor Bank
00ALL | JTIQ Expanded Scope | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
01ALL | JTIQ Expanded Scope | ERIS | Thermal | N/A | 26SP, 29L, 29SP, 29WP | N/A | [7 empty] | N/A
02ALL | JTIQ Expanded Scope | ERIS | Thermal | N/A | 26SP, 29L, 29SP, 29WP | N/A | [7 empty] | N/A
03ALL | JTIQ Expanded Scope | ERIS | Thermal | None | 26SP, 29L, 29SP, 29WP | N/A | [7 empty] | None
04ALL | JTIQ Expanded Scope | ERIS | Thermal | None | 26SP, 29L, 29SP, 29WP | N/A | [7 empty] | None
05ALL | JTIQ Expanded Scope | ERIS | Thermal | N/A | 26SP, 29L, 29SP, 29WP | N/A | [7 empty] | N/A
01NR | JTIQ Expanded Scope | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
02NR | JTIQ Expanded Scope | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
03NR | JTIQ Expanded Scope | NRIS | Thermal | None | 29L | N/A | [7 empty] | None
04NR | JTIQ Expanded Scope | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
05NR | JTIQ Expanded Scope | NRIS | Thermal | N/A | 29L | N/A | [7 empty] | N/A
00NR | JTIQ Expanded Scope | NRIS | Thermal | None | 26SP, 29SP, 29WP | N/A | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
ERAS-2025-001 | ERAS-2025-001 | 02 NEBRASKA | 170753 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (Non-shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | 0 | 100% | 0 | 1
ERAS-2025-001 | ERAS-2025-001 | 02 NEBRASKA | 170752 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | 0 | 100% | 0 | 1
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade | Current Study | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to MUSTANG 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | 3136456.95 | 100% | 3136456.95 | 0.30607
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade | Current Study | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to XTO_MAHONEY 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | 4081811.58 | 100% | 4081811.58 | 0.30607
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170759 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | 28993147 | 100% | 28993147 | 1
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170758 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | 3817643 | 100% | 3817643 | 1
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | BRU SUB to XTO MAHONEY 230 kV Line Rebuild | Current Study | Rebuild 1.76 miles BRU_SUB to XTO_MAHONEY 230 kV line to a minimum of 680 MVA | 1554975.84 | 100% | 1554975.84 | 0.69393
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% | 73524573 | 0.23195
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% | 73524573 | 0.04787
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% | 73524573 | 0.01185
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | Current Study | Build a new CARTHAG5 to CARTHG 2 161-69 kV transformer 3 with a rating of 84 MVA | 6075000 | 100% | 6075000 | 0.01479
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 2158361.0297 | 14.39% | 15000000 | 0.03601
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 1380500.012 | 9.203% | 15000000 | 0.03669
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 2159251.8303 | 14.4% | 15000000 | 0.03586
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 2226166.5903 | 14.84% | 15000000 | 0.06665
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 416466.8368 | 2.776% | 15000000 | 0.03325
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 746091.466 | 4.974% | 15000000 | 0.03574
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 3339249.8855 | 22.26% | 15000000 | 0.06665
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 1380500.012 | 9.203% | 15000000 | 0.03669
ERAS-2025-031 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 455295.3238 | 3.035% | 15000000 | 0.03635
ERAS-2025-029 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 516001.367 | 3.44% | 15000000 | 0.03635
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 222115.6463 | 1.481% | 15000000 | 0.03325
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 3.173% | 9932652 | 0.01496
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 2.005% | 9932652 | 0.01286
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 2.841% | 9932652 | 0.0125
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 3.128% | 9932652 | 0.0125
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 5.052% | 9932652 | 0.01292
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 7.332% | 9932652 | 0.015
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 24.12% | 9932652 | 0.03317
ERAS-2025-025 | ERAS-2025-001 | 04 SOUTHEAST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 16.43% | 9932652 | 0.09603
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 23.04% | 9932652 | 0.03168
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 3.226% | 9932652 | 0.0132
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 5.3% | 9932652 | 0.01412
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 4.349% | 9932652 | 0.01271
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 635102.6427 | 10.53% | 6031219.88 | 0.20461
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 1044145.3249 | 17.31% | 6031219.88 | 0.21529
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 1374232.7921 | 22.79% | 6031219.88 | 0.22668
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 671050.943 | 11.13% | 6031219.88 | 0.22138
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 1128788.559 | 18.72% | 6031219.88 | 0.24244
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 892111.577 | 14.79% | 6031219.88 | 0.21022
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 285788.0413 | 4.738% | 6031219.88 | 0.16836
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-016 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-018 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-020 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-014 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-015 | ERAS-2025-001 CF | 03 CENTRAL | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-017 | ERAS-2025-001 CF | 03 CENTRAL | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-027 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-028 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-030 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-036 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-016 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-018 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-020 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-014 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-027 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-028 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-030 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-036 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 6031219.88 | N/A
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 7415154.7641 | 10.53% | 70417639.32 | 0.20461
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 12190941.5256 | 17.31% | 70417639.32 | 0.21529
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 16044884.9519 | 22.79% | 70417639.32 | 0.22668
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 7834869.9282 | 11.13% | 70417639.32 | 0.22138
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 13179195.4524 | 18.72% | 70417639.32 | 0.24244
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 10415868.1851 | 14.79% | 70417639.32 | 0.21022
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 3336724.5127 | 4.738% | 70417639.32 | 0.16836
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 170761 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | 14804258 | 100% | 14804258 | 1
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 170760 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | 3827454 | 100% | 3827454 | 1
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Comanche 345 kV New Substation | Current Study | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 16200000 | 100% | 16200000 | 0.33634
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-003 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 | N/A
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Current Study | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | 21600000 | 100% | 21600000 | 0.37149
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Contingent | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | 0 | 0% | 21600000 | N/A
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Comanche Tap-New Comanche 345 kV Ckt 1 New Line | Current Study | Build a 4 mile 345 kV Ckt 1 from Comanche Tap to the Comanche 345 kV New Substation | 15600000 | 100% | 15600000 | 0.0772
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 21293458.9114 | 52.31% | 40710000 | 0.04901
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 19416541.0886 | 47.69% | 40710000 | 0.04469
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 40710000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 40710000 | N/A
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | 9867000 | 100% | 9867000 | 0.11475
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | 0 | 0% | 9867000 | N/A
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | 12006000 | 100% | 12006000 | 0.10602
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | 0 | 0% | 12006000 | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502412 | ERIS | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 8836000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502412 | ERIS | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 8836000 | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502415 | ERIS | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 6112000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502415 | ERIS | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 6112000 | N/A
ERAS-2025-005 | ERAS-2025-001 | 04 SOUTHEAST | 170763 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | 15452461 | 100% | 15452461 | 1
ERAS-2025-005 | ERAS-2025-001 | 04 SOUTHEAST | 170762 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | 3790119 | 100% | 3790119 | 1
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502409 | NRIS | Duncan - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502409 | NRIS | Duncan - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502415 | NRIS | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 81256000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502415 | NRIS | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 81256000 | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502412 | NRIS | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502412 | NRIS | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502409 | ERIS | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 35100000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502409 | ERIS | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 35100000 | N/A
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 4691779.0822 | 52.31% | 8970000 | 0.04901
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 4278220.9178 | 47.69% | 8970000 | 0.04469
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 170578 | NRIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 8970000 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 170578 | NRIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 8970000 | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 503211 | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 16661900 | N/A
ERAS-2025-003 | ERAS-2025-001 CF | 04 SOUTHEAST | 503211 | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 16661900 | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 503211 | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 16661900 | N/A
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 | 0.08308
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 | 0.09855
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 | N/A
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 762377.5346 | 11.51% | 6621188 | 0.05787
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 1173512.3782 | 17.72% | 6621188 | 0.05701
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 1382752.0436 | 20.88% | 6621188 | 0.05374
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 731644.1079 | 11.05% | 6621188 | 0.05687
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 1103846.7881 | 16.67% | 6621188 | 0.05586
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 1032767.0549 | 15.6% | 6621188 | 0.05734
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 434288.0925 | 6.559% | 6621188 | 0.06028
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 1907420.3902 | 11.51% | 16565793.75 | 0.05787
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 2936053.7748 | 17.72% | 16565793.75 | 0.05701
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 3459558.1884 | 20.88% | 16565793.75 | 0.05374
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 1830527.2997 | 11.05% | 16565793.75 | 0.05687
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 2761754.8729 | 16.67% | 16565793.75 | 0.05586
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 2583917.8743 | 15.6% | 16565793.75 | 0.05734
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 1086561.3496 | 6.559% | 16565793.75 | 0.06028
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 157186 | NRIS | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Contingent | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 0 | 34.77% | 593064 | 0.04856
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 157186 | NRIS | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Contingent | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 0 | 65.23% | 593064 | 0.04858
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 58.56% | 3907935 | 0.02268
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 21.53% | 3907935 | 0.0083
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 4.869% | 3907935 | 0.01692
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 9.129% | 3907935 | 0.01692
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 5.919% | 3907935 | 0.01097
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 | 50% | 243120 | 0.02939
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 | 50% | 243120 | 0.03379
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 170757 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (Non-shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | 0 | 100% | 0 | 1
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 170756 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | 330000 | 100% | 330000 | 1
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 170765 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (NSNU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | 24611060 | 100% | 24611060 | 1
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 170764 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | 4055881 | 100% | 4055881 | 1
ERAS-2025-009 | ERAS-2025-001 | 04 SOUTHEAST | 170767 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (Non-shared NU) (GRDA) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | TBD | 100% | TBD | 1
ERAS-2025-009 | ERAS-2025-001 | 04 SOUTHEAST | 170766 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation | 2953500 | 100% | 2953500 | 1
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170771 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | 32764203 | 100% | 32764203 | 1
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170770 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | 3793557 | 100% | 3793557 | 1
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 170769 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | 0 | 100% | 0 | 1
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 170768 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | 0 | 100% | 0 | 1
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | 170772 | ERIS | Holcomb 345 kV Substation ERAS-2025-015 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015 (400MW/Hybrid), into Holcomb 345 kV Substation | 5238900 | 100% | 5238900 | 1
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 170806 | ERIS | Holcomb 345 kV Substation ERAS-2025-015/ERAS-2025-017 Interconnection (Shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015/ERAS-2025-017 (400/600MW/Hybrid/Thermal), into Holcomb 345 kV Substation | 23113320 | 60% | 38522200 | 1
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | 170806 | ERIS | Holcomb 345 kV Substation ERAS-2025-015/ERAS-2025-017 Interconnection (Shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015/ERAS-2025-017 (400/600MW/Hybrid/Thermal), into Holcomb 345 kV Substation | 15408880 | 40% | 38522200 | 1
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 170773 | ERIS | Holcomb 345 kV Substation ERAS-2025-017 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-017 (600MW/Thermal), into Holcomb 345 kV Substation | 5238900 | 100% | 5238900 | 1
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 170774 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004 (779MW/Thermal), into Horseshoe Lake 138kV Substation | 0 | 100% | 0 | 1
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 170807 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004/ERAS-2025-010 Interconnection (Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004/ERAS-2025-010 (779/496MW/Thermal/Thermal), into Horseshoe Lake 138kV Substation | 0 | 39.4% | 0 | 1
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 170807 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004/ERAS-2025-010 Interconnection (Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004/ERAS-2025-010 (779/496MW/Thermal/Thermal), into Horseshoe Lake 138kV Substation | 0 | 60.6% | 0 | 1
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 170775 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-010 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-010 (496MW/Thermal), into Horseshoe Lake 138kV Substation | 0 | 100% | 0 | 1
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | TBD | ERIS | Kummer Ridge 345 kV Capacitor Bank | Current Study | Install 300 MVAR Capacitor Bank at Kummer Ridge 345 kV substation | 10000000 | 50% | 20000000 | 0.01779
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | TBD | ERIS | Kummer Ridge 345 kV Capacitor Bank | Current Study | Install 300 MVAR Capacitor Bank at Kummer Ridge 345 kV substation | 10000000 | 50% | 20000000 | 0.01779
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 57045.3356 | 4.322% | 1320000 | 0.02928
ERAS-2025-003 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 55442.188 | 4.2% | 1320000 | 0.0332
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 222431.4331 | 16.85% | 1320000 | 0.03247
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 341124.5906 | 25.84% | 1320000 | 0.05269
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 144951.2626 | 10.98% | 1320000 | 0.03255
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 40955.8604 | 3.103% | 1320000 | 0.0286
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 59867.5434 | 4.535% | 1320000 | 0.02868
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 199257.8877 | 15.1% | 1320000 | 0.02983
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 198923.8987 | 15.07% | 1320000 | 0.02978
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | TBD | ERIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | 2139000 | 100% | 2139000 | 0.06574
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | 0 | 0% | 2139000 | N/A
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 170808 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011/ (750MW/Thermal), into Leland Olds 345kV Switchyard | 11450012 | 100% | 11450012 | 1
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 170778 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011 (750MW/Thermal), into Leland Olds 345kV Switchyard | 2927868 | 100% | 2927868 | 1
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 170821 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | 17000000 | 100% | 17000000 | 1
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 170779 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | 13000000 | 100% | 13000000 | 1
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 8.926% | 1366342009.8205 | 0.11172
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 25.47% | 1366342009.8205 | 0.20406
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 27.9% | 1366342009.8205 | 0.17881
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 8.204% | 1366342009.8205 | 0.10515
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 3.255% | 1366342009.8205 | 0.02716
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 21.94% | 1366342009.8205 | 0.20086
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 4.302% | 1366342009.8205 | 0.09847
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-016 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-018 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-020 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-014 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-027 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-028 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-030 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-036 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 | N/A
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 169968 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 0 | 0% | 1050598691 | 0.10841
ERAS-2025-015 | ERAS-2025-001 CF | 03 CENTRAL | 169968 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 0 | 0% | 1050598691 | N/A
ERAS-2025-017 | ERAS-2025-001 CF | 03 CENTRAL | 169968 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 0 | 0% | 1050598691 | N/A
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 170781 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | 4641893 | 100% | 4641893 | 1
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 170780 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | 2743634 | 100% | 2743634 | 1
ERAS-2025-022 | ERAS-2025-001 | 04 SOUTHEAST | 170783 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (Non-shared NU) (PEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | 1165190 | 100% | 1165190 | 1
ERAS-2025-022 | ERAS-2025-001 | 04 SOUTHEAST | 170782 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (TOIF) (PEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | 2573308 | 100% | 2573308 | 1
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | 170809 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | 2122145 | 100% | 2122145 | 1
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | 170819 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007/013 Interconnection (Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007/013 (450.6/450.6MW/Thermal/Thermal), into Mullin Creek 345 kV Substation | 10947387 | 50% | 21894774 | 1
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | 170819 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007/013 Interconnection (Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007/013 (450.6/450.6MW/Thermal/Thermal), into Mullin Creek 345 kV Substation | 10947387 | 50% | 21894774 | 1
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | 170810 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-013 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-013 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | 1765342 | 100% | 1765342 | 1
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 | 0.18975
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 | 0.21266
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | 0 | 0% | 61120000 | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | 0 | 0% | 61120000 | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 501015 | NRIS | NE 10th - Reno 138 kV Line Rebuild | Contingent | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 0 | 0% | 8392000 | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 501015 | NRIS | NE 10th - Reno 138 kV Line Rebuild | Contingent | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 0 | 0% | 8392000 | N/A
ERAS-2025-029 | ERAS-2025-001 | 03 CENTRAL | 170812 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (Non-shared NU) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | 3159667 | 100% | 3159667 | 1
ERAS-2025-029 | ERAS-2025-001 | 03 CENTRAL | 170811 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (TOIF) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | 0 | 100% | 0 | 1
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 170755 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | 20961370 | 100% | 20961370 | 1
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 170754 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | 3550583 | 100% | 3550583 | 1
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 170785 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (Non-shared NU) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | 6595300 | 100% | 6595300 | 1
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 170784 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (TOIF) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | 1035871 | 100% | 1035871 | 1
ERAS-2025-023 | ERAS-2025-001 | 04 SOUTHEAST | 170787 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | 3862241 | 100% | 3862241 | 1
ERAS-2025-023 | ERAS-2025-001 | 04 SOUTHEAST | 170786 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | 5406476 | 100% | 5406476 | 1
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 170791 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | 17180394 | 100% | 17180394 | 1
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 170790 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | 3113165 | 100% | 3113165 | 1
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 170793 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | 24133953 | 100% | 24133953 | 1
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 170792 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | 5236562 | 100% | 5236562 | 1
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 13.81% | 224939250 | 0.12984
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 20.82% | 224939250 | 0.12531
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 10.85% | 224939250 | 0.05225
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 12.1% | 224939250 | 0.11655
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 15.22% | 224939250 | 0.09543
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 18.74% | 224939250 | 0.12893
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 8.455% | 224939250 | 0.14539
ERAS-2025-031 | ERAS-2025-001 | 03 CENTRAL | 170814 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (Non-shared NU) (KC BPU) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | 2548040 | 100% | 2548040 | 1
ERAS-2025-031 | ERAS-2025-001 | 03 CENTRAL | 170813 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (TOIF) (KC BPU) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | 0 | 100% | 0 | 1
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1 | Current Study | Rebuild the existing SEWARD 3 to ST-JOHN3 115 kV line 1 (14.69 miles) to a minimum rating of 115 MVA | 5108640.2743 | 34.78% | 14690000 | 0.43225
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1 | Current Study | Rebuild the existing SEWARD 3 to ST-JOHN3 115 kV line 1 (14.69 miles) to a minimum rating of 115 MVA | 9581359.7257 | 65.22% | 14690000 | 0.43237
ERAS-2025-003 | ERAS-2025-001 | 04 SOUTHEAST | 170795 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (Non-shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | 0 | 100% | 0 | 1
ERAS-2025-003 | ERAS-2025-001 | 04 SOUTHEAST | 170794 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | 0 | 100% | 0 | 1
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 170816 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (Non-shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | 9918207 | 100% | 9918207 | 1
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 170815 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | 2118099 | 100% | 2118099 | 1
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1 | Current Study | Replace the existing SEWRDMW3 to SEWARD 2 115-69 kV transformer 1 with a minimum rating of 55 MVA | 2086505.3399 | 34.78% | 6000000 | 0.09048
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1 | Current Study | Replace the existing SEWRDMW3 to SEWARD 2 115-69 kV transformer 1 with a minimum rating of 55 MVA | 3913494.6601 | 65.22% | 6000000 | 0.09051
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 4820459.721 | 39.51% | 12200000 | 0.07316
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 4820459.721 | 39.51% | 12200000 | 0.07316
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 684920.966 | 5.614% | 12200000 | 0.01171
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 1027381.449 | 8.421% | 12200000 | 0.01171
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 118501.2705 | 0.9713% | 12200000 | 0.01013
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 222189.8821 | 1.821% | 12200000 | 0.01013
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 237762.9143 | 1.949% | 12200000 | 0.01084
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | TBD | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 268324.0761 | 2.199% | 12200000 | 0.00734
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | TBD | ERIS | Replacement of two disconnect switches at Antelope Valley Station | Current Study | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | 125000 | 50% | 250000 | 0.12488
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | TBD | ERIS | Replacement of two disconnect switches at Antelope Valley Station | Current Study | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | 125000 | 50% | 250000 | 0.12488
ERAS-2025-035 | ERAS-2025-001 | 01 NORTH | 170789 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (Non-shared NU) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | TBD | 100% | TBD | 1
ERAS-2025-035 | ERAS-2025-001 | 01 NORTH | 170788 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (TOIF) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | TBD | 100% | TBD | 1
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 170805 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (Non-shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | 300000 | 100% | 300000 | 1
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 170804 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | 1809896 | 100% | 1809896 | 1
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 170777 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/thermal), into State Line 439 161 kV Substation | 28031567.78 | 100% | 28031567.78 | 1
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 170776 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/Thermal), into State Line 439 161 kV Substation | 1434591.61 | 100% | 1434591.61 | 1
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 170797 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | 2030268 | 100% | 2030268 | 1
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 170796 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | 3809606 | 100% | 3809606 | 1
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV CKT 1 Transformer Replacement | Current Study | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | 8302968 | 100% | 8302968 | 0.18
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | NRIS | Trosper - Reno 138 kV Line Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | N/A
ERAS-2025-003 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | NRIS | Trosper - Reno 138 kV Line Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | NRIS | Trosper - Reno 138 kV Line Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | N/A
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | 0.12074
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | 0.12339
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 | N/A
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 170799 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | 1433543 | 100% | 1433543 | 1
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 170798 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | 2868488 | 100% | 2868488 | 1
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 170818 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (Non-shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | 6901474 | 100% | 6901474 | 1
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 170817 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | 737202 | 100% | 737202 | 1
ERAS-2025-025 | ERAS-2025-001 | 04 SOUTHEAST | 170801 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | 17000000 | 100% | 17000000 | 1
ERAS-2025-025 | ERAS-2025-001 | 04 SOUTHEAST | 170800 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | 2000018 | 100% | 2000018 | 1
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 170803 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | 0 | 100% | 0 | 1
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 170802 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | 0 | 100% | 0 | 1
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | YOAKUM to BRU SUB 230 kV Line Rebuild | Current Study | Rebuild 5.35 miles YOAKUM to BRU_SUB 230 kV line to a minimum of 665 MVA | 4726773.15 | 100% | 4726773.15 | 0.69393
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | YOAKUM to MUSTANG 230 kV Line Rebuild | Current Study | Rebuild 15.65 miles YOAKUM to MUSTANG 230 kV line to a minimum of 620 MVA | 13826915.85 | 100% | 13826915.85 | 0.15548
Total | [7 empty] | 784546773.71

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Replacement of two disconnect switches at Antelope Valley Station | TBD | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | BEPC | TBD (36-month lead time) | 250000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | TBD | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | KCPL | TBD (36-month lead time) | 1320000
Contingent | ERAS-2025-001 | Steady State | 03 CENTRAL | 2024 ITP | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 169968 | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | SUNC | 4784800% | 1050598691
Model Correction | ERAS-2025-001 | Steady State | 03 CENTRAL | 2021 ITP | ERIS | Joplin West 7th - Stateline 161 kV Line (Model Correction) | 92143 | Rebuild approximately 5.5 miles of the existing 161 kV line from Joplin West 7th to Stateline to 558 MVA. | EMDE | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | TBD | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | AEPW | TBD (36-month lead time) | 21600000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 345 kV New Substation | TBD | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | AEPW | TBD (36-month lead time) | 16200000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche Tap-New Comanche 345 kV Ckt 1 New Line | TBD | Build a 4 mile 345 kV Ckt 1 from Comanche Tap to the Comanche 345 kV New Substation | AEPW | TBD (36-month lead time) | 15600000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | AEPW | TBD (36-month lead time) | 12006000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | AEPW | TBD (36-month lead time) | 9867000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | AEPW | TBD (36-month lead time) | 2139000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36-month lead time) | 8970000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36-month lead time) | 40710000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | 500030 | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 9044000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | 500003 | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 6178000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Multi - Horseshoe Lake Reconfiguration | 900189 | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | OKGE | TBD (36-month lead time) | 61120000
Model Correction | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | ERAS-2025-004 and ERAS-2025-010 Model Correction | N/A | Turn on the auxillary loads at ERAS-2025-004 and ERAS-2025-010 | OKGE | N/A | 0
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | 500030 | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 9044000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | 500003 | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 6178000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Multi - Horseshoe Lake Reconfiguration | 900189 | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | OKGE | TBD (36-month lead time) | 61120000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild | 502409 | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | AEPW | TBD (36-month lead time) | 35100000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild | 502412 | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | AEPW | TBD (36-month lead time) | 8836000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild | 502415 | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | AEPW | TBD (36-month lead time) | 6112000
Contingent | ERAS-2025-001 | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | TBD | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | SPS | TBD (36-month lead time) | 1366342009.8205
Contingent | ERAS-2025-001 | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | 170066, 170093 | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | OKGE/SPS | TBD (36-month lead time) | 224939250
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | TBD | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | AEPW | TBD (36-month lead time) | 6031219.88
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | TBD | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | AEPW | TBD (36-month lead time) | 70417639.32
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | ELKCITY 230/138 kV Transformer Replacement | TBD | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | AEPW | TBD (36-month lead time) | 6621188
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | TBD | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | AEPW | TBD (36-month lead time) | 16565793.75
Model Correction | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction) | TBD | Correct the Mcdowel Creek to Potter County 230 kV Line rating to SN/SE 497.2/547 MVA. | SPS | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tolk 345/230 kV CKT 1 Transformer Replacement | TBD | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | SPS | TBD (36-month lead time) | 8302968
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade | TBD | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to XTO_MAHONEY 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | SPS | TBD (36-month lead time) | 4081811.58
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade | TBD | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to MUSTANG 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | SPS | TBD (36-month lead time) | 3136456.95
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | YOAKUM to BRU SUB 230 kV Line Rebuild | TBD | Rebuild 5.35 miles YOAKUM to BRU_SUB 230 kV line to a minimum of 665 MVA | SPS | TBD (36-month lead time) | 4726773.15
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | YOAKUM to MUSTANG 230 kV Line Rebuild | TBD | Rebuild 15.65 miles YOAKUM to MUSTANG 230 kV line to a minimum of 620 MVA | SPS | TBD (36-month lead time) | 13826915.85
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | BRU SUB to XTO MAHONEY 230 kV Line Rebuild | TBD | Rebuild 1.76 miles BRU_SUB to XTO_MAHONEY 230 kV line to a minimum of 680 MVA | SPS | TBD (36-month lead time) | 1554975.84
Contingent | ERAS-2025-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Andrews to Road Runner 345 kV Line | 170597 | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | SPS | TBD (36-month lead time) | 73524573
Current Study | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Kummer Ridge 345 kV Capacitor Bank | TBD | Install 300 MVAR Capacitor Bank at Kummer Ridge 345 kV substation | BEPC | TBD (60-month lead time) | 20000000
Model Correction | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Antelope Valley Station – Leland Old 345 kV Ckt 1 and Ckt 2 Model Correction | TBD | Correct the Antelope Valley Station – Leland Old 345 kV Ckt 1 and Ckt 2 Summer Ratings to 1127 (summer normal)/1195 (summer emergency) and Winter Ratings to 1195 (winter normal)/1195 (winter emergency) | BEPC | N/A | 0
Model Correction | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | NRIS | Roadrunner 345/115 kV transformer #2 Model Correction | TBD | Model correction on the Roadrunner 345/115 kV transformer #2 | SPS | N/A | 0
Model Correction | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | NRIS | Roadrunner 345/115 kV transformer #3 Model Correction | TBD | Model correction on the Roadrunner 345/115 kV transformer #3 | SPS | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | TBD | Build a new CARTHAG5 to CARTHG 2 161-69 kV transformer 3 with a rating of 84 MVA | SWPA | TBD (36-month lead time) | 6075000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | TBD | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | SUNC | TBD (36-month lead time) | 15000000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST/05 SOUTHWEST | DPA-2017-December-815 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | 82115 | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | WFEC | 4644600% | 9932652
Model Correction | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update | TBD | Update the existing S.W.S.-4 to NORGE--4 138 kV line 1 (22.35 miles) to a rating of 366 MVA | AEPW | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | TBD | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | N/A | TBD (36-month lead time) | 12200000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1 | TBD | Replace the existing SEWRDMW3 to SEWARD 2 115-69 kV transformer 1 with a minimum rating of 55 MVA | MIDW | TBD (36-month lead time) | 6000000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1 | TBD | Rebuild the existing SEWARD 3 to ST-JOHN3 115 kV line 1 (14.69 miles) to a minimum rating of 115 MVA | SUNC | TBD (36-month lead time) | 14690000
Model Correction | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update | TBD | Update the existing SEWRDMW3 to SEWARD 3 115 kV line 1 (2.91 miles) to a rating of 60 MVA | MIDW | N/A | 0
Contingent | ERAS-2025-001 | Steady State | 03 CENTRAL | 2024 ITP | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | 159449 | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | EKC | 4711800% | 3907935
Contingent | ERAS-2025-001 | Steady State | 03 CENTRAL | 2023 ITP | NRIS | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | 157186 | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | SEPC | 4656800% | 593064
Contingent | ERAS-2025-001 | Steady State | 01 NORTH | 2022 ITP | NRIS | Fargo 230 kV Terminal Upgrade | 156282 | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | WAPA | 2025-12-31 (Delayed) | 243120
Model Correction | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | NRIS | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update | TBD | Update the existing ANTELOPE-BE3 to CHARL_CK-BE3 345 kV line 1 (69.9 miles) to a rating of 1195 MVA | BEPC-SPP | N/A | 0
Interconnection | ERAS-2025-001 | Steady State | 02 NEBRASKA | ERAS-2025-001 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (Non-shared NU) (LES) | 170753 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | LES | 36 | 0
Interconnection | ERAS-2025-001 | Steady State | 02 NEBRASKA | ERAS-2025-001 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (TOIF) (LES) | 170752 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | LES | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (Non-shared NU) (SPS) | 170803 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | SPS | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (TOIF) (SPS) | 170802 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | SPS | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (Non-shared NU) (OGE) | 170795 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | OKGE | 6 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (TOIF) (OGE) | 170794 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | OKGE | 6 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004 Interconnection (TOIF) (OGE) | 170774 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004 (779MW/Thermal), into Horseshoe Lake 138kV Substation | OKGE | 24 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004/ERAS-2025-010 Interconnection (Shared NU) (OGE) | 170807 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004/ERAS-2025-010 (779/496MW/Thermal/Thermal), into Horseshoe Lake 138kV Substation | OKGE | 24 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (Non-shared NU) (AEP) | 170763 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | AEPW | 36 | 15452461
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (TOIF) (AEP) | 170762 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | AEPW | 36 | 3790119
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007 Interconnection (TOIF) (Evergy) | 170809 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | Evergy | 48 | 2122145
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-013 Interconnection (TOIF) (Evergy) | 170810 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-013 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | Evergy | 36 | 1765342
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (TOIF) (Evergy) | 170815 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | Evergy | 24 | 2118099
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (Non-shared NU) (Evergy) | 170816 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | Evergy | 24 | 9918207
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (TOIF) (Evergy) | 170817 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | Evergy | 12 | 737202
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (Non-shared NU) (Evergy) | 170818 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | Evergy | 12 | 6901474
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (Non-shared NU) (GRDA) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 170767 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | GRDA | TBD (36-month lead time) | TBD
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (TOIF) (GRDA) | 170766 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation | GRDA |  | 2953500
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-010 Interconnection (TOIF) (OGE) | 170775 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-010 (496MW/Thermal), into Horseshoe Lake 138kV Substation | OKGE | 24 | 0
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (TOIF) (BEPC) | 170778 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011 (750MW/Thermal), into Leland Olds 345kV Switchyard | BEPC | 60 | 2927868
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (Non-Shared NU) (BEPC) | 170821 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | BEPC | 60 | 17000000
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (Non-Shared NU) (BEPC) | 170808 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011/ (750MW/Thermal), into Leland Olds 345kV Switchyard | BEPC | 60 | 11450012
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (TOIF) (BEPC) | 170779 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | BEPC | 60 | 13000000
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007/013 Interconnection (Shared NU) (Evergy) | 170819 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007/013 (450.6/450.6MW/Thermal/Thermal), into Mullin Creek 345 kV Substation | Evergy | 48 | 21894774
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (Non-shared NU) (SPS) | 170769 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | SPS | 18 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (TOIF) (SPS) | 170768 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | SPS | 18 | 0
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Holcomb 345 kV Substation ERAS-2025-015 Interconnection (TOIF) (SEPC) | 170772 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015 (400MW/Hybrid), into Holcomb 345 kV Substation | SEPC | 60 | 5238900
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Holcomb 345 kV Substation ERAS-2025-015/ERAS-2025-017 Interconnection (Shared NU) (SEPC) | 170806 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015/ERAS-2025-017 (400/600MW/Hybrid/Thermal), into Holcomb 345 kV Substation | SEPC | 60 | 38522200
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (Non-shared NU) (SPS) | 170797 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | SPS | 40 | 2030268
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (TOIF) (SPS) | 170796 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | SPS | 40 | 3809606
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Holcomb 345 kV Substation ERAS-2025-017 Interconnection (TOIF) (SEPC) | 170773 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-017 (600MW/Thermal), into Holcomb 345 kV Substation | SEPC | 60 | 5238900
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (Non-shared NU) (SPS) | 170791 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | SPS | 60 | 17180394
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (TOIF) (SPS) | 170790 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | SPS | 60 | 3113165
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (Non-shared NU) (MIDW) | 170785 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | MIDW | 30 | 6595300
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (TOIF) (MIDW) | 170784 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | MIDW | 30 | 1035871
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (Non-shared NU) (SPS) | 170771 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | SPS | 60 | 32764203
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (TOIF) (SPS) | 170770 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | SPS | 60 | 3793557
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (Non-shared NU) (SPS) | 170759 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | SPS | 60 | 28993147
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (TOIF) (SPS) | 170758 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | SPS | 60 | 3817643
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (Non-shared NU) (PEC) | 170783 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | PEC | 52 | 1165190
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (TOIF) (PEC) | 170782 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | PEC | 52 | 2573308
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (Non-shared NU) (AEP) | 170787 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | AEPW | 36 | 3862241
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (TOIF) (AEP) | 170786 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | AEPW | 36 | 5406476
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (Non-shared NU) (AEP) | 170761 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | AEPW | 36 | 14804258
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (TOIF) (AEP) | 170760 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | AEPW | 36 | 3827454
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (Non-shared NU) (WFEC) | 170801 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | WFEC | 66 | 17000000
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (TOIF) (WFEC) | 170800 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | WFEC | 66 | 2000018
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (Non-shared NU) (AEP) | 170793 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | AEPW | 42 | 24133953
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (TOIF) (AEP) | 170792 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | AEPW | 42 | 5236562
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (Non-shared NU) (SPS) | 170781 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | SPS | 30 | 4641893
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (TOIF) (SPS) | 170780 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | SPS | 30 | 2743634
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (Non-shared NU) (SPS) | 170799 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | SPS | 60 | 1433543
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (TOIF) (SPS) | 170798 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | SPS | 60 | 2868488
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (Non-shared NU) (KACY) | 170812 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | KACY | 20 | 3159667
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (TOIF) (KACY) | 170811 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | KACY | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (NSNU) (SPS) | 170765 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | SPS | 60 | 24611060
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (TOIF) (SPS) | 170764 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | SPS | 60 | 4055881
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (Non-shared NU) (KC BPU) | 170814 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | KC BPU | 20 | 2548040
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (TOIF) (KC BPU) | 170813 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | KC BPU | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (Non-shared NU) (SEPC) | 170805 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | SEPC | 40 | 300000
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (TOIF) (SEPC) | 170804 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | SEPC | 40 | 1809896
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (Non-shared NU) (SEPC) | 170757 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | SEPC | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (TOIF) (SEPC) | 170756 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | SEPC | 40 | 330000
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (Non-shared NU) (EDE) | 170777 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/thermal), into State Line 439 161 kV Substation | EDE | 54 | 28031567.78
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (TOIF) (EDE) | 170776 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/Thermal), into State Line 439 161 kV Substation | EDE | 54 | 1434591.61
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (Non-shared NU) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 170789 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | NWPS | TBD (36-month lead time) | TBD
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (TOIF) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 170788 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | NWPS | TBD (36-month lead time) | TBD
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (Non-shared NU) (SPS) | 170755 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | SPS | 48 | 20961370
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (TOIF) (SPS) | 170754 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | SPS | 48 | 3550583
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST/05 SOUTHWEST | ERAS-2025-001 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | TBD | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | AEPW | TBD (36 month lead time) | 6031219.88
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST/05 SOUTHWEST | ERAS-2025-001 | NRIS | Comanche 345 kV New Substation | TBD | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | AEPW | TBD (36 month lead time) | 16200000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | TBD | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | AEPW | TBD (36 month lead time) | 21600000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36 month lead time) | 40710000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | AEPW | TBD (36 month lead time) | 9867000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | AEPW | TBD (36 month lead time) | 12006000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Duncan - Duncan Tap 138 kV Line Rebuild | 502409 | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | AEPW | 4616300% | 81256000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | 502415 | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | AEPW | 4616300% | 81256000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | 502412 | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | AEPW | 4616300% | 81256000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | DISIS-2020-001 | NRIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | 170578 | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36 month lead time) | 8970000
Contingent | ERAS-2025-001 CF | Steady State | 03 CENTRAL | 2024 ITP | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 169968 | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | SEPC/TSGT/ITC GP | 4784800% | 1050598691
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | AEPW | TBD (36 month lead time) | 2139000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST/05 SOUTHWEST | 2025 ITP | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | TBD | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | SPS | 4780500% | 1366342009.8205
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | 503211 | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | OKGE | 4690500% | 16661900
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Multi - Horseshoe Lake Reconfiguration | TBD | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | OKGE | 4727000% | 61120000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Multi - Horseshoe Lake Reconfiguration | TBD | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | OKGE | 4727000% | 61120000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | NE 10th - Reno 138 kV Line Rebuild | 501015 | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | OKGE | 4727000% | 8392000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Trosper - Reno 138 kV Line Rebuild | 500003 | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | OKGE | 4727000% | 6178000
6649063889.231

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 27L and 27SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
ERAS-2025-011 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03308 | 4675200% | 224639813 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03308 | 4675200% | 16186000 | 0
ERAS-2025-011 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001 | Yes | Yes | 0.12556 | TBD (36 month lead time) | 5906325 | 5906325
ERAS-2025-011 | 01 NORTH | ERIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | Yes | 0.06365 | TBD (36 month lead time) | 1101824 | 1101824
ERAS-2025-011 | 01 NORTH | NRIS | TBD | TBD | Replacement of two disconnect switches at Antelope Valley Station | Replacement of two disconnect switches at Antelope Valley Station | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | ERAS-2025-001 | No | Yes | 0.12168 | TBD (36 month lead time) | 250000 | 250000
ERAS-2025-011 | 01 NORTH | ERIS | TBD | TBD | Bison - Hankinson - Big Stone South 345 kV | Bison - Hankinson - Big Stone South 345 kV | Add two 345/230 kV transformers at the existing Hankinson 230 kV substation. Build a new 72 mile 345 kV line between Hankinson 345 kV substation and Bigstone South 345 kV substation. Build a new 75 mile 345 kV line between Hankinson 345 kV substation and Bison 345 kV substation. | JTIQ Upgrade | Yes | Yes | 0.03781 | 4894500% | 476000000 | 0
ERAS-2025-011 | 01 NORTH | ERIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.07839 | 4821400% | 331000000 | 0
ERAS-2025-011 | 01 NORTH | NRIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.04033 | 4821400% | 331000000 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06997 | 4851900% | 368295711 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0628 | 4851900% | 368295711 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03172 | 4851900% | 368295711 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03084 | 4851900% | 368295711 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07022 | 4851900% | 368295711 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07022 | 4851900% | 368295711 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03838 | 4845800% | 162439000 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06828 | 4845800% | 162439000 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04471 | 4858000% | 3376000 | 0
ERAS-2025-011 | 01 NORTH | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04374 | 4858000% | 3376000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03308 | 4675200% | 224639813 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03308 | 4675200% | 16186000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001 | Yes | Yes | 0.1167 | TBD (36 month lead time) | 5906325 | 5906325
ERAS-2025-012 | 01 NORTH | ERIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | Yes | 0.06362 | TBD (36 month lead time) | 1101824 | 1101824
ERAS-2025-012 | 01 NORTH | NRIS | TBD | TBD | Replacement of two disconnect switches at Antelope Valley Station | Replacement of two disconnect switches at Antelope Valley Station | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | ERAS-2025-001 | No | Yes | 0.1014 | TBD (36 month lead time) | 250000 | 250000
ERAS-2025-012 | 01 NORTH | ERIS | TBD | TBD | Bison - Hankinson - Big Stone South 345 kV | Bison - Hankinson - Big Stone South 345 kV | Add two 345/230 kV transformers at the existing Hankinson 230 kV substation. Build a new 72 mile 345 kV line between Hankinson 345 kV substation and Bigstone South 345 kV substation. Build a new 75 mile 345 kV line between Hankinson 345 kV substation and Bison 345 kV substation. | JTIQ Upgrade | Yes | Yes | 0.04197 | 4894500% | 476000000 | 0
ERAS-2025-012 | 01 NORTH | NRIS | TBD | TBD | Bison - Hankinson - Big Stone South 345 kV | Bison - Hankinson - Big Stone South 345 kV | Add two 345/230 kV transformers at the existing Hankinson 230 kV substation. Build a new 72 mile 345 kV line between Hankinson 345 kV substation and Bigstone South 345 kV substation. Build a new 75 mile 345 kV line between Hankinson 345 kV substation and Bison 345 kV substation. | JTIQ Upgrade | Yes | Yes | 0.03258 | 4894500% | 476000000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.07886 | 4821400% | 331000000 | 0
ERAS-2025-012 | 01 NORTH | NRIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.0408 | 4821400% | 331000000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06971 | 4851900% | 368295711 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06292 | 4851900% | 368295711 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03167 | 4851900% | 368295711 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0308 | 4851900% | 368295711 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07016 | 4851900% | 368295711 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07016 | 4851900% | 368295711 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03772 | 4845800% | 162439000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06813 | 4845800% | 162439000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0304 | 4845800% | 162439000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04475 | 4858000% | 3376000 | 0
ERAS-2025-012 | 01 NORTH | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04355 | 4858000% | 3376000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03266 | 4675200% | 224639813 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03266 | 4675200% | 16186000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | Yes | 0.06783 | TBD (36 month lead time) | 1101824 | 1101824
ERAS-2025-035 | 01 NORTH | ERIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.10019 | 4821400% | 331000000 | 0
ERAS-2025-035 | 01 NORTH | NRIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.06217 | 4821400% | 331000000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07332 | 4851900% | 368295711 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06745 | 4851900% | 368295711 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03356 | 4851900% | 368295711 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03263 | 4851900% | 368295711 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07458 | 4851900% | 368295711 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07458 | 4851900% | 368295711 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03489 | 4845800% | 162439000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06878 | 4845800% | 162439000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03389 | 4845800% | 162439000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04533 | 4858000% | 3376000 | 0
ERAS-2025-035 | 01 NORTH | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04392 | 4858000% | 3376000 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.13736 | 4748300% | 2849669 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.13736 | 4748300% | 6114594 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220745 | 157385 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 - 70th & Bluff 161 kV Ckt 1 Rebuild (LES) | Rebuild 17.7 miles of 161 kV Ckt 1 line from Sub 1214 161 kV substation to 70th & Bluff161 kV substation with a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.13736 | 4717800% | 1453879 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | TBD | TBD | Lyons Co – Lakefield 345 kV | Lyons Co – Lakefield 345 kV | Build a new 80 mile 345 kV line between Lyon County 345 kV substation and Lakefield 345 kV Substation | JTIQ Upgrade | Yes | Yes | 0.05638 | 4821400% | 331000000 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07896 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05072 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05072 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.08196 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.12796 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.11013 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.11013 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05059 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04919 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03549 | 4851900% | 368295711 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.13269 | 4845800% | 162439000 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0969 | 4845800% | 162439000 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03579 | 4845800% | 162439000 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.07791 | 4845800% | 162439000 | 0
ERAS-2025-001 | 02 NEBRASKA | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05355 | 4845800% | 162439000 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.04741 | 4858000% | 3376000 | 0
ERAS-2025-001 | 02 NEBRASKA | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.06777 | 4858000% | 3376000 | 0
ERAS-2025-006 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.08278 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-006 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05442 | 4845800% | 162439000 | 0
ERAS-2025-006 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05035 | 4845800% | 162439000 | 0
ERAS-2025-006 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03092 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05385 | 4851900% | 368295711 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0558 | 4851900% | 368295711 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05521 | 4851900% | 368295711 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05521 | 4851900% | 368295711 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05407 | 4845800% | 162439000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.08238 | 4845800% | 162439000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.11077 | 4845800% | 162439000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.1146 | 4845800% | 162439000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.06265 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.06265 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.13418 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.15119 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.43862 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.09061 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07315 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07315 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.18068 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.4628 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.17244 | 4858000% | 3376000 | 0
ERAS-2025-007 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03653 | 4858000% | 3376000 | 0
ERAS-2025-008 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.11581 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-008 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04152 | 4845800% | 162439000 | 0
ERAS-2025-008 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03903 | 4858000% | 3376000 | 0
ERAS-2025-008 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03443 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05385 | 4851900% | 368295711 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0558 | 4851900% | 368295711 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05521 | 4851900% | 368295711 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05521 | 4851900% | 368295711 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05407 | 4845800% | 162439000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.08238 | 4845800% | 162439000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.11077 | 4845800% | 162439000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.1146 | 4845800% | 162439000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.06265 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.06265 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.13418 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.15119 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.43862 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.09061 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07315 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07315 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.18068 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.4628 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.17244 | 4858000% | 3376000 | 0
ERAS-2025-013 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03653 | 4858000% | 3376000 | 0
ERAS-2025-015 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04492 | 4675200% | 224639813 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04954 | 4675200% | 224639813 | 0
ERAS-2025-015 | 03 CENTRAL | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04235 | 4675200% | 254838000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04841 | 4675200% | 254838000 | 0
ERAS-2025-015 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04492 | 4675200% | 16186000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04954 | 4675200% | 16186000 | 0
ERAS-2025-015 | 03 CENTRAL | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04235 | 4675200% | 842000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.0993 | 4784800% | 1050598691 | 0
ERAS-2025-015 | 03 CENTRAL | ERIS | 900026 | 500080 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | Yes | 0.04313 | 4707500% | 81824362.95 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 900026 | 500080 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | Yes | 0.04154 | 4707500% | 81824362.95 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.03122 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-015 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.06993 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-015 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03231 | 4845800% | 162439000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06682 | 4845800% | 162439000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05859 | 4845800% | 162439000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03545 | 4858000% | 3376000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03383 | 4858000% | 3376000 | 0
ERAS-2025-015 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03475 | 4858000% | 3376000 | 0
ERAS-2025-017 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04991 | 4675200% | 224639813 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04954 | 4675200% | 224639813 | 0
ERAS-2025-017 | 03 CENTRAL | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04721 | 4675200% | 254838000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04841 | 4675200% | 254838000 | 0
ERAS-2025-017 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04991 | 4675200% | 16186000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04954 | 4675200% | 16186000 | 0
ERAS-2025-017 | 03 CENTRAL | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04721 | 4675200% | 842000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.0993 | 4784800% | 1050598691 | 0
ERAS-2025-017 | 03 CENTRAL | ERIS | 900026 | 500080 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | Yes | 0.04177 | 4707500% | 81824362.95 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 900026 | 500080 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | Yes | 0.04154 | 4707500% | 81824362.95 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.03122 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-017 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.06993 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-017 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03677 | 4845800% | 162439000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.06682 | 4845800% | 162439000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05859 | 4845800% | 162439000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03545 | 4858000% | 3376000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03383 | 4858000% | 3376000 | 0
ERAS-2025-017 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03475 | 4858000% | 3376000 | 0
ERAS-2025-019 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.07862 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-019 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04009 | 4845800% | 162439000 | 0
ERAS-2025-019 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04382 | 4845800% | 162439000 | 0
ERAS-2025-019 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03064 | 4858000% | 3376000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10206 | 4617400% | 1329162 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10514 | 4617400% | 1329162 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10206 | 4617400% | 1329161 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10514 | 4617400% | 1329161 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | TBD | TBD | Nashua 345/161 kV Ckt 2 Transformer | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.06164 | 4633800% | 24750244 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | TBD | TBD | Nashua 345/161 kV Ckt 2 Transformer | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.0568 | 4633800% | 24750244 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503666 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jaggard Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jaggard Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03455 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503666 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jaggard Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jaggard Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03518 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503668 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jarbalo Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jarbalo Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03455 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503668 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jarbalo Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jarbalo Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03518 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503673 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 53rd & Mund 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at 53rd & Mund 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.11114 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503673 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 53rd & Mund 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at 53rd & Mund 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.10955 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900341 | 502741 | Line - Crosstown - Blue Valley Station 161 kV New Line | Crosstown - Blue Valley Station 161 kV New Line | Build a 5.63-mile 161 kV Ckt 1 line from Crosstown to Blue Valley Station | 2025 ITP | Yes | Yes | 0.06883 | 4725600% | 21642007.4341 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900341 | 502741 | Line - Crosstown - Blue Valley Station 161 kV New Line | Crosstown - Blue Valley Station 161 kV New Line | Build a 5.63-mile 161 kV Ckt 1 line from Crosstown to Blue Valley Station | 2025 ITP | Yes | Yes | 0.0661 | 4725600% | 21642007.4341 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503667 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jaggard Jct. 115 kV Ckt 1 Terminal Upgrade toward 166th Street 115 kV | Upgrade terminal equipment at Jaggard Jct. 115 kV substation for Ckt 1 toward 166th Street 115 kV | 2025 ITP | Yes | Yes | 0.03518 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503670 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jaggard Jct. 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at Jaggard Jct. 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.03455 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503670 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jaggard Jct. 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at Jaggard Jct. 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.03518 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503669 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jarbalo Jct. 115 kV Ckt 1 Terminal Upgrade toward 166th Street 115 kV | Upgrade terminal equipment at Jarbalo Jct. 115 kV substation for Ckt 1 toward 166th Street 115 kV | 2025 ITP | Yes | Yes | 0.03455 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503669 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jarbalo Jct. 115 kV Ckt 1 Terminal Upgrade toward 166th Street 115 kV | Upgrade terminal equipment at Jarbalo Jct. 115 kV substation for Ckt 1 toward 166th Street 115 kV | 2025 ITP | Yes | Yes | 0.03518 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503672 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Pentagon 115 kV Ckt 1 Terminal Upgrade toward 53rd & Mund 115 kV | Upgrade terminal equipment at Pentagon 115 kV substation for Ckt 1 toward 53rd & Mund 115 kV | 2025 ITP | Yes | Yes | 0.11114 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 900393 | 503672 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Pentagon 115 kV Ckt 1 Terminal Upgrade toward 53rd & Mund 115 kV | Upgrade terminal equipment at Pentagon 115 kV substation for Ckt 1 toward 53rd & Mund 115 kV | 2025 ITP | Yes | Yes | 0.10955 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 900393 | 503671 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Pentagon 115 kV Ckt 1 Terminal Upgrade toward Jaggard Jct. 115 kV | Upgrade terminal equipment at Pentagon 115 kV substation for Ckt 1 toward Jaggard Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03455 | 4652500% | 16800000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05795 | 4845800% | 162439000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04002 | 4845800% | 162439000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04187 | 4845800% | 162439000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.11499 | 4858000% | 3376000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.05316 | 4858000% | 3376000 | 0
ERAS-2025-029 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07787 | 4858000% | 3376000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07608 | 4858000% | 3376000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03396 | 4858000% | 3376000 | 0
ERAS-2025-029 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03205 | 4858000% | 3376000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10197 | 4617400% | 1329162 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10496 | 4617400% | 1329162 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10197 | 4617400% | 1329161 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10496 | 4617400% | 1329161 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | TBD | TBD | Nashua 345/161 kV Ckt 2 Transformer | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.06035 | 4633800% | 24750244 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | TBD | TBD | Nashua 345/161 kV Ckt 2 Transformer | Nashua 345/161 kV Ckt 2 Transformer | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.05571 | 4633800% | 24750244 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503666 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jaggard Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jaggard Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03323 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503666 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jaggard Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jaggard Jct. 115 kV | 2025 ITP | Yes | Yes | 0.0344 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503668 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jarbalo Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jarbalo Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03323 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503668 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 166th Street 115 kV Ckt 1 Terminal Upgrade toward Jarbalo Jct. 115 kV | Upgrade terminal equipment at 166th Street 115 kV substation for Ckt 1 toward Jarbalo Jct. 115 kV | 2025 ITP | Yes | Yes | 0.0344 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503673 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 53rd & Mund 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at 53rd & Mund 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.1075 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503673 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | 53rd & Mund 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at 53rd & Mund 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.10616 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900341 | 502741 | Line - Crosstown - Blue Valley Station 161 kV New Line | Crosstown - Blue Valley Station 161 kV New Line | Build a 5.63-mile 161 kV Ckt 1 line from Crosstown to Blue Valley Station | 2025 ITP | Yes | Yes | 0.0708 | 4725600% | 21642007.4341 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900341 | 502741 | Line - Crosstown - Blue Valley Station 161 kV New Line | Crosstown - Blue Valley Station 161 kV New Line | Build a 5.63-mile 161 kV Ckt 1 line from Crosstown to Blue Valley Station | 2025 ITP | Yes | Yes | 0.06834 | 4725600% | 21642007.4341 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503667 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jaggard Jct. 115 kV Ckt 1 Terminal Upgrade toward 166th Street 115 kV | Upgrade terminal equipment at Jaggard Jct. 115 kV substation for Ckt 1 toward 166th Street 115 kV | 2025 ITP | Yes | Yes | 0.0344 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503670 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jaggard Jct. 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at Jaggard Jct. 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.03323 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503670 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jaggard Jct. 115 kV Ckt 1 Terminal Upgrade toward Pentagon 115 kV | Upgrade terminal equipment at Jaggard Jct. 115 kV substation for Ckt 1 toward Pentagon 115 kV | 2025 ITP | Yes | Yes | 0.0344 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503669 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jarbalo Jct. 115 kV Ckt 1 Terminal Upgrade toward 166th Street 115 kV | Upgrade terminal equipment at Jarbalo Jct. 115 kV substation for Ckt 1 toward 166th Street 115 kV | 2025 ITP | Yes | Yes | 0.03323 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503669 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Jarbalo Jct. 115 kV Ckt 1 Terminal Upgrade toward 166th Street 115 kV | Upgrade terminal equipment at Jarbalo Jct. 115 kV substation for Ckt 1 toward 166th Street 115 kV | 2025 ITP | Yes | Yes | 0.0344 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503672 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Pentagon 115 kV Ckt 1 Terminal Upgrade toward 53rd & Mund 115 kV | Upgrade terminal equipment at Pentagon 115 kV substation for Ckt 1 toward 53rd & Mund 115 kV | 2025 ITP | Yes | Yes | 0.1075 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 900393 | 503672 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Pentagon 115 kV Ckt 1 Terminal Upgrade toward 53rd & Mund 115 kV | Upgrade terminal equipment at Pentagon 115 kV substation for Ckt 1 toward 53rd & Mund 115 kV | 2025 ITP | Yes | Yes | 0.10616 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 900393 | 503671 | Sub - Jarbalo Jct. - Mund 115 kV Terminal Upgrades | Pentagon 115 kV Ckt 1 Terminal Upgrade toward Jaggard Jct. 115 kV | Upgrade terminal equipment at Pentagon 115 kV substation for Ckt 1 toward Jaggard Jct. 115 kV | 2025 ITP | Yes | Yes | 0.03323 | 4652500% | 16800000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03297 | 4851900% | 368295711 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03171 | 4851900% | 368295711 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220873 | 170533 170535 170569 | Line - Raun 345 kV - S3452 345 kV New Line (JTIQ) | Raun - S3452 345 kV Ckt 1 New Line | Build approximately 72 mile 345 kV Ckt 1 line from S3452 345 kV substation to OPPD/MEC demarcation point and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03171 | 4851900% | 368295711 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05933 | 4845800% | 162439000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04574 | 4845800% | 162439000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.042 | 4845800% | 162439000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.12322 | 4858000% | 3376000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.05334 | 4858000% | 3376000 | 0
ERAS-2025-031 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.08629 | 4858000% | 3376000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.07674 | 4858000% | 3376000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03433 | 4858000% | 3376000 | 0
ERAS-2025-031 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03222 | 4858000% | 3376000 | 0
ERAS-2025-032 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.07862 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-032 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04009 | 4845800% | 162439000 | 0
ERAS-2025-032 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04383 | 4845800% | 162439000 | 0
ERAS-2025-032 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03064 | 4858000% | 3376000 | 0
ERAS-2025-033 | 03 CENTRAL | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.03732 | 4784800% | 1050598691 | 0
ERAS-2025-033 | 03 CENTRAL | ERIS | 900026 | 500080 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | Yes | 0.0506 | 4707500% | 81824362.95 | 0
ERAS-2025-033 | 03 CENTRAL | NRIS | 900026 | 500080 | Line - Smokey Hills - Summit 230 kV Rebuild (2) | Smokey Hills - Summit 230 kV Ckt 1 Rebuild | Rebuild 38.56-mile Ckt 1 line from Smokey Hills 230 kV substation to Summit 230 kV substation | 2025 ITP | Yes | Yes | 0.05046 | 4707500% | 81824362.95 | 0
ERAS-2025-033 | 03 CENTRAL | ERIS | TBD | TBD | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Rebuild the existing CUDAHY 3 to CRKCK 3 115 kV line 1 (9.53 miles) to a standard rating of 135 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.12526 | TBD (36 month lead time) | 250000 | 250000
ERAS-2025-033 | 03 CENTRAL | NRIS | TBD | TBD | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Rebuild the existing CUDAHY 3 to CRKCK 3 115 kV line 1 (9.53 miles) to a standard rating of 135 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.12844 | TBD (36 month lead time) | 250000 | 250000
ERAS-2025-033 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.07909 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-033 | 03 CENTRAL | ERIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.03419 | 4845800% | 162439000 | 0
ERAS-2025-033 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.05373 | 4845800% | 162439000 | 0
ERAS-2025-033 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.04359 | 4845800% | 162439000 | 0
ERAS-2025-033 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03453 | 4858000% | 3376000 | 0
ERAS-2025-033 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03274 | 4858000% | 3376000 | 0
ERAS-2025-034 | 03 CENTRAL | ERIS | 220903 | 170133 | Line - Aurora H.T. 161 kV - Monett 161 kV Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.5 mile Ckt1 line from Aurora H.T. 161 kV Ckt1 substation to Monett 161 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.11297 | 4699600% | 23159596 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | 220903 | 170133 | Line - Aurora H.T. 161 kV - Monett 161 kV Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.5 mile Ckt1 line from Aurora H.T. 161 kV Ckt1 substation to Monett 161 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.11389 | 4699600% | 23159596 | 0
ERAS-2025-034 | 03 CENTRAL | ERIS | 220880 | 159383 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at N Reeds Spring 161 kV Ckt 1 substation for the line from N Reeds Spring 161 kV Ckt 1 substation to S Reeds Spring 161 kV Ckt 1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05971 | 4742300% | 843321 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | 220880 | 159383 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at N Reeds Spring 161 kV Ckt 1 substation for the line from N Reeds Spring 161 kV Ckt 1 substation to S Reeds Spring 161 kV Ckt 1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05474 | 4742300% | 843321 | 0
ERAS-2025-034 | 03 CENTRAL | ERIS | 220880 | 159382 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reeds Spring - S Reeds Spring 161 kV Rebuild | Rebuild 1.5 mile Ckt 1 line from N Reed Spring 161 kV substation to S Reed Spring 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05971 | 4742300% | 2543371 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | 220880 | 159382 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reeds Spring - S Reeds Spring 161 kV Rebuild | Rebuild 1.5 mile Ckt 1 line from N Reed Spring 161 kV substation to S Reed Spring 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05474 | 4742300% | 2543371 | 0
ERAS-2025-034 | 03 CENTRAL | ERIS | 220880 | 159384 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | S Reed Spring 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at S Reeds Spring 161 kV Ckt 1 substation for the line from S Reeds Spring 161 kV Ckt substation to N Reeds Spring 161 kV Ckt 1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05971 | 4705800% | 136473 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | 220880 | 159384 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | S Reed Spring 161 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at S Reeds Spring 161 kV Ckt 1 substation for the line from S Reeds Spring 161 kV Ckt substation to N Reeds Spring 161 kV Ckt 1 substation with a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05474 | 4705800% | 136473 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | TBD | TBD | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | ERAS-2025-001 | No | Yes | 0.07351 | TBD (36 month lead time) | 1320000 | 1320000
ERAS-2025-034 | 03 CENTRAL | NRIS | 220874 | 170536 | Line - Auburn 345 kV - Hoyt 345 kV New Line (JTIQ) | S3771 - Hoyt 345 kV Ckt 1 New Line (EKC) | Build approximately 55 mile 345 kV Ckt 1 line from S3771 345 kV substation to Hoyt 345 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | JTIQ Upgrade | Yes | Yes | 0.0344 | 4845800% | 162439000 | 0
ERAS-2025-034 | 03 CENTRAL | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03034 | 4858000% | 3376000 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.05761 | 4858000% | 3376000 | 0
ERAS-2025-034 | 03 CENTRAL | NRIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.05727 | 4858000% | 3376000 | 0
ERAS-2025-003 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03729 | 4743400% | 224939250 | 0
ERAS-2025-003 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.03193 | 4780500% | 1366342009.8205 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 220739 | 157393 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Pennsylvania 138 kV Terminal Upgrade | Install a 2000 Amp switch at the Pennsylvania 138 kV substation. | 2023 ITP | Yes | Yes | 0.04914 | 4599200% | 200000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 220739 | 157393 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Pennsylvania 138 kV Terminal Upgrade | Install a 2000 Amp switch at the Pennsylvania 138 kV substation. | 2023 ITP | Yes | Yes | 0.0505 | 4599200% | 200000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03771 | 4743400% | 224939250 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900019 | 503210 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Horseshoe Lake 138 kV Ckt 1 Rebuild | Rebuild 7.87-mile Ckt 1 line from Dunjee 138 kV substation to Horseshoe Lake 138 kV substation | 2025 ITP | Yes | Yes | 0.09409 | 4690500% | 16661900 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900019 | 503210 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Horseshoe Lake 138 kV Ckt 1 Rebuild | Rebuild 7.87-mile Ckt 1 line from Dunjee 138 kV substation to Horseshoe Lake 138 kV substation | 2025 ITP | Yes | Yes | 0.08319 | 4690500% | 16661900 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900019 | 503211 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Reno 138 kV Ckt 1 Rebuild | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.09409 | 4690500% | 16661900 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900019 | 503211 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Reno 138 kV Ckt 1 Rebuild | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.08319 | 4690500% | 16661900 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900189 | 501068 | Multi - Horseshoe Lake Reconfiguration | Horseshoe Lake - Green Pastures Ckt 1 138 kV Voltage Conversion | Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line to 138 kV | 2025 ITP | Yes | Yes | 0.10988 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900183 | 501036 | Line - Horseshoe Lake - Midway 138 kV New Line | Horseshoe Lake - Midway 138 kV New Line | Build a 5.06-mile 138 kV Ckt 2 line from Horseshoe Lake to Midway | 2025 ITP | Yes | Yes | 0.05673 | 4725600% | 14300000 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900189 | 501061 | Multi - Horseshoe Lake Reconfiguration | Kelly Ave. - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2.8-miles 138 kV ckt 1 line from Kelly Ave. - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.06085 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900189 | 501061 | Multi - Horseshoe Lake Reconfiguration | Kelly Ave. - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2.8-miles 138 kV ckt 1 line from Kelly Ave. - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.06754 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.03378 | 4780500% | 1366342009.8205 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900315 | 502602 | Line - Lone Oak - Chisholm Creek 138 kV New Line | Lone Oak - Chisholm Creek 138 kV New Line | Build a 3.53-mile 138 kV Ckt 1 line from Lone Oak to Chisholm Creek | 2025 ITP | Yes | Yes | 0.0381 | 4725600% | 13750000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900315 | 502602 | Line - Lone Oak - Chisholm Creek 138 kV New Line | Lone Oak - Chisholm Creek 138 kV New Line | Build a 3.53-mile 138 kV Ckt 1 line from Lone Oak to Chisholm Creek | 2025 ITP | Yes | Yes | 0.03712 | 4725600% | 13750000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900189 | TBD | Multi - Horseshoe Lake Reconfiguration | Multi - Horseshoe Lake Reconfiguration | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | 2025 ITP | Yes | Yes | 0.33697 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | TBD | TBD | Multi - Horseshoe Lake Reconfiguration - Farrier Addition Substation | Multi - Horseshoe Lake Reconfiguration - Farrier Addition Substation | Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 2025 ITP | Yes | Yes | 0.33697 | TBD (36 month lead time) | TBD | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900177 | 501015 | Line - NE 10th - Reno 138 kV Rebuild | NE 10th - Reno 138 kV Line Rebuild | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.06869 | 4727000% | 8392000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900177 | 501015 | Line - NE 10th - Reno 138 kV Rebuild | NE 10th - Reno 138 kV Line Rebuild | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.06893 | 4727000% | 8392000 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900189 | 501066 | Multi - Horseshoe Lake Reconfiguration | Remington Park - Green Pastures Ckt 1 138 kV Voltage Conversion | Convert the existing 69 kV line from Green Pastures to Deep Fork Tap to Remington Tap to 138 kV to create a Ckt 1 138 kV line from Green Pastures to Remington Park | 2025 ITP | Yes | Yes | 0.10988 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900189 | 501066 | Multi - Horseshoe Lake Reconfiguration | Remington Park - Green Pastures Ckt 1 138 kV Voltage Conversion | Convert the existing 69 kV line from Green Pastures to Deep Fork Tap to Remington Tap to 138 kV to create a Ckt 1 138 kV line from Green Pastures to Remington Park | 2025 ITP | Yes | Yes | 0.1323 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900189 | 501063 | Multi - Horseshoe Lake Reconfiguration | Stonewall - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2-miles 138 kV ckt 1 line from Stonewall - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.0581 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900189 | 501063 | Multi - Horseshoe Lake Reconfiguration | Stonewall - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2-miles 138 kV ckt 1 line from Stonewall - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.06488 | 4727000% | 61120000 | 0
ERAS-2025-004 | 04 SOUTHEAST | ERIS | 900002 | 500003 | Line - Trosper - Reno 138 kV Rebuild | Trosper - Reno 138 kV Line Rebuild | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.12156 | 4727000% | 6178000 | 0
ERAS-2025-004 | 04 SOUTHEAST | NRIS | 900002 | 500003 | Line - Trosper - Reno 138 kV Rebuild | Trosper - Reno 138 kV Line Rebuild | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.12211 | 4727000% | 6178000 | 0
ERAS-2025-005 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03279 | 4743400% | 224939250 | 0
ERAS-2025-005 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.03015 | 4780500% | 1366342009.8205 | 0
ERAS-2025-005 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.03744 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-005 | 04 SOUTHEAST | ERIS | 220885 | 170543 | Bus - Sibley 345 kV Bus Reconfiguration (JTIQ) | Sibley - 345 kV Bus Reconfiguration | T-Line re-terminal to Sibley 345 kV bus reconfiguration | JTIQ Upgrade | Yes | Yes | 0.03993 | 4858000% | 3376000 | 0
ERAS-2025-009 | 04 SOUTHEAST | ERIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.05428 | 4666100% | 4765714 | 0
ERAS-2025-009 | 04 SOUTHEAST | NRIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.05648 | 4666100% | 4765714 | 0
ERAS-2025-009 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03313 | 4743400% | 224939250 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 220739 | 157393 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Pennsylvania 138 kV Terminal Upgrade | Install a 2000 Amp switch at the Pennsylvania 138 kV substation. | 2023 ITP | Yes | Yes | 0.04914 | 4599200% | 200000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 220739 | 157393 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Pennsylvania 138 kV Terminal Upgrade | Install a 2000 Amp switch at the Pennsylvania 138 kV substation. | 2023 ITP | Yes | Yes | 0.05113 | 4599200% | 200000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03775 | 4743400% | 224939250 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900019 | 503210 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Horseshoe Lake 138 kV Ckt 1 Rebuild | Rebuild 7.87-mile Ckt 1 line from Dunjee 138 kV substation to Horseshoe Lake 138 kV substation | 2025 ITP | Yes | Yes | 0.09409 | 4690500% | 16661900 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900019 | 503210 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Horseshoe Lake 138 kV Ckt 1 Rebuild | Rebuild 7.87-mile Ckt 1 line from Dunjee 138 kV substation to Horseshoe Lake 138 kV substation | 2025 ITP | Yes | Yes | 0.09866 | 4690500% | 16661900 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900019 | 503211 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Reno 138 kV Ckt 1 Rebuild | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.09409 | 4690500% | 16661900 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900019 | 503211 | Line - Horseshoe Lake - Dunjee - Reno 138 kV Reconductor | Dunjee - Reno 138 kV Ckt 1 Rebuild | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.09866 | 4690500% | 16661900 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900189 | 501068 | Multi - Horseshoe Lake Reconfiguration | Horseshoe Lake - Green Pastures Ckt 1 138 kV Voltage Conversion | Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line to 138 kV | 2025 ITP | Yes | Yes | 0.10988 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900183 | 501036 | Line - Horseshoe Lake - Midway 138 kV New Line | Horseshoe Lake - Midway 138 kV New Line | Build a 5.06-mile 138 kV Ckt 2 line from Horseshoe Lake to Midway | 2025 ITP | Yes | Yes | 0.05673 | 4725600% | 14300000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900183 | 501036 | Line - Horseshoe Lake - Midway 138 kV New Line | Horseshoe Lake - Midway 138 kV New Line | Build a 5.06-mile 138 kV Ckt 2 line from Horseshoe Lake to Midway | 2025 ITP | Yes | Yes | 0.05668 | 4725600% | 14300000 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900189 | 501061 | Multi - Horseshoe Lake Reconfiguration | Kelly Ave. - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2.8-miles 138 kV ckt 1 line from Kelly Ave. - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.06085 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900189 | 501061 | Multi - Horseshoe Lake Reconfiguration | Kelly Ave. - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2.8-miles 138 kV ckt 1 line from Kelly Ave. - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.05589 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.03373 | 4780500% | 1366342009.8205 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900315 | 502602 | Line - Lone Oak - Chisholm Creek 138 kV New Line | Lone Oak - Chisholm Creek 138 kV New Line | Build a 3.53-mile 138 kV Ckt 1 line from Lone Oak to Chisholm Creek | 2025 ITP | Yes | Yes | 0.0381 | 4725600% | 13750000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900315 | 502602 | Line - Lone Oak - Chisholm Creek 138 kV New Line | Lone Oak - Chisholm Creek 138 kV New Line | Build a 3.53-mile 138 kV Ckt 1 line from Lone Oak to Chisholm Creek | 2025 ITP | Yes | Yes | 0.03829 | 4725600% | 13750000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900189 | TBD | Multi - Horseshoe Lake Reconfiguration | Multi - Horseshoe Lake Reconfiguration | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | 2025 ITP | Yes | Yes | 0.17315 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | TBD | TBD | Multi - Horseshoe Lake Reconfiguration - Farrier Addition Substation | Multi - Horseshoe Lake Reconfiguration - Farrier Addition Substation | Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 2025 ITP | Yes | Yes | 0.17315 | TBD (36 month lead time) | TBD | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900177 | 501015 | Line - NE 10th - Reno 138 kV Rebuild | NE 10th - Reno 138 kV Line Rebuild | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.06869 | 4727000% | 8392000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900177 | 501015 | Line - NE 10th - Reno 138 kV Rebuild | NE 10th - Reno 138 kV Line Rebuild | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.07392 | 4727000% | 8392000 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900189 | 501066 | Multi - Horseshoe Lake Reconfiguration | Remington Park - Green Pastures Ckt 1 138 kV Voltage Conversion | Convert the existing 69 kV line from Green Pastures to Deep Fork Tap to Remington Tap to 138 kV to create a Ckt 1 138 kV line from Green Pastures to Remington Park | 2025 ITP | Yes | Yes | 0.10988 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900189 | 501066 | Multi - Horseshoe Lake Reconfiguration | Remington Park - Green Pastures Ckt 1 138 kV Voltage Conversion | Convert the existing 69 kV line from Green Pastures to Deep Fork Tap to Remington Tap to 138 kV to create a Ckt 1 138 kV line from Green Pastures to Remington Park | 2025 ITP | Yes | Yes | 0.09726 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900189 | 501063 | Multi - Horseshoe Lake Reconfiguration | Stonewall - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2-miles 138 kV ckt 1 line from Stonewall - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.0581 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900189 | 501063 | Multi - Horseshoe Lake Reconfiguration | Stonewall - Remington Park Ckt 1 138 kV New Line | Rebuild the existing 2-miles 138 kV ckt 1 line from Stonewall - Remmington Tap then extend the line to Remington Park 138 kV substation | 2025 ITP | Yes | Yes | 0.05527 | 4727000% | 61120000 | 0
ERAS-2025-010 | 04 SOUTHEAST | ERIS | 900002 | 500003 | Line - Trosper - Reno 138 kV Rebuild | Trosper - Reno 138 kV Line Rebuild | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.12156 | 4727000% | 6178000 | 0
ERAS-2025-010 | 04 SOUTHEAST | NRIS | 900002 | 500003 | Line - Trosper - Reno 138 kV Rebuild | Trosper - Reno 138 kV Line Rebuild | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 2025 ITP | Yes | Yes | 0.12476 | 4727000% | 6178000 | 0
ERAS-2025-022 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.0617 | 4599200% | 9281667 | 0
ERAS-2025-022 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.06127 | 4599200% | 9281667 | 0
ERAS-2025-022 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.0617 | 4599200% | 5613374 | 0
ERAS-2025-022 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.06127 | 4599200% | 5613374 | 0
ERAS-2025-022 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03581 | 4743400% | 224939250 | 0
ERAS-2025-022 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.03873 | 4780500% | 1366342009.8205 | 0
ERAS-2025-022 | 04 SOUTHEAST | NRIS | TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Yes | Yes | 0.06212 | TBD (36 month lead time) | 825000 | 825000
ERAS-2025-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.05783 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-023 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03347 | 4743400% | 224939250 | 0
ERAS-2025-024 | 04 SOUTHEAST | ERIS | 900298 | 502409 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan - Duncan Tap 138 kV Line Rebuild | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 2025 ITP | Yes | Yes | 0.05801 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | 900298 | 502409 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan - Duncan Tap 138 kV Line Rebuild | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 2025 ITP | Yes | Yes | 0.03418 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | ERIS | 900298 | 502415 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 2025 ITP | Yes | Yes | 0.05801 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | 900298 | 502415 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 2025 ITP | Yes | Yes | 0.03418 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | ERIS | 900298 | 502412 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 2025 ITP | Yes | Yes | 0.05801 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | 900298 | 502412 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 2025 ITP | Yes | Yes | 0.03418 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.07021 | 4780500% | 1366342009.8205 | 0
ERAS-2025-024 | 04 SOUTHEAST | ERIS | 900298 | 502421 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Marlow - Duncan Eastside 138 kV Line Rebuild | Rebuild 9.75-mile Ckt 1 line from Marlow 138 kV substation to Duncan Eastside 138 kV substation | 2025 ITP | Yes | Yes | 0.05801 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | 900298 | 502421 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Marlow - Duncan Eastside 138 kV Line Rebuild | Rebuild 9.75-mile Ckt 1 line from Marlow 138 kV substation to Duncan Eastside 138 kV substation | 2025 ITP | Yes | Yes | 0.03418 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | ERIS | 900298 | 502418 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Rush Springs Tap - Marlow 138 kV Line Rebuild | Rebuild 8.59-mile Ckt 1 line from Rush Springs Tap 138 kV substation to Marlow 138 kV substation | 2025 ITP | Yes | Yes | 0.05801 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | 900298 | 502418 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Rush Springs Tap - Marlow 138 kV Line Rebuild | Rebuild 8.59-mile Ckt 1 line from Rush Springs Tap 138 kV substation to Marlow 138 kV substation | 2025 ITP | Yes | Yes | 0.03418 | 4616300% | 81256000 | 0
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | 170578 | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Rebuild the existing Duncan to Duncan Bois D' Arc 138 kV line (3.9 miles) to a minimum rating of 190 MVA. Upgrade RCTL at Duncan | DISIS-2020-001 | Yes | Yes | 0.04536 | TBD (36 month lead time) | 8970000 | 8970000
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.27675 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.29947 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | ERAS-2025-001 | No | Yes | 0.37642 | TBD (36 month lead time) | 21600000 | 21600000
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | ERAS-2025-001 | No | Yes | 0.04536 | TBD (36 month lead time) | 40710000 | 40710000
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | ERAS-2025-001 | No | Yes | 0.10932 | TBD (36 month lead time) | 9867000 | 9867000
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | ERAS-2025-001 | No | Yes | 0.10124 | TBD (36 month lead time) | 12006000 | 12006000
ERAS-2025-024 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | ERAS-2025-001 | No | Yes | 0.06396 | TBD (36 month lead time) | 2139000 | 2139000
ERAS-2025-025 | 04 SOUTHEAST | ERIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.03348 | 4675200% | 10000000 | 0
ERAS-2025-025 | 04 SOUTHEAST | ERIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.03348 | 4675200% | 2177750 | 0
ERAS-2025-025 | 04 SOUTHEAST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.04318 | 4743400% | 224939250 | 0
ERAS-2025-025 | 04 SOUTHEAST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.04707 | 4780500% | 1366342009.8205 | 0
ERAS-2025-025 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.0396 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-025 | 04 SOUTHEAST | NRIS | TBD | TBD | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | ERAS-2025-001 | No | Yes | 0.05463 | TBD (36 month lead time) | 21600000 | 21600000
ERAS-2025-002 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.06156 | 4743400% | 224939250 | 0
ERAS-2025-002 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.17879 | 4780500% | 1366342009.8205 | 0
ERAS-2025-002 | 05 SOUTHWEST | ERIS | 900380 | 503501 | Line - Lubbock South - Wolfforth 230 kV Rebuild | Lubbock South - Wolfforth 230 kV Line Rebuild | Rebuild 14.62-mile Ckt 1 line from Lubbock South 230 kV substation to Wolfforth 230 kV substation | 2025 ITP | Yes | Yes | 0.03017 | 4727000% | 34978000 | 0
ERAS-2025-002 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.0897 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-002 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.24956 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-002 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.11975 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-002 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.0503 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-002 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.0503 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-014 | 05 SOUTHWEST | ERIS | 220817 | 170190 | Device - Channing 230 kV Capacitor | Channing 230 kV Capacitor | Install a 14.4 MVAR Capacitor at Channing 230 kV substation | 2024 ITP | Yes | Yes | 0.03023 | 4673600% | 6732794 | 0
ERAS-2025-014 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.11357 | 4743400% | 224939250 | 0
ERAS-2025-014 | 05 SOUTHWEST | ERIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.1036 | 4725600% | 91069269.4413 | 0
ERAS-2025-014 | 05 SOUTHWEST | ERIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.12498 | 4725600% | 91069269.4413 | 0
ERAS-2025-014 | 05 SOUTHWEST | NRIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.0923 | 4725600% | 91069269.4413 | 0
ERAS-2025-014 | 05 SOUTHWEST | ERIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.05277 | 4689100% | 18874145 | 0
ERAS-2025-014 | 05 SOUTHWEST | NRIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.04864 | 4689100% | 18874145 | 0
ERAS-2025-014 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.21847 | 4780500% | 1366342009.8205 | 0
ERAS-2025-014 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.06949 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-014 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.20071 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-014 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.1005 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-014 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05261 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-014 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05261 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-014 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Road Runner to Andrews 345 kV New Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | ERAS-2025-001 | No | Yes | 0.23951 | TBD (36 month lead time) | 73524573 | 73524573
ERAS-2025-016 | 05 SOUTHWEST | ERIS | 220817 | 170190 | Device - Channing 230 kV Capacitor | Channing 230 kV Capacitor | Install a 14.4 MVAR Capacitor at Channing 230 kV substation | 2024 ITP | Yes | Yes | 0.03066 | 4673600% | 6732794 | 0
ERAS-2025-016 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.11678 | 4743400% | 224939250 | 0
ERAS-2025-016 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.08603 | 4780500% | 1366342009.8205 | 0
ERAS-2025-016 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.0657 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-016 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.19127 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-016 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.0969 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-016 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05345 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-016 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05345 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-016 | 05 SOUTHWEST | NRIS | TBD | TBD | Tolk 345/230 kV CKT 1 Transformer Replacement | Tolk 345/230 kV CKT 1 Transformer Replacement | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | ERAS-2025-001 | No | Yes | 0.22178 | TBD (36 month lead time) | 8302968 | 8302968
ERAS-2025-018 | 05 SOUTHWEST | ERIS | 220817 | 170190 | Device - Channing 230 kV Capacitor | Channing 230 kV Capacitor | Install a 14.4 MVAR Capacitor at Channing 230 kV substation | 2024 ITP | Yes | Yes | 0.03021 | 4673600% | 6732794 | 0
ERAS-2025-018 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.11648 | 4743400% | 224939250 | 0
ERAS-2025-018 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.1032 | 4780500% | 1366342009.8205 | 0
ERAS-2025-018 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.06566 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-018 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.19116 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-018 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.09687 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-018 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05348 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-018 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05348 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-018 | 05 SOUTHWEST | NRIS | TBD | TBD | Tolk 345/230 kV CKT 1 Transformer Replacement | Tolk 345/230 kV CKT 1 Transformer Replacement | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | ERAS-2025-001 | No | Yes | 0.175 | TBD (36 month lead time) | 8302968 | 8302968
ERAS-2025-020 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.11193 | 4743400% | 224939250 | 0
ERAS-2025-020 | 05 SOUTHWEST | ERIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.10871 | 4725600% | 91069269.4413 | 0
ERAS-2025-020 | 05 SOUTHWEST | NRIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.11744 | 4725600% | 91069269.4413 | 0
ERAS-2025-020 | 05 SOUTHWEST | ERIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.05569 | 4689100% | 18874145 | 0
ERAS-2025-020 | 05 SOUTHWEST | NRIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.05249 | 4689100% | 18874145 | 0
ERAS-2025-020 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.1956 | 4780500% | 1366342009.8205 | 0
ERAS-2025-020 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.07005 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-020 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.20206 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-020 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.10104 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-020 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05256 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-020 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05256 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-020 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Road Runner to Andrews 345 kV New Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | ERAS-2025-001 | No | Yes | 0.0419 | TBD (36 month lead time) | 73524573 | 73524573
ERAS-2025-021 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.04055 | 4743400% | 224939250 | 0
ERAS-2025-021 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.1907 | 4780500% | 1366342009.8205 | 0
ERAS-2025-021 | 05 SOUTHWEST | ERIS | 900380 | 503501 | Line - Lubbock South - Wolfforth 230 kV Rebuild | Lubbock South - Wolfforth 230 kV Line Rebuild | Rebuild 14.62-mile Ckt 1 line from Lubbock South 230 kV substation to Wolfforth 230 kV substation | 2025 ITP | Yes | Yes | 0.03153 | 4727000% | 34978000 | 0
ERAS-2025-021 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.20689 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-021 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.20689 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-021 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05164 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-021 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05164 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-026 | 05 SOUTHWEST | NRIS | 900298 | 502409 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan - Duncan Tap 138 kV Line Rebuild | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 2025 ITP | Yes | Yes | 0.03096 | 4616300% | 81256000 | 0
ERAS-2025-026 | 05 SOUTHWEST | NRIS | 900298 | 502415 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 2025 ITP | Yes | Yes | 0.03096 | 4616300% | 81256000 | 0
ERAS-2025-026 | 05 SOUTHWEST | NRIS | 900298 | 502412 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 2025 ITP | Yes | Yes | 0.03096 | 4616300% | 81256000 | 0
ERAS-2025-026 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.07129 | 4780500% | 1366342009.8205 | 0
ERAS-2025-026 | 05 SOUTHWEST | NRIS | 900298 | 502421 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Marlow - Duncan Eastside 138 kV Line Rebuild | Rebuild 9.75-mile Ckt 1 line from Marlow 138 kV substation to Duncan Eastside 138 kV substation | 2025 ITP | Yes | Yes | 0.03096 | 4616300% | 81256000 | 0
ERAS-2025-026 | 05 SOUTHWEST | NRIS | 900298 | 502418 | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild | Rush Springs Tap - Marlow 138 kV Line Rebuild | Rebuild 8.59-mile Ckt 1 line from Rush Springs Tap 138 kV substation to Marlow 138 kV substation | 2025 ITP | Yes | Yes | 0.03096 | 4616300% | 81256000 | 0
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | 170578 | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Rebuild the existing Duncan to Duncan Bois D' Arc 138 kV line (3.9 miles) to a minimum rating of 190 MVA. Upgrade RCTL at Duncan | DISIS-2020-001 | Yes | Yes | 0.04097 | TBD (36 month lead time) | 8970000 | 8970000
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.33377 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.33874 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | ERAS-2025-001 | No | Yes | 0.07351 | TBD (36 month lead time) | 21600000 | 21600000
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | ERAS-2025-001 | No | Yes | 0.04097 | TBD (36 month lead time) | 40710000 | 40710000
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | ERAS-2025-001 | No | Yes | 0.06412 | TBD (36 month lead time) | 9867000 | 9867000
ERAS-2025-026 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | ERAS-2025-001 | No | Yes | 0.05682 | TBD (36 month lead time) | 12006000 | 12006000
ERAS-2025-027 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.10316 | 4743400% | 224939250 | 0
ERAS-2025-027 | 05 SOUTHWEST | ERIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.03316 | 4725600% | 91069269.4413 | 0
ERAS-2025-027 | 05 SOUTHWEST | NRIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.03584 | 4725600% | 91069269.4413 | 0
ERAS-2025-027 | 05 SOUTHWEST | ERIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.05596 | 4689100% | 18874145 | 0
ERAS-2025-027 | 05 SOUTHWEST | NRIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.05542 | 4689100% | 18874145 | 0
ERAS-2025-027 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.09673 | 4780500% | 1366342009.8205 | 0
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | BRU SUB to XTO MAHONEY 230 kV Line Rebuild | BRU SUB to XTO MAHONEY 230 kV Line Rebuild | Rebuild 1.76 miles BRU_SUB to XTO_MAHONEY 230 kV line to a minimum of 680 MVA | ERAS-2025-001 | No | Yes | 0.69037 | TBD (36 month lead time) | 1554975.84 | 1554975.84
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.07266 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.20828 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.10353 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05239 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05239 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | Tolk 345/230 kV CKT 1 Transformer Replacement | Tolk 345/230 kV CKT 1 Transformer Replacement | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | ERAS-2025-001 | No | Yes | 0.04086 | TBD (36 month lead time) | 8302968 | 8302968
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | YOAKUM to BRU SUB 230 kV Line Rebuild | YOAKUM to BRU SUB 230 kV Line Rebuild | Rebuild 5.35 miles YOAKUM to BRU_SUB 230 kV line to a minimum of 665 MVA | ERAS-2025-001 | No | Yes | 0.69037 | TBD (36 month lead time) | 4726773.15 | 4726773.15
ERAS-2025-027 | 05 SOUTHWEST | NRIS | TBD | TBD | YOAKUM to MUSTANG 230 kV Line Rebuild | YOAKUM to MUSTANG 230 kV Line Rebuild | Rebuild 15.65 miles YOAKUM to MUSTANG 230 kV line to a minimum of 620 MVA | ERAS-2025-001 | No | Yes | 0.152 | TBD (36 month lead time) | 13826915.85 | 13826915.85
ERAS-2025-028 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.08199 | 4743400% | 224939250 | 0
ERAS-2025-028 | 05 SOUTHWEST | ERIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.04036 | 4725600% | 91069269.4413 | 0
ERAS-2025-028 | 05 SOUTHWEST | NRIS | 900121 | 500689 | Multi - Hobbs - Kiowa 345 kV Line Tap at Lea National 115 kV | Hobbs - Kiowa 345 kV Line Tap | Tap the existing Hobbs - Kiowa 345 kV Ckt 1 line at new Lea National substation | 2025 ITP | Yes | Yes | 0.0321 | 4725600% | 91069269.4413 | 0
ERAS-2025-028 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.03545 | 4780500% | 1366342009.8205 | 0
ERAS-2025-028 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.08152 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-028 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.22977 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-028 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.11196 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-028 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05128 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-028 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05128 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-030 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.11556 | 4743400% | 224939250 | 0
ERAS-2025-030 | 05 SOUTHWEST | ERIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.0396 | 4689100% | 18874145 | 0
ERAS-2025-030 | 05 SOUTHWEST | NRIS | 900432 | 504321 | XFR - Hobbs 230/115 kV | Hobbs 230/345 kV Ckt 2 Transformer | Install new 230/345 Ckt 2 transformer at Hobbs | 2025 ITP | Yes | Yes | 0.04208 | 4689100% | 18874145 | 0
ERAS-2025-030 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.19237 | 4780500% | 1366342009.8205 | 0
ERAS-2025-030 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.06795 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-030 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.19689 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-030 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.09904 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-030 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05291 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-030 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05291 | TBD (36 month lead time) | 16565793.75 | 16565793.75
ERAS-2025-036 | 05 SOUTHWEST | ERIS | 220817 | 170190 | Device - Channing 230 kV Capacitor | Channing 230 kV Capacitor | Install a 14.4 MVAR Capacitor at Channing 230 kV substation | 2024 ITP | Yes | Yes | 0.04012 | 4673600% | 6732794 | 0
ERAS-2025-036 | 05 SOUTHWEST | NRIS | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Potter to Beckham 345 kV Line | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.13211 | 4743400% | 224939250 | 0
ERAS-2025-036 | 05 SOUTHWEST | NRIS | 900423 | TBD | Line - Crawfish Draw - Phantom 765 kV New Line | Line - Crawfish Draw - Phantom 765 kV New Line | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 2025 ITP | No | Yes | 0.08972 | 4780500% | 1366342009.8205 | 0
ERAS-2025-036 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to LES 345 kV Line Rebuild | COMANC7 TAP to LES 345 kV Line Rebuild | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | ERAS-2025-001 | No | Yes | 0.0507 | TBD (36 month lead time) | 6031219.88 | 6031219.88
ERAS-2025-036 | 05 SOUTHWEST | NRIS | TBD | TBD | COMANC7 TAP to OKU 345 kV Line Rebuild | COMANC7 TAP to OKU 345 kV Line Rebuild | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | ERAS-2025-001 | No | Yes | 0.15413 | TBD (36 month lead time) | 70417639.32 | 70417639.32
ERAS-2025-036 | 05 SOUTHWEST | NRIS | TBD | TBD | Comanche 345 kV New Substation | Comanche 345 kV New Substation | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | ERAS-2025-001 | No | Yes | 0.08256 | TBD (36 month lead time) | 16200000 | 16200000
ERAS-2025-036 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY 230/138 kV Transformer Replacement | ELKCITY 230/138 kV Transformer Replacement | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | ERAS-2025-001 | No | Yes | 0.05608 | TBD (36 month lead time) | 6621188 | 6621188
ERAS-2025-036 | 05 SOUTHWEST | NRIS | TBD | TBD | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | ERAS-2025-001 | No | Yes | 0.05608 | TBD (36 month lead time) | 16565793.75 | 16565793.75

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converged | ERAS-2025-001 | 01NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 02NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 03NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 04NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 CF | 01NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 CF | 02NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 CF | 03NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 CF | 04NR | 0 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.21802 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.42858 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.15128 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.31598 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.25312 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.38791 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.07585 |  | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.15598 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.15623 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.28152 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.17268 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.20736 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.15155 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.12 |  | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13502 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13683 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08543 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12761 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10989 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13877 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14876 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29WP | ERAS-2025-020 | " | Non-Converged |  |  | 0.04599 |  | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.04152 |  | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29L | ERAS-2025-021 | " | Non-Converged |  |  | 0.0444 |  | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.15598 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.15623 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.28152 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.17268 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.20736 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.15155 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.12 |  | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 500001_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 500001_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 500001_2 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_1 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_4 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_5 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_7 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511456_8 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511468_0 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511468_3 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 511468_4 - Potential P4 Event | TDF Impact | Potter to Beckham 345 kV Line (2024 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13188 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13368 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08226 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29L | ERAS-2025-021 | " | Non-Converged |  |  | 0.06165 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12446 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10674 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13563 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14562 |  | POI 515375_39 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13502 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13683 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08543 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12761 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10989 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13877 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14876 |  | POI 515554_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13212 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13392 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08249 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12469 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10697 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13587 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14586 |  | POI 515554_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13212 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13392 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08249 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12469 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10697 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13587 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14586 |  | POI 515677_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13185 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13365 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08224 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29L | ERAS-2025-021 | " | Non-Converged |  |  | 0.06163 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12443 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10671 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.1356 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14559 |  | POI 515677_14 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13188 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13368 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08226 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29L | ERAS-2025-021 | " | Non-Converged |  |  | 0.06165 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12446 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10674 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13563 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14562 |  | POI 516106_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13185 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13365 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08224 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29L | ERAS-2025-021 | " | Non-Converged |  |  | 0.06163 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12443 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10671 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.1356 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14559 |  | POI 516106_9 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.13502 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.13683 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.08543 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.12761 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.10989 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.13877 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14876 |  | POI 523097_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_12 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_17 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_21 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_24 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_26 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_27 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.27011 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.2831 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.18431 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.26203 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22933 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.28444 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.26208 |  | POI 523097_6 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 525832_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 762467_0 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 762467_1 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-018 | " | Non-Converged |  |  | 0.17737 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-020 | " | Non-Converged |  |  | 0.17727 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-021 | " | Non-Converged |  |  | 0.23678 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-027 | " | Non-Converged |  |  | 0.19157 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-028 | " | Non-Converged |  |  | 0.22143 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-030 | " | Non-Converged |  |  | 0.17331 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 29SP | ERAS-2025-036 | " | Non-Converged |  |  | 0.14715 |  | POI 762467_2 - Potential P4 Event | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 05NR | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 05ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 05ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 05NR | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25706 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27211 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.34123 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28132 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.31244 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26481 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20412 | 113.97 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27179 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28111 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.35086 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.29227 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.32227 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27554 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20588 | 117.7675 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23073 | 103.61 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24244 | 103.61 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28198 | 103.61 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24835 | 103.61 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27004 | 103.61 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23706 | 103.61 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 102.64 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 103.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.22853 | 101.5 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23751 | 101.5 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26617 | 101.5 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24284 | 101.5 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26106 | 101.5 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23319 | 101.5 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 103.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 102.64 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25705 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27211 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.34107 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28131 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.31241 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26481 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20412 | 113.83 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27178 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28111 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.35071 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.29226 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.32224 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27554 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20587 | 117.7329 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 103.11 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 103.13 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23719 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24714 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.28271 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25299 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27307 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24238 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20211 | 102.93 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2276 | 106.28 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23658 | 106.28 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26525 | 106.28 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24191 | 106.28 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26014 | 106.28 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23227 | 106.28 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.22853 | 101.5 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23751 | 101.5 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26617 | 101.5 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24284 | 101.5 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26106 | 101.5 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23319 | 101.5 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.22767 | 105 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23665 | 105 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26531 | 105 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24198 | 105 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2602 | 105 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23233 | 105 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.22767 | 105 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23665 | 105 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26531 | 105 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24198 | 105 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2602 | 105 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23233 | 105 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2276 | 106.5 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23658 | 106.5 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26525 | 106.5 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24191 | 106.5 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26014 | 106.5 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23227 | 106.5 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2276 | 106.28 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23658 | 106.28 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26525 | 106.28 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24191 | 106.28 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26014 | 106.28 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23227 | 106.28 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2276 | 106.5 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23658 | 106.5 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26525 | 106.5 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24191 | 106.5 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26014 | 106.5 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23227 | 106.5 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.22853 | 101.5 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23751 | 101.5 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26617 | 101.5 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24284 | 101.5 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.26106 | 101.5 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23319 | 101.5 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.23842 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24865 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.2767 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.25345 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.27167 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.24404 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 |  | 1176 | 0.20258 | 103.13 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.2027 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.21287 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.24795 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.21894 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.23964 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.20797 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 |  | 0.16699 | 106.19 | System Intact | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25706 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27211 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.34123 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28132 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.31244 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26481 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20412 | 114.27 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27179 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28111 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.35086 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.29227 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.32227 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27554 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20588 | 117.9939 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23073 | 103.95 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24244 | 103.95 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28198 | 103.95 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24835 | 103.95 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27004 | 103.95 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23706 | 103.95 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 102.95 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 103.44 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.22853 | 101.78 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23751 | 101.78 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26617 | 101.78 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24284 | 101.78 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26106 | 101.78 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23319 | 101.78 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 103.44 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 102.95 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25705 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27211 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.34107 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28131 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.31241 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26481 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20412 | 114.11 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27178 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28111 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.35071 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.29226 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.32224 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27554 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20587 | 117.9592 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 103.44 | POI 511587_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 103.45 | POI 511587_1 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23719 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24714 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.28271 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25299 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27307 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24238 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20211 | 103.25 | POI 511587_2 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2276 | 106.46 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23658 | 106.46 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26525 | 106.46 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24191 | 106.46 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26014 | 106.46 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23227 | 106.46 | POI 515375_39 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.22853 | 101.78 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23751 | 101.78 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26617 | 101.78 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24284 | 101.78 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26106 | 101.78 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23319 | 101.78 | POI 515554_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.22767 | 105.29 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23665 | 105.29 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26531 | 105.29 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24198 | 105.29 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2602 | 105.29 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23233 | 105.29 | POI 515554_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.22767 | 105.29 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23665 | 105.29 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26531 | 105.29 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24198 | 105.29 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2602 | 105.29 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23233 | 105.29 | POI 515677_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2276 | 106.68 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23658 | 106.68 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26525 | 106.68 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24191 | 106.68 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26014 | 106.68 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23227 | 106.68 | POI 515677_14 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2276 | 106.46 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23658 | 106.46 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26525 | 106.46 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24191 | 106.46 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26014 | 106.46 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23227 | 106.46 | POI 516106_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2276 | 106.68 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23658 | 106.68 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26525 | 106.68 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24191 | 106.68 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26014 | 106.68 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23227 | 106.68 | POI 516106_9 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.22853 | 101.78 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23751 | 101.78 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26617 | 101.78 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24284 | 101.78 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.26106 | 101.78 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23319 | 101.78 | POI 523097_0 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.23842 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24865 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.2767 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.25345 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.27167 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.24404 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 |  | 1176 | 0.20258 | 103.41 | POI 523097_27 - Potential P4 Event | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.2027 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.21287 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.24795 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.21894 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.23964 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.20797 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | 1011 |  | 0.16699 | 106.39 | System Intact | TDF Impact | COMANC7 TAP to OKU 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.37 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.04 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.34 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07851 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07822 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08174 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07835 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07836 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07829 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07883 | 112.09 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.87 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.1 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 110.92 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.1 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.87 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07585 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07477 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07478 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07441 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07277 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07904 | 108.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.63 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.89 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.63 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.89 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.37 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.38 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.38 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.01 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.27 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.89 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.89 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.04 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 111.9 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.34 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07957 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07989 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08395 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08042 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08174 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07965 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07793 | 119 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07597 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07624 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08013 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07676 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07802 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07602 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07447 | 114.97 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07674 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07702 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08093 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07754 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07881 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0768 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07523 | 115.38 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.13 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.16 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0792 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07825 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07876 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07797 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0766 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07864 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08193 | 113.45 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0786 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0783 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08179 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07843 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07843 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07837 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07894 | 112.26 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07874 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07844 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08195 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07858 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07858 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07851 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07907 | 112.42 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07874 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07844 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08195 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07858 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07858 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07851 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07907 | 112.42 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07851 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07822 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08174 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07835 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07836 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07829 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07883 | 112.15 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08002 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07967 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08294 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07978 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07968 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07976 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08051 | 114 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08002 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07967 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08294 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07978 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07968 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07977 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08052 | 114 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07851 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07822 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08174 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07835 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07836 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07829 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07883 | 112.1 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07851 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07822 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08174 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07835 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07836 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07829 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07883 | 112.09 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0786 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.0783 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.08179 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07843 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07843 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07837 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 |  | 330 | 0.07894 | 112.26 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05517 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05436 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05454 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05424 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05331 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05467 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 3WXFMR ELKCTY-6 138 1 | 279 |  | 0.05746 | 104.06 | System Intact | TDF Impact | ELKCITY 230/138 kV Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.24 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.23 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 114.35 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.1 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07851 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07822 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08174 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07835 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07836 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07829 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07883 | 107.17 | P12:345:OKGE:BKRBKR4890:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.13 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.52 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 114.23 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.52 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.13 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07585 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07477 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07478 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07441 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07277 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07904 | 105.6 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 114.99 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 115.48 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 114.99 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 115.48 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.22 | POI 500001_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.24 | POI 500001_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.22 | POI 500001_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 114.32 | POI 511456_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.21 | POI 511456_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 115.48 | POI 511456_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 115.47 | POI 511456_5 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 114.35 | POI 511456_6 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 115.5 | POI 511456_7 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.1 | POI 511456_8 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07957 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07989 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08395 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08042 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08174 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07965 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07793 | 128.09 | POI 511468_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07597 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07624 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08013 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07676 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07802 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07602 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07447 | 122.96 | POI 511468_3 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07674 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08093 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07754 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07881 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0768 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07523 | 123.24 | POI 511468_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.57 | POI 511587_0 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.62 | POI 511587_1 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0792 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07825 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07876 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0766 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07864 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08193 | 110.43 | POI 511587_2 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0786 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0783 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08179 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07843 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07843 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07837 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07894 | 107.47 | POI 515375_12 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07874 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07844 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08195 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07858 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07858 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07851 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07907 | 107.58 | POI 515375_19 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07874 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07844 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08195 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07858 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07858 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07851 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07907 | 107.58 | POI 515375_25 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07851 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07822 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08174 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07835 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07836 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07829 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07883 | 107.25 | POI 515375_30 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08002 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07967 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08294 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07978 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07968 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07976 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08051 | 109.43 | POI 515375_35 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08002 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07967 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08294 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07978 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07968 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07977 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08052 | 109.43 | POI 515375_36 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07851 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07822 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08174 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07835 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07836 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07829 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07883 | 107.18 | POI 515375_37 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07851 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07822 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08174 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07835 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07836 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07829 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07883 | 107.17 | POI 515375_38 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0786 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0783 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08179 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07843 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07843 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07837 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07894 | 107.47 | POI 515375_4 - Potential P4 Event | Cumulative Impact | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.46 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.46 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.46 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.46 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.46 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.46 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.47 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.47 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.47 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.47 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.47 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.47 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.59 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.59 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.59 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.59 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.59 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.59 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.42 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.42 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.42 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.42 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.42 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.42 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05802 | 115.33 | 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05382 | 115.33 | 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05326 | 115.33 | 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05537 | 115.33 | 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08925 | 115.33 | 523221 XIT_INTG 6 230 523869 CHAN+TASCOS6 230 1 | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05804 | 118.08 | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05383 | 118.08 | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05328 | 118.08 | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05538 | 118.08 | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08926 | 118.08 | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05779 | 113.7 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0536 | 113.7 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05305 | 113.7 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 113.7 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08889 | 113.7 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05325 | 101.11 | P12:345:OKGE:BKRBKR4290:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05052 | 101.11 | P12:345:OKGE:BKRBKR4290:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05037 | 101.11 | P12:345:OKGE:BKRBKR4290:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05147 | 101.11 | P12:345:OKGE:BKRBKR4290:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.077 | 101.11 | P12:345:OKGE:BKRBKR4290:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.55 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.55 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05394 | 109.55 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.55 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.55 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.55 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07827 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07524 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05965 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07341 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06733 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0767 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10316 | 118.61 | P12:345:SPS:J06:1:HITCHLAND_POTTERCO___:EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05325 | 101.1 | P42:345:OKGE:SB_BOER:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05052 | 101.1 | P42:345:OKGE:SB_BOER:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05037 | 101.1 | P42:345:OKGE:SB_BOER:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05147 | 101.1 | P42:345:OKGE:SB_BOER:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.077 | 101.1 | P42:345:OKGE:SB_BOER:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07827 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07524 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05965 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07341 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06733 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0767 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10316 | 118.6 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.11 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.11 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.11 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.11 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.11 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.11 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.35 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.35 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.35 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.35 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.35 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.35 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.11 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.11 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.11 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.11 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.11 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.11 | P55:138:AEPW:NR5O.K.U:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.35 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.35 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.35 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.35 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.35 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.35 | P55:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.45 | POI 500001_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.45 | POI 500001_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.45 | POI 500001_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.45 | POI 500001_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.45 | POI 500001_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.45 | POI 500001_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.47 | POI 500001_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.47 | POI 500001_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.47 | POI 500001_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.47 | POI 500001_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.47 | POI 500001_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.47 | POI 500001_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.45 | POI 500001_2 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.45 | POI 500001_2 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.45 | POI 500001_2 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.45 | POI 500001_2 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.45 | POI 500001_2 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.45 | POI 500001_2 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.57 | POI 511456_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.57 | POI 511456_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.57 | POI 511456_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.57 | POI 511456_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.57 | POI 511456_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.57 | POI 511456_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.6 | POI 511456_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.6 | POI 511456_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.6 | POI 511456_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.6 | POI 511456_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.6 | POI 511456_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.6 | POI 511456_1 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.35 | POI 511456_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.35 | POI 511456_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.35 | POI 511456_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.35 | POI 511456_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.35 | POI 511456_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.35 | POI 511456_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.34 | POI 511456_5 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.34 | POI 511456_5 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.34 | POI 511456_5 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.34 | POI 511456_5 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.34 | POI 511456_5 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.34 | POI 511456_5 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.59 | POI 511456_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.59 | POI 511456_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.59 | POI 511456_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.59 | POI 511456_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.59 | POI 511456_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.59 | POI 511456_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 109.38 | POI 511456_7 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 109.38 | POI 511456_7 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 109.38 | POI 511456_7 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 109.38 | POI 511456_7 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 109.38 | POI 511456_7 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 109.38 | POI 511456_7 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.42 | POI 511456_8 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.42 | POI 511456_8 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.42 | POI 511456_8 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.42 | POI 511456_8 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.42 | POI 511456_8 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.42 | POI 511456_8 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05714 | 116.25 | POI 511468_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05435 | 116.25 | POI 511468_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05414 | 116.25 | POI 511468_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05149 | 116.25 | POI 511468_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05534 | 116.25 | POI 511468_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08111 | 116.25 | POI 511468_0 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05736 | 116 | POI 511468_3 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05457 | 116 | POI 511468_3 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05435 | 116 | POI 511468_3 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0517 | 116 | POI 511468_3 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05556 | 116 | POI 511468_3 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08133 | 116 | POI 511468_3 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05694 | 115.46 | POI 511468_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05415 | 115.46 | POI 511468_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05393 | 115.46 | POI 511468_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05128 | 115.46 | POI 511468_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05514 | 115.46 | POI 511468_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.08092 | 115.46 | POI 511468_4 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0772 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07427 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05898 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07246 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0665 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07569 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10169 | 117.05 | POI 523097_12 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07827 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07524 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05965 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07341 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06733 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0767 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10316 | 118.6 | POI 523097_17 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07827 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07524 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05965 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07341 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06733 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0767 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10316 | 121.63 | POI 523097_21 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07827 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07524 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05965 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07341 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06733 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0767 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10316 | 118.59 | POI 523097_24 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07827 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07524 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05965 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07341 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06733 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0767 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10316 | 118.61 | POI 523097_26 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0717 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06885 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05377 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.06706 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0612 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07024 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0959 | 106.53 | POI 523097_27 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0772 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-020 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07427 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-021 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.05898 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07246 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-028 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.0665 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-030 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.07569 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-036 | FROM->TO | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 |  | 318.7 | 0.10169 | 117.05 | POI 523097_6 - Potential P4 Event | Cumulative Impact | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-018 | FROM->TO | 525549 TOLK 7 345 3WXFMR ABBXNL844501 230 1 |  | 556 | 0.25683 | 104.59 | 525549 TOLK 7 345 3WXFMR ABB XNL8445-01 2 | TDF Impact | Tolk 345/230 kV CKT 1 Transformer Replacement
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527011 XTO_MAHONEY6 230 1 |  | 498 | 1 | 106.19 | P12:230:SPS:K79:1:YOAKUM_BRU___:HV: | TDF Impact | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527011 XTO_MAHONEY6 230 1 |  | 498 | 1 | 106.54 | P12:230:SPS:K79:1:YOAKUM_BRU___:HV: | TDF Impact | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527011 XTO_MAHONEY6 230 1 |  | 498 | 1 | 108.79 | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: | TDF Impact | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527011 XTO_MAHONEY6 230 1 |  | 498 | 1 | 109.19 | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: | TDF Impact | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527149 MUSTANG 6 230 1 |  | 498 | 1 | 102.45 | P12:230:SPS:K79:1:YOAKUM_BRU___:HV: | TDF Impact | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527149 MUSTANG 6 230 1 |  | 498 | 1 | 105.04 | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: | TDF Impact | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526784 AMOCOWASSON6 230 527149 MUSTANG 6 230 1 |  | 498 | 1 | 101.6 | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: | TDF Impact | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68814 | 100.19 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68571 | 100.35 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68572 | 100.35 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68814 | 103.13 | 527018 BENNETT 3 115 527051 ODC_TP 3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68836 | 100.43 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69514 | 103.58 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69514 | 103.82 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69514 | 104.14 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68814 | 103.56 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.71842 | 111.96 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 100.81 | 527257 FLATLAND 3 115 527258 ALG-SOLAR 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69265 | 104.38 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69271 | 104.41 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69659 | 103.25 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 104.22 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 103.43 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 103.43 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 103.31 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68871 | 100.87 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68871 | 100.87 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 103.1 | ERAS-2025-028_POI_788941_Generator_outage | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 100.87 | GEN527901 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 100.87 | GEN527902 1 | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 100.61 | P11:115:SPS:HOBBSPLT1:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 100.6 | P11:115:SPS:HOBBSPLT2:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69127 | 103.7 | P12:115:SPS:T57.1.MUSTG.SEGRVS:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68924 | 102.99 | P12:115:SPS:U01.1.MUST.SHLLCO2:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69514 | 104.07 | P12:115:SPS:U14.1.DNV:S.INKBASN:__:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68814 | 103.39 | P12:115:SPS:V49.1.YOAKUM.SHLCO2:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69131 | 103.03 | P12:115:SPS:W14.1.SMINLE.GAINES:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.69659 | 103.66 | P12:115:SPS:W35.1.GAINES.JNSDRW:::HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 1 | 108.79 | P12:230:SPS:K55:1:AMOCOWASSON_MUSTANG___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 1 | 104.55 | P12:230:SPS:K55:1:AMOCOWASSON_MUSTANG___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.79855 | 133.44 | P12:230:SPS:K56:1:YOAKUM_MUSTANG___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.71061 | 114.03 | P12:230:SPS:K69:1:MUSTANG_SEMINOLE___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68864 | 103.97 | P12:230:SPS:K82:1:BRUSUB_OXYBRU___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 1 | 112.63 | P12:230:SPS:R12:1:AMOCOWASSON_XTOMAHONEY___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 1 | 112.43 | P12:230:SPS:R12:1:AMOCOWASSON_XTOMAHONEY___:HV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68879 | 100.96 | P12:345:SPS:JXX:1:SIDWNDER_GAINES___:EHV: | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68869 | 100.72 | POI 527020_0 - Potential P4 Event | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68869 | 100.72 | POI 527020_1 - Potential P4 Event | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 |  | 470 | 0.68869 | 100.72 | POI 527020_2 - Potential P4 Event | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527009 BRU_SUB 6 230 1 | 470 |  | 0.68864 | 101.91 | System Intact | TDF Impact | YOAKUM to BRU SUB 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527149 MUSTANG 6 230 1 |  | 447 | 0.65864 | 123.89 | P12:230:SPS:K79:1:YOAKUM_BRU___:HV: | TDF Impact | YOAKUM to MUSTANG 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 526935 YOAKUM 6 230 527149 MUSTANG 6 230 1 |  | 447 | 0.65864 | 126.06 | P12:230:SPS:R11:1:BRUSUB_XTOMAHONEY___:HV: | TDF Impact | YOAKUM to MUSTANG 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68814 | 121.24 | 526934 YOAKUM 3 115 527041 ARCO_TP 3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68571 | 121.43 | 526935 YOAKUM 6 230 3WXFMR SIEM 0127501 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68572 | 121.44 | 526935 YOAKUM 6 230 3WXFMR SIEM 0147201 2 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.66 | 119.19 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68814 | 124.72 | 527018 BENNETT 3 115 527051 ODC_TP 3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68836 | 121.53 | 527028 INK_BASIN 6 230 3WXFMR ALS3798PH331 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69514 | 125.25 | 527033 XTO_CORNEL+3 115 527068 SHELLC3_TP 3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69514 | 125.53 | 527036 SHELL_C2 3 115 527068 SHELLC3_TP 3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69514 | 125.91 | 527036 SHELL_C2 3 115 527136 DENVER_S 3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68814 | 125.22 | 527051 ODC_TP 3 115 527062 SHELL_CO2 3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.72708 | 106.45 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.71842 | 135.12 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 121.98 | 527257 FLATLAND 3 115 527258 ALG-SOLAR 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69265 | 126.19 | 527276 SEMINOLE 6 230 3WXFMR SIEM 0142502 2 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69271 | 126.23 | 527276 SEMINOLE 6 230 3WXFMR SIEM 1462501 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69659 | 124.86 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 126 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 125.07 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 125.07 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 124.93 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68871 | 122.05 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68871 | 122.05 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 101.38 | 788945 ERA-2025-27 230 3WXFMR ERA-2025-27 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 102.02 | 788945 ERA-2025-27 230 3WXFMR ERA-2025-27 2 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 101.38 | ERAS-2025-027_POI_72_Generator_outage | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 102.02 | ERAS-2025-027_POI_73_Generator_outage | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 124.67 | ERAS-2025-028_POI_788941_Generator_outage | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 117.66 | GEN527161 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 117.63 | GEN527162 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 109.81 | GEN527163 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 110.2 | GEN527164 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 110.62 | GEN527165 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 113.68 | GEN527166 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 122.05 | GEN527901 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 122.05 | GEN527902 1 | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 121.74 | P11:115:SPS:HOBBSPLT1:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68864 | 121.74 | P11:115:SPS:HOBBSPLT2:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68884 | 117.66 | P11:115:SPS:MUSTANG1:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68889 | 117.63 | P11:115:SPS:MUSTANG2:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68961 | 109.81 | P11:230:SPS:MUSTANG3:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68919 | 110.2 | P11:230:SPS:MUSTANG4:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68914 | 110.61 | P11:230:SPS:MUSTANG5:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68881 | 113.68 | P11:230:SPS:MUSTANG6:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69127 | 125.39 | P12:115:SPS:T57.1.MUSTG.SEGRVS:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68924 | 124.55 | P12:115:SPS:U01.1.MUST.SHLLCO2:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69514 | 125.82 | P12:115:SPS:U14.1.DNV:S.INKBASN:__:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68814 | 125.01 | P12:115:SPS:V49.1.YOAKUM.SHLCO2:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69131 | 124.59 | P12:115:SPS:W14.1.SMINLE.GAINES:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.69659 | 125.34 | P12:115:SPS:W35.1.GAINES.JNSDRW:::HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.67805 | 120.98 | P12:230:SPS:K33:1:AMOCOSS_YOAKUM___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 1 | 131.27 | P12:230:SPS:K55:1:AMOCOWASSON_MUSTANG___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 1 | 126.39 | P12:230:SPS:K55:1:AMOCOWASSON_MUSTANG___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29WP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 471 | 1 | 107.09 | P12:230:SPS:K55:1:AMOCOWASSON_MUSTANG___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.8174 | 112.73 | P12:230:SPS:K56:1:YOAKUM_MUSTANG___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.79855 | 160.43 | P12:230:SPS:K56:1:YOAKUM_MUSTANG___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29WP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 471 | 0.79938 | 104.52 | P12:230:SPS:K56:1:YOAKUM_MUSTANG___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.71831 | 108.42 | P12:230:SPS:K69:1:MUSTANG_SEMINOLE___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.71061 | 137.57 | P12:230:SPS:K69:1:MUSTANG_SEMINOLE___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.66826 | 118.28 | P12:230:SPS:R07:1:YOAKUM_INKBASIN___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 26SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 1 | 135.8 | P12:230:SPS:R12:1:AMOCOWASSON_XTOMAHONEY___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 1 | 135.68 | P12:230:SPS:R12:1:AMOCOWASSON_XTOMAHONEY___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29WP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 471 | 1 | 114.93 | P12:230:SPS:R12:1:AMOCOWASSON_XTOMAHONEY___:HV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68286 | 120.48 | P12:345:SPS:J17:1:TUCOINT_YOAKUM34___:EHV:_A | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.67975 | 120.02 | P12:345:SPS:J18:1:YOAKUM34_HOBBSINT___:EHV:_A | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68879 | 122.15 | P12:345:SPS:JXX:1:SIDWNDER_GAINES___:EHV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68286 | 120.52 | P42:345:SPS:TUCO-NR50:::EHV: | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68286 | 120.48 | POI 525832_3 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68286 | 120.52 | POI 525832_6 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68286 | 120.5 | POI 525832_8 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68288 | 120.48 | POI 525832_9 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.67975 | 120.02 | POI 526936_0 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.66064 | 118.95 | POI 526936_2 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68869 | 121.87 | POI 527020_0 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68869 | 121.87 | POI 527020_1 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.68869 | 121.87 | POI 527020_2 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.67975 | 118.76 | POI 788939_0 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.67975 | 118.76 | POI 788939_1 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 |  | 399 | 0.67975 | 118.83 | POI 788939_2 - Potential P4 Event | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 05ALL | 1 | 29SP | ERAS-2025-027 | FROM->TO | 527009 BRU_SUB 6 230 527011 XTO_MAHONEY6 230 1 | 399 |  | 0.68864 | 123.28 | System Intact | TDF Impact | BRU SUB to XTO MAHONEY 230 kV Line Rebuild
Thermal | ERAS-2025-001 | 01NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 02NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 03NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 04NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 01NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 02NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 03NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 04NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 05ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 05NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 05ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 05ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 05NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 04ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 04ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 04ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 04ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 CF | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 00ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 00ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 00ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 00ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 00ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 CF | 00ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.38 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.38 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.38 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43917 | 131.51 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.32 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.55 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43917 | 131.51 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.32 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.55 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43917 | 131.51 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.32 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.55 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.32 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.55 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.52 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133.01 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.52 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133.01 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.52 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133.01 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133.01 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49258 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49265 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.4926 | 154.78 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49258 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49265 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.4926 | 154.78 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49258 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49265 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.4926 | 154.78 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49258 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.49265 | 156.27 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.54 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.54 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.54 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.54 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.79926 | 239.73 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.79937 | 239.25 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.7994 | 237.88 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.79926 | 239.73 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.79937 | 239.25 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.7994 | 237.88 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.79926 | 239.73 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.79937 | 239.25 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.7994 | 237.88 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.79937 | 239.25 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.7994 | 237.88 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 122.89 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 118.63 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 117.77 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 122.89 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 118.63 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 117.77 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 122.89 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 118.63 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 117.77 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 118.63 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 117.77 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.17 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.17 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.17 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.82 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.88 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.82 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.88 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.82 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.88 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.82 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.88 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.91 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 120.29 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.79 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.91 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 120.29 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.79 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.91 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 120.29 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.79 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 120.29 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.79 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.17 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.17 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.17 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.01 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.81 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 125.8 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.05 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.15 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 125.8 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.05 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.15 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 125.8 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.05 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.15 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.05 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.15 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42816 | 125.71 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42819 | 123.37 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42841 | 122.33 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42816 | 125.71 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42819 | 123.37 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42841 | 122.33 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42816 | 125.71 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42819 | 123.37 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42841 | 122.33 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42819 | 123.37 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42841 | 122.33 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43302 | 130.29 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.09 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.28 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43302 | 130.29 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.09 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.28 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43302 | 130.29 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.09 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.28 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.09 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.28 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 130.47 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 128.82 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 128.78 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 130.47 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 128.82 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 128.78 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 130.47 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 128.82 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 128.78 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 128.82 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 128.78 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.80089 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.801 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.80101 | 239.21 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.80089 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.801 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.80101 | 239.21 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.80089 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.801 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.80101 | 239.21 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.801 | 240.65 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.80101 | 239.21 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43655 | 124.68 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 121.64 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 120.79 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43655 | 124.68 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 121.64 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 120.79 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43655 | 124.68 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 121.64 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 120.79 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 121.64 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 120.79 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43655 | 125.69 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 123.47 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 122.58 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43655 | 125.69 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 123.47 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 122.58 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43655 | 125.69 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 123.47 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 122.58 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43662 | 123.47 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.4367 | 122.58 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.14 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.49 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.14 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.49 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.14 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.49 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 129.14 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.49 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 128.97 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.31 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 128.97 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.31 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 128.97 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.31 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43708 | 128.97 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43712 | 128.31 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.69885 | 190.57 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69939 | 177.36 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69881 | 176.75 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.69885 | 190.57 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69939 | 177.36 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69881 | 176.75 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.69885 | 190.57 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69939 | 177.36 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69881 | 176.75 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69939 | 177.36 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.69881 | 176.75 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.1 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.92 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.1 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.92 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.1 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.92 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.1 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.92 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 123.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 123.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 123.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 123.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 124.76 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 122.02 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 121.09 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 124.76 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 122.02 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 121.09 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 124.76 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 122.02 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 121.09 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 122.02 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 121.09 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.52 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.52 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.52 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 133 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.96 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43917 | 131.53 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.33 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43917 | 131.53 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.33 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43917 | 131.53 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.33 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43923 | 131.33 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43925 | 130.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.36 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 132.73 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.68 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.36 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 132.73 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.68 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.44486 | 134.36 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 132.73 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.68 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44491 | 132.73 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.44485 | 132.68 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 125.55 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 123.27 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 122.35 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 125.55 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 123.27 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 122.35 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43691 | 125.55 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 123.27 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 122.35 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43699 | 123.27 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43706 | 122.35 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42596 | 130.47 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42613 | 128.82 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42603 | 128.78 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42596 | 130.47 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42613 | 128.82 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42603 | 128.78 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42596 | 130.47 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42613 | 128.82 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42603 | 128.78 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42613 | 128.82 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42603 | 128.78 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 117.72 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 114.63 | GEN511851 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 114.15 | GEN511851 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.38 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.38 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43391 | 121.38 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43395 | 119.69 | GEN511852 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43402 | 119.19 | GEN511852 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.66 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.86 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.68 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.88 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.68 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.68 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.88 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 129.68 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.88 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 128.88 | POI 500001_2- Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.77 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.83 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.77 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.83 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.77 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.83 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.77 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.83 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.79 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.85 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.79 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.85 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.79 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.85 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.79 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.85 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.74 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.8 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 126.14 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.43 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.52 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 126.14 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.43 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.52 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 126.14 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.43 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.52 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.43 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.52 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 126.03 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.31 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.4 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 126.03 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.31 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.4 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42776 | 126.03 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.31 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.4 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 123.31 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 122.4 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42448 | 130.84 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42452 | 130.77 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42458 | 128.47 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42448 | 130.84 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42452 | 130.77 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42458 | 128.47 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.42448 | 130.84 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42452 | 130.77 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42458 | 128.47 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42452 | 130.77 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42458 | 128.47 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 124.79 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 123.83 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 124.79 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 123.83 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 124.79 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 123.83 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42776 | 124.79 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.42799 | 123.83 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.66 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43302 | 130.54 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.9 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.66 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43302 | 130.54 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.9 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.66 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43302 | 130.54 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.9 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43306 | 130.66 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43303 | 129.9 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.86 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 124.57 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.86 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 124.57 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.86 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 124.57 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 124.57 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.32 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.5 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.3 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.25 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.1 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.91 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.25 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.1 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.91 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43137 | 125.25 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.1 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.91 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43145 | 123.1 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43137 | 122.91 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.62 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.43 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 123.61 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.42 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.55 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.09 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.91 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.53 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.08 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.89 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.53 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.08 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.89 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 265 | 0.43136 | 125.53 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.08 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.89 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43144 | 124.08 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 |  | 235 | 0.43136 | 123.89 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43395 | 147.27 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43402 | 146.61 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 |  | 0.43391 | 143.17 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43395 | 147.27 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43402 | 146.61 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 |  | 0.43391 | 143.17 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43395 | 147.27 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43402 | 146.61 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 |  | 0.43391 | 143.17 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43395 | 147.27 | System Intact | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 |  | 0.43402 | 146.61 | System Intact | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.19 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.4396 | 131.66 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.4396 | 131.66 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.4396 | 131.66 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.12 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.32 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.12 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.32 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.12 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.32 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.12 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50742 | 168.92 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50735 | 168.44 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.5074 | 164.01 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50742 | 168.92 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50735 | 168.44 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.5074 | 164.01 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50742 | 168.92 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50735 | 168.44 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.5074 | 164.01 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50742 | 168.92 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.50735 | 168.44 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.80412 | 243 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.80399 | 242.38 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.8041 | 241.48 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.80412 | 243 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.80399 | 242.38 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.8041 | 241.48 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.80412 | 243 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.80399 | 242.38 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.8041 | 241.48 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.80412 | 243 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.8041 | 241.48 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.62 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.22 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.62 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.22 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.62 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.22 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.2 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.22 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 131.97 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 131.12 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 129.79 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 131.97 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 131.12 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 129.79 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 131.97 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 131.12 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 129.79 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 131.12 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 129.79 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 132.5 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 131.52 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.74 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 132.5 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 131.52 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.74 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 132.5 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 131.52 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.74 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 132.5 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 131.52 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 134.11 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45086 | 133.74 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 132.78 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 134.11 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45086 | 133.74 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 132.78 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 134.11 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45086 | 133.74 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 132.78 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 134.11 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 132.78 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 135.93 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45086 | 134.74 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 134.55 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 135.93 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45086 | 134.74 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 134.55 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 135.93 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45086 | 134.74 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 134.55 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45097 | 135.93 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.4509 | 134.55 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.17 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.6 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.19 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.17 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.6 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.19 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.17 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.6 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.19 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.17 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.19 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.46 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.69 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.46 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.69 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.46 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.69 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.46 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.83 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.89 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.84 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.83 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.89 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.84 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.83 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44326 | 134.89 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.84 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44333 | 135.83 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44332 | 134.84 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 135.82 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 135.82 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 135.82 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 135.82 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 134.48 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 133.81 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 133.07 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 134.48 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 133.81 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 133.07 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 134.48 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 133.81 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 133.07 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 134.48 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 133.07 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.13 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.32 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.13 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.32 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.13 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.32 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 146.13 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.77 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.4396 | 131.66 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.4396 | 131.66 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.4396 | 131.66 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43965 | 131.47 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.43967 | 130.69 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 145.81 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.46 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.14 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 145.81 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.46 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.14 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 145.81 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.46 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.46062 | 144.14 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46064 | 145.81 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.46056 | 145.46 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 135.72 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 134.6 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 134.33 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 135.72 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 134.6 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 134.33 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 135.72 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.45121 | 134.6 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 134.33 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45133 | 135.72 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.45126 | 134.33 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 126.41 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 126.66 | GEN511851 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 125.7 | GEN511851 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.19 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.19 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 265 | 0.44824 | 130.19 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44832 | 131.88 | GEN511852 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 |  | 235 | 0.44825 | 130.9 | GEN511852 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44832 | 161.72 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44825 | 160.51 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 |  | 0.44824 | 153.26 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44832 | 161.72 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44825 | 160.51 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 |  | 0.44824 | 153.26 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44832 | 161.72 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44825 | 160.51 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 |  | 0.44824 | 153.26 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44832 | 161.72 | System Intact | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 |  | 0.44825 | 160.51 | System Intact | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08644 | 100.57 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 114 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 114 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.51 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.51 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.054 | 123.39 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09238 | 123.39 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05305 | 113.82 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0915 | 113.82 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 113.65 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 113.65 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.13 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.13 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.88 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.88 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.54 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.54 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.95 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.95 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 120.09 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 120.09 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.49 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.49 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.54 | P55:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.54 | P55:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.95 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.95 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.54 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.54 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.95 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.95 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.54 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.54 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.95 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.95 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 120.09 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 120.09 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.49 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.49 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.054 | 123.39 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09238 | 123.39 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05305 | 113.82 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0915 | 113.82 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 118.22 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 118.22 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 115.66 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 115.66 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08826 | 103.5 | P12:345:OKGE:BKRBKR3670:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0882 | 109.06 | P23:345:OKGE:IF_MICO7302:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08702 | 103.73 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05301 | 104.74 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09284 | 104.74 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05177 | 101.53 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09168 | 101.53 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0738 | 118.19 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10571 | 118.19 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07217 | 115.59 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10421 | 115.59 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.73 | P42:345:OKGE:SB_MICO7311:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.75 | P42:345:OKGE:SB_MICO7381:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08824 | 104.48 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07962 | 100.09 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08716 | 100.07 | 511467 L.E.S.-4 138 511486 ELGINJT4 138 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.12634 | 107.11 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.12565 | 103.66 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 115.45 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 115.45 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 105.9 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 105.9 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07973 | 100.42 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08644 | 100.6 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08644 | 100.31 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 118.96 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 118.96 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 109.39 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.39 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 113.86 | POI 511409_0 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 113.86 | POI 511409_0 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.36 | POI 511409_0 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.36 | POI 511409_0 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 113.79 | POI 511409_1 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 113.79 | POI 511409_1 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.28 | POI 511409_1 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.28 | POI 511409_1 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 114 | POI 511409_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 114 | POI 511409_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.51 | POI 511409_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.51 | POI 511409_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 115.63 | POI 511409_4 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 115.63 | POI 511409_4 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 113.12 | POI 511409_4 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 113.12 | POI 511409_4 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 116.53 | POI 511409_5 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 116.53 | POI 511409_5 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 114 | POI 511409_5 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 114 | POI 511409_5 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 107.28 | POI 511468_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 107.28 | POI 511468_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 104.88 | POI 511468_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 104.88 | POI 511468_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 110.83 | POI 511468_5 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 110.83 | POI 511468_5 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 101.32 | POI 511468_5 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 101.32 | POI 511468_5 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 120.09 | POI 511568_1 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 120.09 | POI 511568_1 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.49 | POI 511568_1 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.49 | POI 511568_1 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.45 | POI 511568_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.45 | POI 511568_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.88 | POI 511568_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.88 | POI 511568_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.054 | 122.81 | POI 511568_3 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09238 | 122.81 | POI 511568_3 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05305 | 113.24 | POI 511568_3 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0915 | 113.24 | POI 511568_3 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.05 | POI 511568_4 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.05 | POI 511568_4 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 109.47 | POI 511568_4 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.47 | POI 511568_4 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.54 | POI 511568_5 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.54 | POI 511568_5 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 109.95 | POI 511568_5 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.95 | POI 511568_5 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.65 | POI 514801_12 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08826 | 103.92 | POI 514801_13 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.5 | POI 514801_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0882 | 109.06 | POI 514801_3 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08702 | 103.73 | POI 514801_3 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.75 | POI 514801_6 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.73 | POI 514801_9 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 115.91 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 115.91 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.35 | POI 760938_0 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.35 | POI 760938_0 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 115.91 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 115.91 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.36 | POI 760938_1 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.36 | POI 760938_1 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 115.88 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 115.88 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.33 | POI 760938_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.33 | POI 760938_2 - Potential P4 Event | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03736 | 134.16 | System Intact | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.07849 | 134.16 | System Intact | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03652 | 128.86 | System Intact | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.0777 | 128.86 | System Intact | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 124.86 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 126.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 124.86 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 126.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 124.2 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 125.97 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 124.2 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 125.97 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 130.42 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 132.15 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 130.42 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 132.15 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06229 | 129.75 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06386 | 131.72 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06007 | 129.75 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06166 | 131.72 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 124.6 | POI 511409_0 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 126.34 | POI 511409_0 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 124.6 | POI 511409_0 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 126.34 | POI 511409_0 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 124.46 | POI 511409_1 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 126.21 | POI 511409_1 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 124.46 | POI 511409_1 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 126.21 | POI 511409_1 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 124.86 | POI 511409_2 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 126.58 | POI 511409_2 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 124.86 | POI 511409_2 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 126.58 | POI 511409_2 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 127.02 | POI 511409_4 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 128.75 | POI 511409_4 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 127.02 | POI 511409_4 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 128.75 | POI 511409_4 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 128.2 | POI 511409_5 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 129.92 | POI 511409_5 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 128.2 | POI 511409_5 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 129.92 | POI 511409_5 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06268 | 124.22 | POI 511468_0 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06425 | 125.98 | POI 511468_0 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06046 | 124.22 | POI 511468_0 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06204 | 125.98 | POI 511468_0 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 115.9 | POI 511468_2 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 117.63 | POI 511468_2 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 115.9 | POI 511468_2 - Potential P4 Event | TDF Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 117.63 | POI 511468_2 - Potential P4 Event | Cumulative Impact | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 119.44 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 117.82 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 119.44 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 117.82 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 118.83 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 117.16 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 118.83 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 117.16 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 125.01 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 123.39 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 125.01 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 123.39 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06386 | 124.56 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06229 | 122.64 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06166 | 124.56 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06007 | 122.64 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 119.2 | POI 511409_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 117.56 | POI 511409_0 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 119.2 | POI 511409_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 117.56 | POI 511409_0 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 119.07 | POI 511409_1 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 117.42 | POI 511409_1 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 119.07 | POI 511409_1 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 117.42 | POI 511409_1 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 119.44 | POI 511409_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 117.82 | POI 511409_2 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 119.44 | POI 511409_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 117.82 | POI 511409_2 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 121.61 | POI 511409_4 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 119.98 | POI 511409_4 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 121.61 | POI 511409_4 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 119.98 | POI 511409_4 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 122.79 | POI 511409_5 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 121.16 | POI 511409_5 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 122.79 | POI 511409_5 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 121.16 | POI 511409_5 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06425 | 118.84 | POI 511468_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06268 | 117.18 | POI 511468_0 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06204 | 118.84 | POI 511468_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06046 | 117.18 | POI 511468_0 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06423 | 110.49 | POI 511468_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06267 | 108.83 | POI 511468_2 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06202 | 110.49 | POI 511468_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.06044 | 108.83 | POI 511468_2 - Potential P4 Event | TDF Impact | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 109.99 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 108.7 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 109.99 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 108.7 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 109.38 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 108.04 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 109.38 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 108.04 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 115.56 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 114.28 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 115.56 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 114.28 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06386 | 115.09 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06229 | 113.44 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06166 | 115.09 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06007 | 113.44 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 109.75 | POI 511409_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 108.44 | POI 511409_0 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 109.75 | POI 511409_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 108.44 | POI 511409_0 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 109.62 | POI 511409_1 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 108.3 | POI 511409_1 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 109.62 | POI 511409_1 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 108.3 | POI 511409_1 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 109.99 | POI 511409_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 108.7 | POI 511409_2 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 109.99 | POI 511409_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 108.7 | POI 511409_2 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 112.16 | POI 511409_4 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 110.87 | POI 511409_4 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 112.16 | POI 511409_4 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 110.87 | POI 511409_4 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 113.33 | POI 511409_5 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06267 | 112.05 | POI 511409_5 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 113.33 | POI 511409_5 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06044 | 112.05 | POI 511409_5 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06425 | 109.39 | POI 511468_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06268 | 108.07 | POI 511468_0 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06204 | 109.39 | POI 511468_0 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06046 | 108.07 | POI 511468_0 - Potential P4 Event | TDF Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06423 | 101.04 | POI 511468_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.06202 | 101.04 | POI 511468_2 - Potential P4 Event | Cumulative Impact | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | P11:13.8:AEPW:COM1-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 106.68 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 106.68 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 106.68 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.49 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.41 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.4396 | 172.62 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.49 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.41 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.4396 | 172.62 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.49 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.41 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.4396 | 172.62 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.49 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.41 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 118.02 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.46 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 118.02 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.46 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 118.02 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.46 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.46 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.42682 | 148.2 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42735 | 137 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42662 | 133.99 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.42682 | 148.2 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42735 | 137 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42662 | 133.99 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.42682 | 148.2 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42735 | 137 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42662 | 133.99 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42735 | 137 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.42662 | 133.99 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.72093 | 250.53 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72161 | 236.02 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72083 | 234.45 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.72093 | 250.53 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72161 | 236.02 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72083 | 234.45 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.72093 | 250.53 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72161 | 236.02 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72083 | 234.45 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72161 | 236.02 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.72083 | 234.45 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38353 | 111.6 | P12:138:AEPW:CORNVIL4:SANTAFE::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38353 | 111.6 | P12:138:AEPW:CORNVIL4:SANTAFE::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38353 | 111.6 | P12:138:AEPW:CORNVIL4:SANTAFE::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 119.36 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.55 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.45 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 119.36 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.55 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.45 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 119.36 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.55 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.45 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.55 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.45 | P12:138:AEPW:GRADY 4:SANTAFE::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 142.24 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.93 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.81 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 142.24 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.93 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.81 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 142.24 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.93 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.81 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.93 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.81 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.3689 | 112.11 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.3689 | 112.11 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.3689 | 112.11 | P12:138:AEPW:CORNVIL4:NORGE--4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 107.07 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 107.07 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 107.07 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.42 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.42 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.42 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.76 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.76 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.76 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.67 | P12:69:AEPW-OMPA:COMANC-2:OMWALTR2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.67 | P12:69:AEPW-OMPA:COMANC-2:OMWALTR2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.67 | P12:69:AEPW-OMPA:COMANC-2:OMWALTR2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.88 | P12:69:AEPW-OMPA:WALTRS-2:OMWALTR2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.88 | P12:69:AEPW-OMPA:WALTRS-2:OMWALTR2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.88 | P12:69:AEPW-OMPA:WALTRS-2:OMWALTR2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 125.63 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.86 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.49 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 125.63 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.86 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.49 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 125.63 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.86 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.49 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.86 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.49 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 111.91 | P12:69:WFEC-AEPW:COMANCH2:WALTRS-2::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 111.91 | P12:69:WFEC-AEPW:COMANCH2:WALTRS-2::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 111.91 | P12:69:WFEC-AEPW:COMANCH2:WALTRS-2::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | P12:138-13.8:AEPW:COMANC-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 107.27 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 107.27 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 107.27 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35638 | 112.07 | P13:138-345:AEPW:L.E.S.-4_#1:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35638 | 112.07 | P13:138-345:AEPW:L.E.S.-4_#1:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35638 | 112.07 | P13:138-345:AEPW:L.E.S.-4_#1:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34256 | 109.7 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34256 | 109.7 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34256 | 109.7 | P13:138-345:AEPW:L.E.S.-4_#2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 127.12 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 111.57 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 110.32 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 127.12 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 111.57 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 110.32 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 127.12 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 111.57 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 110.32 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 111.57 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 110.32 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36873 | 116.03 | P55:345:AEPW:NR4PITTSB-7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36873 | 116.03 | P55:345:AEPW:NR4PITTSB-7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36873 | 116.03 | P55:345:AEPW:NR4PITTSB-7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | P55:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.53 | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.53 | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.53 | P55:138:AEPW:NR5O.K.U:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36873 | 116.03 | P52:345:AEPW:NR4PITTSB-7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36873 | 116.03 | P52:345:AEPW:NR4PITTSB-7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36873 | 116.03 | P52:345:AEPW:NR4PITTSB-7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.53 | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.53 | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.53 | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36079 | 108.42 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36079 | 108.42 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36079 | 108.42 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35529 | 109.38 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35529 | 109.38 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35529 | 109.38 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36068 | 111.95 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36068 | 111.95 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36068 | 111.95 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37007 | 111 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37007 | 111 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37007 | 111 | P12:138:WFEC:ANADRKO_COMANCHE:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37106 | 116.68 | P12:069:WFEC:BASELN_COMCH_RSHPRNG:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37106 | 116.68 | P12:069:WFEC:BASELN_COMCH_RSHPRNG:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37106 | 116.68 | P12:069:WFEC:BASELN_COMCH_RSHPRNG:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37219 | 117.34 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.61 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37219 | 117.34 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.61 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37219 | 117.34 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.61 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.61 | P12:138:WFEC:COMACHE_LOCO:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 111.91 | P12:069:WFEC:COMACHE_WALTERS:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 111.91 | P12:069:WFEC:COMACHE_WALTERS:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 111.91 | P12:069:WFEC:COMACHE_WALTERS:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 124.13 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 106.31 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 104.94 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 124.13 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 106.31 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 104.94 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 124.13 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 106.31 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 104.94 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 106.31 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 104.94 | P12:069:WFEC:COMANCHE_DUNCAN:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.55 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.08 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.55 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.08 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.55 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.08 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.55 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.08 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.6 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.6 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.6 | 500001 COMANC7_TAP 345 511607 O.K.U.3-7 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 128.13 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 112.23 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 109.32 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 128.13 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 112.23 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 109.32 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 128.13 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 112.23 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 109.32 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 112.23 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 109.32 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 111.6 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 111.6 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 111.6 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 111.75 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 111.75 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 111.75 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 111.53 | 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 111.53 | 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 111.53 | 511423 FLE TAP4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 111.6 | 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 111.6 | 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 111.6 | 511423 FLE TAP4 138 511586 TONKAWA4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 110.57 | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 110.57 | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36707 | 110.57 | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.35 | 511436 COMANC-2 69.0 511524 L-DISTP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.35 | 511436 COMANC-2 69.0 511524 L-DISTP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.35 | 511436 COMANC-2 69.0 511524 L-DISTP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37273 | 109.51 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37273 | 109.51 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37273 | 109.51 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37273 | 110.9 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37273 | 110.9 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37273 | 110.9 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 112.09 | 511449 CORNVIL4 138 511502 N29CHIK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 112.09 | 511449 CORNVIL4 138 511502 N29CHIK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36899 | 112.09 | 511449 CORNVIL4 138 511502 N29CHIK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 111.68 | 511449 CORNVIL4 138 511516 ALEX BR4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 111.68 | 511449 CORNVIL4 138 511516 ALEX BR4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 111.68 | 511449 CORNVIL4 138 511516 ALEX BR4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 125.62 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.84 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.47 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 125.62 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.84 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.47 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 125.62 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.84 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.47 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 108.84 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 107.47 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 142.13 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.72 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.61 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 142.13 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.72 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.61 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 142.13 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.72 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.61 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 139.72 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 138.61 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 141.17 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 136.61 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 135.52 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 141.17 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 136.61 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 135.52 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 141.17 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 136.61 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 135.52 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 136.61 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 135.52 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 138.97 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 132.61 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 131.43 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 138.97 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 132.61 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 131.43 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 138.97 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 132.61 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 131.43 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 132.61 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 131.43 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 124.91 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 107.54 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 106.17 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 124.91 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 107.54 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 106.17 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.38024 | 124.91 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 107.54 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 106.17 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38081 | 107.54 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.38017 | 106.17 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36102 | 110.13 | 511467 L.E.S.-4 138 511486 ELGINJT4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36102 | 110.13 | 511467 L.E.S.-4 138 511486 ELGINJT4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36102 | 110.13 | 511467 L.E.S.-4 138 511486 ELGINJT4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 100.37 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 100.37 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 100.37 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 100.37 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 111.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 111.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 111.86 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 109.65 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 109.65 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 109.65 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.3689 | 111.44 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.3689 | 111.44 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.3689 | 111.44 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36194 | 112.12 | 511477 S.W.S.-4 138 511563 ELSWORTH 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36194 | 112.12 | 511477 S.W.S.-4 138 511563 ELSWORTH 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36194 | 112.12 | 511477 S.W.S.-4 138 511563 ELSWORTH 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 110.61 | 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 110.61 | 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36154 | 110.61 | 511477 S.W.S.-4 138 511586 TONKAWA4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36194 | 111.73 | 511486 ELGINJT4 138 511563 ELSWORTH 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36194 | 111.73 | 511486 ELGINJT4 138 511563 ELSWORTH 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36194 | 111.73 | 511486 ELGINJT4 138 511563 ELSWORTH 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 118 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.43 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 118 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.43 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 118 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.43 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.43 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 125.42 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 108.62 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 107.2 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 125.42 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 108.62 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 107.2 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 125.42 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 108.62 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 107.2 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 108.62 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 107.2 | 511491 RUSHSPT4 138 511492 SANTAFE4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 126.55 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 110.62 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 109.26 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 126.55 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 110.62 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 109.26 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 126.55 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 110.62 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 109.26 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 110.62 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 109.26 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 119.14 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.12 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.06 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 119.14 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.12 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.06 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 119.14 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.12 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.06 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 103.12 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37222 | 101.06 | 511492 SANTAFE4 138 511562 ROUNDCK4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 112.29 | 511492 SANTAFE4 138 511569 DRFTSND4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 112.29 | 511492 SANTAFE4 138 511569 DRFTSND4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 112.29 | 511492 SANTAFE4 138 511569 DRFTSND4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.57 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.51 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.4396 | 172.71 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.57 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.51 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.4396 | 172.71 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.57 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.51 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.4396 | 172.71 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43965 | 178.57 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.43967 | 177.51 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 117.93 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.3 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 117.93 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.3 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37437 | 117.93 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.3 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37493 | 101.3 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 110.69 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 110.69 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37311 | 110.69 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 112.02 | 511514 PHILPS 4 138 511515 TEXAS 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 112.02 | 511514 PHILPS 4 138 511515 TEXAS 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 112.02 | 511514 PHILPS 4 138 511515 TEXAS 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 112.02 | 511514 PHILPS 4 138 511560 GRADY 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 112.02 | 511514 PHILPS 4 138 511560 GRADY 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 112.02 | 511514 PHILPS 4 138 511560 GRADY 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 111.81 | 511515 TEXAS 4 138 511516 ALEX BR4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 111.81 | 511515 TEXAS 4 138 511516 ALEX BR4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 111.81 | 511515 TEXAS 4 138 511516 ALEX BR4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.51 | 511524 L-DISTP2 69.0 511526 L-RLITP2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.51 | 511524 L-DISTP2 69.0 511526 L-RLITP2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.51 | 511524 L-DISTP2 69.0 511526 L-RLITP2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.52 | 511526 L-RLITP2 69.0 529311 OMWALTR2 69.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.52 | 511526 L-RLITP2 69.0 529311 OMWALTR2 69.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36692 | 109.52 | 511526 L-RLITP2 69.0 529311 OMWALTR2 69.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 118.62 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 102.21 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 118.62 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 102.21 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37235 | 118.62 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 102.21 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37292 | 102.21 | 511560 GRADY 4 138 511562 ROUNDCK4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 112.28 | 511569 DRFTSND4 138 3WXFMR MPT 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 112.28 | 511569 DRFTSND4 138 3WXFMR MPT 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 112.28 | 511569 DRFTSND4 138 3WXFMR MPT 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.78 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.78 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.78 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36971 | 111.95 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36971 | 111.95 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36971 | 111.95 | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36971 | 111.74 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36971 | 111.74 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36971 | 111.74 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37162 | 116.52 | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37162 | 116.52 | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37162 | 116.52 | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37162 | 116.35 | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37162 | 116.35 | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37162 | 116.35 | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37004 | 110.89 | 520814 ANADARK4 138 520923 GEORGIA4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37004 | 110.89 | 520814 ANADARK4 138 520923 GEORGIA4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37004 | 110.89 | 520814 ANADARK4 138 520923 GEORGIA4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 111.6 | 520864 COMANCH4 138 520900 EMPIRE 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 111.6 | 520864 COMANCH4 138 520900 EMPIRE 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 111.6 | 520864 COMANCH4 138 520900 EMPIRE 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37219 | 117.28 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.54 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37219 | 117.28 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.54 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37219 | 117.28 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.54 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37281 | 100.54 | 520864 COMANCH4 138 520981 LOCO 4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 111.37 | 520900 EMPIRE 4 138 520912 FLETCH-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 111.37 | 520900 EMPIRE 4 138 520912 FLETCH-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 111.37 | 520900 EMPIRE 4 138 520912 FLETCH-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37004 | 111.11 | 520912 FLETCH-4 138 520923 GEORGIA4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37004 | 111.11 | 520912 FLETCH-4 138 520923 GEORGIA4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37004 | 111.11 | 520912 FLETCH-4 138 520923 GEORGIA4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.69 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.69 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.69 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.15 | 525832 TUCO_INT 7 345 525839 G17-151TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.15 | 525832 TUCO_INT 7 345 525839 G17-151TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.15 | 525832 TUCO_INT 7 345 525839 G17-151TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.31 | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.31 | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.31 | 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 128.94 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 114.9 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 113.67 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 128.94 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 114.9 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 113.67 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.41061 | 128.94 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 114.9 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 113.67 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41082 | 114.9 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.41054 | 113.67 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 119.62 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 107.05 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 104.83 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 119.62 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 107.05 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 104.83 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 119.62 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 107.05 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 104.83 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 107.05 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 104.83 | 529344 OMDUNE-4 138 529351 OMDUNTP1-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 118.32 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 104.57 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 102.22 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 118.32 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 104.57 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 102.22 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 118.32 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 104.57 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 102.22 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 104.57 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 102.22 | 529351 OMDUNTP1-4 138 529352 OMDUNTP2-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 116.84 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 102.23 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 116.84 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 102.23 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 116.84 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 102.23 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 102.23 | 529352 OMDUNTP2-4 138 529354 OMDUNELDER-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 122.21 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 122.21 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 122.21 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | 789744 ERA-2025-26 345 789745 ERA26-GEN1 19.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 119.85 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 103.29 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 100.71 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 119.85 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 103.29 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 100.71 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 119.85 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 103.29 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 100.71 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 103.29 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 100.71 | 789744 ERA-2025-26 345 789746 ERA26-GEN2 21.0 2 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.33192 | 128.13 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 112.23 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 109.32 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.33192 | 128.13 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 112.23 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 109.32 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.33192 | 128.13 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 112.23 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 109.32 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 112.23 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 109.32 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 122.21 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 122.21 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 122.21 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 105.79 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36983 | 103.06 | ERAS-2025-026_POI_70_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.33192 | 119.85 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 103.29 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 100.71 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.33192 | 119.85 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 103.29 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 100.71 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.33192 | 119.85 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 103.29 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 100.71 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.33255 | 103.29 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.3316 | 100.71 | ERAS-2025-026_POI_71_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | GEN511851 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | GEN511851 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 102.55 | GEN511851 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 106.68 | GEN511852 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 106.68 | GEN511852 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 106.68 | GEN511852 1 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 110.93 | MULTIGEN514941 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 110.93 | MULTIGEN514941 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.37006 | 110.93 | MULTIGEN514941 | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.74 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.39 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.74 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.39 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.74 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.39 | POI 500001_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_0 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.39 | POI 500001_0 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.74 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.38 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.74 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.38 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.74 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.38 | POI 500001_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.96 | POI 500001_1 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.38 | POI 500001_1 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.76 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.99 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.43 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.76 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.99 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.43 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 125.76 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.99 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.43 | POI 500001_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 113.99 | POI 500001_2 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 113.43 | POI 500001_2 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | POI 510907_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | POI 510907_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36865 | 116.05 | POI 510907_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | POI 510907_12 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | POI 510907_12 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36926 | 116.67 | POI 510907_12 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | POI 510907_6 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | POI 510907_6 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36993 | 116.26 | POI 510907_6 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.55 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.55 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.55 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.62 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.62 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.62 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.42 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.42 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 103.42 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 101.93 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 101.93 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 101.93 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 101.16 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 101.16 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 101.16 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | POI 511456_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | POI 511456_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | POI 511456_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | POI 511456_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | POI 511456_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | POI 511456_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | POI 511456_6 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | POI 511456_6 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.81 | POI 511456_6 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_7 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_7 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.61 | POI 511456_7 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | POI 511456_8 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | POI 511456_8 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 110.59 | POI 511456_8 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.32769 | 128.55 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32759 | 116.87 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32829 | 109.37 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.32769 | 128.55 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32759 | 116.87 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32829 | 109.37 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.32769 | 128.55 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32759 | 116.87 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32829 | 109.37 | POI 511468_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32759 | 116.87 | POI 511468_0 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.32829 | 109.37 | POI 511468_0 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 106.57 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 106.57 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.34147 | 106.57 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35038 | 109.69 | POI 511468_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.35021 | 102.49 | POI 511468_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35038 | 109.69 | POI 511468_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.35021 | 102.49 | POI 511468_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.35038 | 109.69 | POI 511468_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.35021 | 102.49 | POI 511468_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.35021 | 102.49 | POI 511468_3 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 126.88 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 117.15 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 116.69 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 126.88 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 117.15 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 116.69 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 126.88 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 117.15 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 116.69 | POI 511468_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36647 | 117.15 | POI 511468_4 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.36683 | 116.69 | POI 511468_4 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36079 | 108.42 | POI 514801_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36079 | 108.42 | POI 514801_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36079 | 108.42 | POI 514801_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.26 | POI 525832_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.26 | POI 525832_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.26 | POI 525832_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.25 | POI 525832_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.25 | POI 525832_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 108.25 | POI 525832_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36658 | 107.87 | POI 525832_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36658 | 107.87 | POI 525832_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36658 | 107.87 | POI 525832_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36662 | 108.13 | POI 525832_3 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36662 | 108.13 | POI 525832_3 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36662 | 108.13 | POI 525832_3 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 116.52 | POI 525832_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 101.04 | POI 525832_4 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 116.52 | POI 525832_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 101.04 | POI 525832_4 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36996 | 116.52 | POI 525832_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 101.04 | POI 525832_4 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37055 | 101.04 | POI 525832_4 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36992 | 116.62 | POI 525832_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37063 | 100.71 | POI 525832_5 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36992 | 116.62 | POI 525832_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37063 | 100.71 | POI 525832_5 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36992 | 116.62 | POI 525832_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37063 | 100.71 | POI 525832_5 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 173 | 0.37063 | 100.71 | POI 525832_5 - Potential P4 Event | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36992 | 116.42 | POI 525832_7 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36992 | 116.42 | POI 525832_7 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36992 | 116.42 | POI 525832_7 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.36 | POI 525839_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.36 | POI 525839_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.36 | POI 525839_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.34 | POI 525839_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.34 | POI 525839_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.34 | POI 525839_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.34 | POI 525839_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.34 | POI 525839_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.34 | POI 525839_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.78 | POI 560088_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.78 | POI 560088_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.78 | POI 560088_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.79 | POI 560088_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.79 | POI 560088_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.79 | POI 560088_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.84 | POI 560088_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.84 | POI 560088_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36884 | 111.84 | POI 560088_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_0 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_0 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_0 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_1 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_1 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_1 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_2 - Potential P4 Event | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_2 - Potential P4 Event | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 |  | 202 | 0.36663 | 109.82 | POI 762467_2 - Potential P4 Event | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 |  | 0.36996 | 122.64 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.37055 | 107.67 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.36983 | 105.18 | System Intact | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 |  | 0.36996 | 122.64 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.37055 | 107.67 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.36983 | 105.18 | System Intact | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 |  | 0.36996 | 122.64 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.37055 | 107.67 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.36983 | 105.18 | System Intact | TDF Impact | Comanche Tap-New Comanche 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.37055 | 107.67 | System Intact | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 |  | 0.36983 | 105.18 | System Intact | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08644 | 100.72 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 114.14 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 114.14 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.68 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.68 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.054 | 123.49 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09238 | 123.49 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05305 | 113.95 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0915 | 113.95 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 113.79 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 113.79 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.29 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.29 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.55 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.55 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.03 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.03 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.64 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.64 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.1 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.1 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 120.19 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 120.19 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.63 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.63 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.64 | P55:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.64 | P55:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.1 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.1 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.64 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.64 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.1 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.1 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.55 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.55 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.03 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.03 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.64 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.64 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.1 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.1 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 120.19 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 120.19 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.63 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.63 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.054 | 123.49 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09238 | 123.49 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05305 | 113.95 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0915 | 113.95 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 118.36 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 118.36 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 115.82 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 115.82 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08826 | 103.64 | P12:345:OKGE:BKRBKR3670:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0882 | 109.18 | P23:345:OKGE:IF_MICO7302:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08702 | 103.88 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05301 | 104.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09284 | 104.87 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05177 | 101.68 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09168 | 101.68 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0738 | 118.32 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10571 | 118.32 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07217 | 115.75 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10421 | 115.75 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.86 | P42:345:OKGE:SB_MICO7311:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.88 | P42:345:OKGE:SB_MICO7381:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08824 | 104.61 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07962 | 100.21 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08716 | 100.21 | 511467 L.E.S.-4 138 511486 ELGINJT4 138 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.12634 | 107.25 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.12565 | 103.82 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 115.57 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 115.57 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.06 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.06 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07973 | 100.55 | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08644 | 100.75 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08644 | 100.45 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.07 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.07 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 109.54 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.54 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 114 | POI 511409_0 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 114 | POI 511409_0 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.52 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.52 | POI 511409_0 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 113.93 | POI 511409_1 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 113.93 | POI 511409_1 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.45 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.45 | POI 511409_1 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 114.14 | POI 511409_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 114.14 | POI 511409_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 111.68 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 111.68 | POI 511409_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 115.77 | POI 511409_4 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 115.77 | POI 511409_4 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 113.28 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 113.28 | POI 511409_4 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 116.66 | POI 511409_5 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 116.66 | POI 511409_5 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 114.16 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 114.16 | POI 511409_5 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.07391 | 107.43 | POI 511468_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10585 | 107.43 | POI 511468_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0723 | 105.05 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.10438 | 105.05 | POI 511468_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 110.95 | POI 511468_5 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 110.95 | POI 511468_5 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 101.48 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 101.48 | POI 511468_5 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 120.19 | POI 511568_1 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 120.19 | POI 511568_1 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.63 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.63 | POI 511568_1 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.55 | POI 511568_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.55 | POI 511568_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.03 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.03 | POI 511568_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.054 | 122.91 | POI 511568_3 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09238 | 122.91 | POI 511568_3 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05305 | 113.38 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0915 | 113.38 | POI 511568_3 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.15 | POI 511568_4 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.15 | POI 511568_4 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 109.62 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 109.62 | POI 511568_4 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 119.64 | POI 511568_5 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 119.64 | POI 511568_5 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05308 | 110.1 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 110.1 | POI 511568_5 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.78 | POI 514801_12 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08826 | 104.05 | POI 514801_13 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.63 | POI 514801_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0882 | 109.18 | POI 514801_3 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08702 | 103.88 | POI 514801_3 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.88 | POI 514801_6 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.08825 | 103.86 | POI 514801_9 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 116.02 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 116.02 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.5 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.5 | POI 760938_0 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 116.03 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 116.03 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.51 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.51 | POI 760938_1 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05404 | 116 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09242 | 116 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05309 | 106.48 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.09154 | 106.48 | POI 760938_2 - Potential P4 Event | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03736 | 134.36 | System Intact | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.07849 | 134.36 | System Intact | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03652 | 129.1 | System Intact | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.0777 | 129.1 | System Intact | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 514941 HSL 4 138 1 |  | 382 | 0.26758 | 100.98 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 514941 HSL 4 138 1 |  | 382 | 0.26758 | 100.98 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 514941 HSL 4 138 1 |  | 382 | 0.26758 | 100.87 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 514941 HSL 4 138 1 |  | 382 | 0.26758 | 100.87 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 104.7 | P12:138:OKGE:BKRBKR1060:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 104.7 | P12:138:OKGE:BKRBKR1060:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.17837 | 106.02 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.17837 | 106.02 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 104.1 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 104.1 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 105.38 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 105.38 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.17837 | 106.11 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.17837 | 106.11 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.17837 | 105.32 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.17837 | 105.32 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 105.9 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 |  | 382 | 0.15063 | 105.9 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14051 | 100.36 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14051 | 100.36 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.13 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.13 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.6 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.6 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.53 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.53 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.6 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.6 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.53 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.53 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.13 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.13 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.53 | P12:138:OKGE:BKRBKR1060:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.53 | P12:138:OKGE:BKRBKR1060:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.3 | P12:138:OKGE:BKRBKR1060:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.3 | P12:138:OKGE:BKRBKR1060:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.95 | P12:138:OKGE:BKRBKR1080:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.95 | P12:138:OKGE:BKRBKR1080:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14249 | 104.62 | P12:138:OKGE:BKRBKR1080:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14249 | 104.62 | P12:138:OKGE:BKRBKR1080:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 123.58 | P12:138:OKGE:BKRBKR1092:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 123.58 | P12:138:OKGE:BKRBKR1092:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 124.1 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 113.81 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 124.1 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 113.81 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.19102 | 125.69 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.19102 | 125.69 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.19181 | 127 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.19258 | 116.04 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.19181 | 127 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.19258 | 116.04 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13895 | 105.66 | P12:138:OKGE:BKRBKR1300:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13895 | 105.66 | P12:138:OKGE:BKRBKR1300:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13973 | 105.65 | P12:138:OKGE:BKRBKR1300:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13973 | 105.65 | P12:138:OKGE:BKRBKR1300:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 105.19 | P12:138:OKGE:BKRBKR1390:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 105.19 | P12:138:OKGE:BKRBKR1390:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1391 | 105.33 | P12:138:OKGE:BKRBKR1390:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1391 | 105.33 | P12:138:OKGE:BKRBKR1390:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.74 | P12:345:OKGE:BKRBKR1430:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.74 | P12:345:OKGE:BKRBKR1430:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.84 | P12:345:OKGE:BKRBKR1430:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.84 | P12:345:OKGE:BKRBKR1430:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 104.4 | P12:138:OKGE:BKRBKR1440::26L_26S:HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 104.4 | P12:138:OKGE:BKRBKR1440::26L_26S:HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 104.42 | P12:138:OKGE:BKRBKR1440::26L_26S:HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 104.42 | P12:138:OKGE:BKRBKR1440::26L_26S:HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 104.75 | P12:138:OKGE:BKRBKR1440::29L_34S:HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 104.75 | P12:138:OKGE:BKRBKR1440::29L_34S:HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 104.77 | P12:138:OKGE:BKRBKR1440::29L_34S:HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 104.77 | P12:138:OKGE:BKRBKR1440::29L_34S:HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13865 | 104.57 | P12:138:OKGE:BKRBKR1690:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13865 | 104.57 | P12:138:OKGE:BKRBKR1690:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13944 | 104.69 | P12:138:OKGE:BKRBKR1690:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13944 | 104.69 | P12:138:OKGE:BKRBKR1690:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16922 | 124.12 | P12:138:OKGE:BKRBKR1760:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16922 | 124.12 | P12:138:OKGE:BKRBKR1760:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17003 | 123.81 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17075 | 115 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17003 | 123.81 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17075 | 115 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16427 | 116.74 | P12:138:OKGE:BKRBKR1780:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16427 | 116.74 | P12:138:OKGE:BKRBKR1780:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16504 | 116.23 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16572 | 108.42 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16504 | 116.23 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16572 | 108.42 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13997 | 104.6 | P12:138:OKGE:BKRBKR1785:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13997 | 104.6 | P12:138:OKGE:BKRBKR1785:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14082 | 104.62 | P12:138:OKGE:BKRBKR1785:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14082 | 104.62 | P12:138:OKGE:BKRBKR1785:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15522 | 113.57 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15522 | 113.57 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15614 | 112.37 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1567 | 105.75 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15614 | 112.37 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1567 | 105.75 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15469 | 109.44 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15469 | 109.44 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15573 | 108.05 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15631 | 102.18 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15573 | 108.05 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15631 | 102.18 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16295 | 124.7 | P12:138:OKGE:BKRBKR1920:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16295 | 124.7 | P12:138:OKGE:BKRBKR1920:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16395 | 125.22 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16479 | 114.5 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16395 | 125.22 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16479 | 114.5 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13378 | 105.35 | P12:138:OKGE:BKRBKR1930:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13378 | 105.35 | P12:138:OKGE:BKRBKR1930:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1347 | 105.81 | P12:138:OKGE:BKRBKR1930:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1347 | 105.81 | P12:138:OKGE:BKRBKR1930:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13866 | 100.62 | P12:069:OKGE:BKRBKR1940:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13866 | 100.62 | P12:069:OKGE:BKRBKR1940:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14716 | 105.17 | P12:138:OKGE-WFEC:BKRBKR2200:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14716 | 105.17 | P12:138:OKGE-WFEC:BKRBKR2200:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.148 | 104.81 | P12:138:OKGE-WFEC:BKRBKR2200:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.148 | 104.81 | P12:138:OKGE-WFEC:BKRBKR2200:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15129 | 104.83 | P12:138:OKGE:BKRBKR2240:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15129 | 104.83 | P12:138:OKGE:BKRBKR2240:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16513 | 108.64 | P12:138:OKGE:BKRBKR3270:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16513 | 108.64 | P12:138:OKGE:BKRBKR3270:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16661 | 109.1 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16725 | 100.93 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16661 | 109.1 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16725 | 100.93 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14513 | 107.92 | P12:069:OKGE:BKRBKR3290:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14513 | 107.92 | P12:069:OKGE:BKRBKR3290:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14588 | 106.83 | P12:069:OKGE:BKRBKR3290:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14588 | 106.83 | P12:069:OKGE:BKRBKR3290:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.49 | P12:345:OKGE:BKRBKR3490:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.49 | P12:345:OKGE:BKRBKR3490:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14193 | 105.39 | P12:138:OKGE-AECI:BKRBKR5070:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14193 | 105.39 | P12:138:OKGE-AECI:BKRBKR5070:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1427 | 105.1 | P12:138:OKGE-AECI:BKRBKR5070:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1427 | 105.1 | P12:138:OKGE-AECI:BKRBKR5070:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 107.11 | P12:138:OKGE-WFEC:BKRBKR6100:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 107.11 | P12:138:OKGE-WFEC:BKRBKR6100:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.56 | P12:138:OKGE-WFEC:BKRBKR6100:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14612 | 100.1 | P12:138:OKGE-WFEC:BKRBKR6100:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.56 | P12:138:OKGE-WFEC:BKRBKR6100:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14612 | 100.1 | P12:138:OKGE-WFEC:BKRBKR6100:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14197 | 100.7 | P13:138:OKGE:BKRBKR_3W022:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14197 | 100.7 | P13:138:OKGE:BKRBKR_3W022:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14305 | 100.58 | P13:138:OKGE:BKRBKR_3W022:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14305 | 100.58 | P13:138:OKGE:BKRBKR_3W022:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14513 | 108.02 | P13:069:OKGE:BKRBKR_3W030:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14513 | 108.02 | P13:069:OKGE:BKRBKR_3W030:::HV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14588 | 106.92 | P13:069:OKGE:BKRBKR_3W030:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14588 | 106.92 | P13:069:OKGE:BKRBKR_3W030:::HV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13947 | 104.67 | P23:345:OKGE:IF_MICO7302:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13947 | 104.67 | P23:345:OKGE:IF_MICO7302:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | P42:345:OKGE:SB_ARIA7381:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | P42:345:OKGE:SB_ARIA7381:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.69 | P42:345:OKGE:SB_ARIA7382:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.69 | P42:345:OKGE:SB_ARIA7382:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.71 | P42:345:OKGE:SB_ARIA7382:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.71 | P42:345:OKGE:SB_ARIA7382:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13946 | 105.48 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13946 | 105.48 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14028 | 104.94 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14028 | 104.94 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 107.11 | P12:138:WFEC:MEEKER_LINCOLN:::: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 107.11 | P12:138:WFEC:MEEKER_LINCOLN:::: | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.56 | P12:138:WFEC:MEEKER_LINCOLN:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14612 | 100.1 | P12:138:WFEC:MEEKER_LINCOLN:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.56 | P12:138:WFEC:MEEKER_LINCOLN:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14612 | 100.1 | P12:138:WFEC:MEEKER_LINCOLN:::: | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14193 | 105.2 | 300135 4LUTHER 138 300136 4MEMORALT 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14193 | 105.2 | 300135 4LUTHER 138 300136 4MEMORALT 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1427 | 104.91 | 300135 4LUTHER 138 300136 4MEMORALT 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1427 | 104.91 | 300135 4LUTHER 138 300136 4MEMORALT 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14193 | 105.36 | 300136 4MEMORALT 138 514906 JNSKAMO4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14193 | 105.36 | 300136 4MEMORALT 138 514906 JNSKAMO4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1427 | 105.08 | 300136 4MEMORALT 138 514906 JNSKAMO4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1427 | 105.08 | 300136 4MEMORALT 138 514906 JNSKAMO4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.57 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.57 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.34 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.34 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.66 | 511437 COMANC-4 138 788837 ERA-24 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.66 | 511437 COMANC-4 138 788837 ERA-24 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.36 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.36 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.22 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.22 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.57 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.57 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 106.07 | 514501 KELLYAV4 138 514835 MEMRIAL4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 106.07 | 514501 KELLYAV4 138 514835 MEMRIAL4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13904 | 105.9 | 514501 KELLYAV4 138 514835 MEMRIAL4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13904 | 105.9 | 514501 KELLYAV4 138 514835 MEMRIAL4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 105.53 | 514501 KELLYAV4 138 514872 REMPKTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 105.53 | 514501 KELLYAV4 138 514872 REMPKTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13904 | 105.34 | 514501 KELLYAV4 138 514872 REMPKTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13904 | 105.34 | 514501 KELLYAV4 138 514872 REMPKTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.23 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.23 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.02 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.02 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.56 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.56 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.35 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.35 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.142 | 106.79 | 514835 MEMRIAL4 138 514837 TENESTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.142 | 106.79 | 514835 MEMRIAL4 138 514837 TENESTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14276 | 106.49 | 514835 MEMRIAL4 138 514837 TENESTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14276 | 106.49 | 514835 MEMRIAL4 138 514837 TENESTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 122.16 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 122.16 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 122.71 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 112.6 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 122.71 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 112.6 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14041 | 104.95 | 514837 TENESTP4 138 514843 84TH ST4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14041 | 104.95 | 514837 TENESTP4 138 514843 84TH ST4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14119 | 104.75 | 514837 TENESTP4 138 514843 84TH ST4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14119 | 104.75 | 514837 TENESTP4 138 514843 84TH ST4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 123.11 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 123.11 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 123.64 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 113.41 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 123.64 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 113.41 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 124.11 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16738 | 124.11 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 124.63 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 114.27 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16747 | 124.63 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16822 | 114.27 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14041 | 104.32 | 514843 84TH ST4 138 514844 BELISLE4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14041 | 104.32 | 514843 84TH ST4 138 514844 BELISLE4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14119 | 104.12 | 514843 84TH ST4 138 514844 BELISLE4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14119 | 104.12 | 514843 84TH ST4 138 514844 BELISLE4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 104.55 | 514861 MUSTANG4 138 514896 MORGAN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 104.55 | 514861 MUSTANG4 138 514896 MORGAN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 104.35 | 514861 MUSTANG4 138 514896 MORGAN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 104.35 | 514861 MUSTANG4 138 514896 MORGAN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 105.2 | 514870 STNWAL 4 138 514872 REMPKTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13903 | 105.2 | 514870 STNWAL 4 138 514872 REMPKTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14092 | 104.02 | 514870 STNWAL 4 138 514872 REMPKTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14092 | 104.02 | 514870 STNWAL 4 138 514872 REMPKTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 105.43 | 514876 SW134TP4 138 514887 WESTMOR4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 105.43 | 514876 SW134TP4 138 514887 WESTMOR4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 105.48 | 514876 SW134TP4 138 514887 WESTMOR4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 105.48 | 514876 SW134TP4 138 514887 WESTMOR4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 104.75 | 514887 WESTMOR4 138 514925 PENN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1378 | 104.75 | 514887 WESTMOR4 138 514925 PENN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 104.77 | 514887 WESTMOR4 138 514925 PENN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13868 | 104.77 | 514887 WESTMOR4 138 514925 PENN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 105.06 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 105.06 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 104.88 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 104.88 | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 105.02 | 514893 XEROX 4 138 514896 MORGAN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 105.02 | 514893 XEROX 4 138 514896 MORGAN 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 104.84 | 514893 XEROX 4 138 514896 MORGAN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 104.84 | 514893 XEROX 4 138 514896 MORGAN 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 105.7 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13803 | 105.7 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 105.53 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13877 | 105.53 | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.7 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14006 | 106.7 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.48 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14069 | 106.48 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14242 | 105.58 | 514927 HSLEAST2 69.0 514971 GRNPAST2 69.0 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14242 | 105.58 | 514927 HSLEAST2 69.0 514971 GRNPAST2 69.0 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1434 | 104.75 | 514927 HSLEAST2 69.0 514971 GRNPAST2 69.0 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1434 | 104.75 | 514927 HSLEAST2 69.0 514971 GRNPAST2 69.0 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16922 | 126.75 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16922 | 126.75 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17003 | 126.59 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17075 | 117.42 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17003 | 126.59 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17075 | 117.42 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15206 | 110.3 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15206 | 110.3 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15306 | 108.94 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15365 | 102.54 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15306 | 108.94 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15365 | 102.54 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15522 | 113.5 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15522 | 113.5 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15614 | 112.3 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1567 | 105.65 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15614 | 112.3 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1567 | 105.65 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13757 | 104.24 | 514953 HOLLYWD4 138 514954 INDNHIL4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13757 | 104.24 | 514953 HOLLYWD4 138 514954 INDNHIL4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13838 | 104.35 | 514953 HOLLYWD4 138 514954 INDNHIL4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13838 | 104.35 | 514953 HOLLYWD4 138 514954 INDNHIL4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13838 | 104.23 | 514954 INDNHIL4 138 515380 INDIANH4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13838 | 104.23 | 514954 INDNHIL4 138 515380 INDIANH4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.12732 | 100.14 | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.12732 | 100.14 | 514959 FOSTER 4 138 515387 NEWDOMI4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13865 | 104.39 | 514961 GM 4 138 515457 AIRDEPT4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13865 | 104.39 | 514961 GM 4 138 515457 AIRDEPT4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13944 | 104.52 | 514961 GM 4 138 515457 AIRDEPT4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13944 | 104.52 | 514961 GM 4 138 515457 AIRDEPT4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16922 | 120.6 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.16922 | 120.6 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17003 | 120.05 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17075 | 111.75 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17003 | 120.05 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.17075 | 111.75 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13866 | 100.67 | 514972 RENO 2 69.0 514980 SUNNYLN2 69.0 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13866 | 100.67 | 514972 RENO 2 69.0 514980 SUNNYLN2 69.0 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13944 | 104.21 | 514984 WILDMRY4 138 515457 AIRDEPT4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13944 | 104.21 | 514984 WILDMRY4 138 515457 AIRDEPT4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15206 | 110.01 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15206 | 110.01 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15306 | 108.66 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15365 | 102.29 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15306 | 108.66 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15365 | 102.29 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15522 | 113.09 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15522 | 113.09 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15614 | 111.88 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1567 | 105.11 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15614 | 111.88 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1567 | 105.11 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14716 | 105.04 | 515047 WARWICK4 138 515366 WFROSST4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14716 | 105.04 | 515047 WARWICK4 138 515366 WFROSST4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.148 | 104.68 | 515047 WARWICK4 138 515366 WFROSST4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.148 | 104.68 | 515047 WARWICK4 138 515366 WFROSST4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15214 | 106.54 | 515059 SQUIRCK4 138 515286 STRLGTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15214 | 106.54 | 515059 SQUIRCK4 138 515286 STRLGTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15316 | 105.03 | 515059 SQUIRCK4 138 515286 STRLGTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15316 | 105.03 | 515059 SQUIRCK4 138 515286 STRLGTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15214 | 106.49 | 515075 FRSTHIL4 138 515286 STRLGTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15214 | 106.49 | 515075 FRSTHIL4 138 515286 STRLGTP4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15316 | 104.99 | 515075 FRSTHIL4 138 515286 STRLGTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.15316 | 104.99 | 515075 FRSTHIL4 138 515286 STRLGTP4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14716 | 105.16 | 515366 WFROSST4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14716 | 105.16 | 515366 WFROSST4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.148 | 104.8 | 515366 WFROSST4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.148 | 104.8 | 515366 WFROSST4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 107.15 | 515442 LINCOLN4 138 520464 MEEKER 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 107.15 | 515442 LINCOLN4 138 520464 MEEKER 4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.61 | 515442 LINCOLN4 138 520464 MEEKER 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14612 | 100.15 | 515442 LINCOLN4 138 520464 MEEKER 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.61 | 515442 LINCOLN4 138 520464 MEEKER 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14612 | 100.15 | 515442 LINCOLN4 138 520464 MEEKER 4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 106.79 | 520464 MEEKER 4 138 520994 MEEKRSW4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14472 | 106.79 | 520464 MEEKER 4 138 520994 MEEKRSW4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.24 | 520464 MEEKER 4 138 520994 MEEKRSW4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14552 | 106.24 | 520464 MEEKER 4 138 520994 MEEKRSW4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1412 | 100.19 | 520913 FRANKLN4 138 520917 FRNKLNS4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1412 | 100.19 | 520913 FRANKLN4 138 520917 FRNKLNS4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.142 | 100.53 | 520913 FRANKLN4 138 520917 FRNKLNS4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.142 | 100.53 | 520913 FRANKLN4 138 520917 FRNKLNS4 138 1 | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1412 | 100.74 | 520913 FRANKLN4 138 521028 PINK SW4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1412 | 100.74 | 520913 FRANKLN4 138 521028 PINK SW4 138 1 | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.66 | ERAS-2025-024_POI_511437_Generator_outage | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.66 | ERAS-2025-024_POI_511437_Generator_outage | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.36 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.36 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13045 | 104.57 | ERAS-2025-026_POI_511494_Generator_outage | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13045 | 104.57 | ERAS-2025-026_POI_511494_Generator_outage | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13184 | 104.34 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13184 | 104.34 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13996 | 104.67 | POI 500001_0 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13996 | 104.67 | POI 500001_0 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13996 | 104.67 | POI 500001_1 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13996 | 104.67 | POI 500001_1 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.35 | POI 500001_1 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1408 | 104.35 | POI 500001_1 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13996 | 104.67 | POI 500001_2 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13996 | 104.67 | POI 500001_2 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14075 | 104.38 | POI 500001_2 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14075 | 104.38 | POI 500001_2 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.83 | POI 511468_5 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.83 | POI 511468_5 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.53 | POI 511568_1 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.53 | POI 511568_1 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.6 | POI 511568_2 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.6 | POI 511568_2 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.2 | POI 511568_3 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.2 | POI 511568_3 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.57 | POI 511568_4 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.57 | POI 511568_4 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | POI 511568_5 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 100.61 | POI 511568_5 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13958 | 104.3 | POI 514801_13 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13958 | 104.3 | POI 514801_13 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13947 | 104.67 | POI 514801_3 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13947 | 104.67 | POI 514801_3 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.7 | POI 514908_0 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.7 | POI 514908_0 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14174 | 104.73 | POI 514908_0 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14174 | 104.73 | POI 514908_0 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.69 | POI 514908_1 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.69 | POI 514908_1 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.71 | POI 514908_1 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.71 | POI 514908_1 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | POI 514908_14 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | POI 514908_14 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | POI 514908_18 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | POI 514908_18 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.69 | POI 514908_2 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.1424 | 106.69 | POI 514908_2 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.7 | POI 514908_2 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14175 | 104.7 | POI 514908_2 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.63 | POI 514908_22 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.63 | POI 514908_22 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.63 | POI 514908_23 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.63 | POI 514908_23 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.63 | POI 514908_24 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14064 | 104.63 | POI 514908_24 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.98 | POI 514908_4 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.98 | POI 514908_4 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.97 | POI 514908_4 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.97 | POI 514908_4 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.98 | POI 514908_5 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.98 | POI 514908_5 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.97 | POI 514908_5 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.97 | POI 514908_5 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.98 | POI 514908_6 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14238 | 106.98 | POI 514908_6 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.97 | POI 514908_6 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14167 | 104.97 | POI 514908_6 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | POI 514908_9 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 104.47 | POI 514908_9 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14158 | 104.3 | POI 515497_25 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14158 | 104.3 | POI 515497_25 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.17 | POI 525832_4 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13998 | 104.17 | POI 525832_4 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.25 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.25 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.57 | POI 760938_0 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.14065 | 100.57 | POI 760938_0 - Potential P4 Event | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.25 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.25 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.24 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 |  | 287 | 0.13983 | 100.24 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 |  | 0.13998 | 102.5 | System Intact | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 |  | 0.13998 | 102.5 | System Intact | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 |  | 0.1408 | 102.42 | System Intact | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 |  | 0.1408 | 102.42 | System Intact | TDF Impact | Dunjee-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 |  | 0.03095 | 115.19 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 68 |  | 0.03093 | 110.53 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13422 | 108.89 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13422 | 108.89 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13422 | 109.53 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13422 | 109.53 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13422 | 108.19 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13422 | 108.19 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13465 | 108.88 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13514 | 101.27 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13465 | 108.88 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13514 | 101.27 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13465 | 109.52 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13514 | 101.83 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13465 | 109.52 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13514 | 101.83 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13465 | 108.16 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13514 | 100.65 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13465 | 108.16 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 |  | 287 | 0.13514 | 100.65 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 103.4 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 103.4 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.72 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.72 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.99 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.99 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P55:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P55:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P52:345:AEPW:NR4TERRYRD7:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.72 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.72 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.99 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.99 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 103.4 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 103.4 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 104.06 | P12:138:OKGE:BKRBKR1092:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 104.06 | P12:138:OKGE:BKRBKR1092:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10558 | 100.83 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10558 | 100.83 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11743 | 107.52 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11743 | 107.52 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11826 | 104.18 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11826 | 104.18 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10124 | 100.97 | P12:138:OKGE:BKRBKR1760:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10124 | 100.97 | P12:138:OKGE:BKRBKR1760:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10519 | 103.73 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10519 | 103.73 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10618 | 101.01 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10618 | 101.01 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12637 | 124.33 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12637 | 124.33 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11792 | 116.69 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11792 | 116.69 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11841 | 100.62 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11841 | 100.62 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12749 | 105.51 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12709 | 121.51 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12749 | 105.51 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12709 | 121.51 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10069 | 100.13 | P12:069:OKGE:BKRBKR3290:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10069 | 100.13 | P12:069:OKGE:BKRBKR3290:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.62 | P12:345:OKGE:BKRBKR3490:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.62 | P12:345:OKGE:BKRBKR3490:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10069 | 100.27 | P13:069:OKGE:BKRBKR_3W030:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10069 | 100.27 | P13:069:OKGE:BKRBKR_3W030:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.52 | P42:345:OKGE:SB_ARIA7381:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.52 | P42:345:OKGE:SB_ARIA7381:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09912 | 102.31 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09912 | 102.31 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09958 | 101.09 | P42:345:OKGE:SB_SEOL7385:::EHV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09958 | 101.09 | P42:345:OKGE:SB_SEOL7385:::EHV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 100.31 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 100.31 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.66 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.66 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 102.64 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 102.64 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 103.1 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 103.1 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10558 | 100.01 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10558 | 100.01 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 103.59 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10502 | 103.59 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10558 | 100.43 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10558 | 100.43 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10519 | 103.41 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10519 | 103.41 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10618 | 100.73 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10618 | 100.73 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10519 | 102.9 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10519 | 102.9 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10618 | 100.27 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.10618 | 100.27 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12637 | 124.94 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12637 | 124.94 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11792 | 117.51 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11792 | 117.51 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11841 | 101.24 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11841 | 101.24 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12749 | 106.12 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12709 | 122.32 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12749 | 106.12 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12709 | 122.32 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12637 | 123.74 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12637 | 123.74 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11792 | 115.97 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11792 | 115.97 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11841 | 100.06 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.11841 | 100.06 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12749 | 104.91 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12709 | 120.73 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12749 | 104.91 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.12709 | 120.73 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09849 | 103.3 | 515051 JACKTWN4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09849 | 103.3 | 515051 JACKTWN4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.0995 | 100.75 | 515051 JACKTWN4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.0995 | 100.75 | 515051 JACKTWN4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09849 | 102.21 | 515051 JACKTWN4 138 515532 WOLVRNT4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09849 | 102.21 | 515051 JACKTWN4 138 515532 WOLVRNT4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09849 | 101.42 | 515057 MOBIL 4 138 515532 WOLVRNT4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09849 | 101.42 | 515057 MOBIL 4 138 515532 WOLVRNT4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09608 | 100.66 | POI 511468_3 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09608 | 100.66 | POI 511468_3 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.99 | POI 511568_1 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.99 | POI 511568_1 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.72 | POI 511568_2 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.72 | POI 511568_2 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 103.32 | POI 511568_3 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 103.32 | POI 511568_3 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.86 | POI 511568_4 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.86 | POI 511568_4 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | POI 511568_5 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09613 | 102.91 | POI 511568_5 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.51 | POI 514908_14 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.51 | POI 514908_14 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.5 | POI 514908_18 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.5 | POI 514908_18 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.75 | POI 514908_22 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.75 | POI 514908_22 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.75 | POI 514908_23 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.75 | POI 514908_23 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.75 | POI 514908_24 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09761 | 100.75 | POI 514908_24 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.52 | POI 514908_9 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09763 | 100.52 | POI 514908_9 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.28 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.28 | POI 760938_0 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.28 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.28 | POI 760938_1 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.28 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 |  | 191 | 0.09615 | 101.28 | POI 760938_2 - Potential P4 Event | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.1406 | 102.12 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.1406 | 102.12 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12921 | 111.73 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12921 | 111.73 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12035 | 105.69 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12035 | 105.69 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12977 | 101.6 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12926 | 108.74 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12977 | 101.6 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.12926 | 108.74 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14287 | 108.5 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14287 | 108.5 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.1333 | 102.78 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.1333 | 102.78 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14299 | 106.17 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14299 | 106.17 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14287 | 107.79 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14287 | 107.79 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.1333 | 102.19 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.1333 | 102.19 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14299 | 105.56 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.14299 | 105.56 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.11364 | 103.64 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.11364 | 103.64 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.11373 | 100.36 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 |  | 266 | 0.11373 | 100.36 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.11502 | 111.92 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.11502 | 111.92 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.10806 | 106.81 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.10806 | 106.81 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.11563 | 100.46 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.11518 | 109.64 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.11563 | 100.46 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 |  | 0.11518 | 109.64 | System Intact | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 108.71 | P12:138:OKGE:BKRBKR1092:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 108.71 | P12:138:OKGE:BKRBKR1092:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 108.32 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 104.73 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 108.32 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 104.73 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.17963 | 112.31 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.17963 | 112.31 | P12:138:OKGE:BKRBKR1093:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1732 | 112.92 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.17412 | 108.44 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1732 | 112.92 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.17412 | 108.44 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1531 | 101.33 | P12:138:OKGE:BKRBKR1370:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1531 | 101.33 | P12:138:OKGE:BKRBKR1370:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15186 | 102.38 | P12:138:OKGE:BKRBKR1370:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15285 | 100.33 | P12:138:OKGE:BKRBKR1370:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15186 | 102.38 | P12:138:OKGE:BKRBKR1370:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15285 | 100.33 | P12:138:OKGE:BKRBKR1370:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 105.54 | P12:138:OKGE:BKRBKR1380:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 105.54 | P12:138:OKGE:BKRBKR1380:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 108.13 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 102.85 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 108.13 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 102.85 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.13088 | 101.89 | P12:138:OKGE:BKRBKR1690:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.13088 | 101.89 | P12:138:OKGE:BKRBKR1690:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18813 | 101.76 | P12:138:OKGE:BKRBKR1700:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18813 | 101.76 | P12:138:OKGE:BKRBKR1700:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18401 | 100.82 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18481 | 105.88 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18401 | 100.82 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18481 | 105.88 | P12:138:OKGE:BKRBKR1700:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15427 | 103.55 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15427 | 103.55 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15084 | 103.11 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1516 | 102.77 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15084 | 103.11 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1516 | 102.77 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.14551 | 101.15 | P12:069:OKGE:BKRBKR1940:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.14551 | 101.15 | P12:069:OKGE:BKRBKR1940:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 122.83 | P12:138:OKGE:BKRBKR4260:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 122.83 | P12:138:OKGE:BKRBKR4260:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 123.17 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 116.03 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 123.17 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 116.03 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 111.76 | P12:138:OKGE:BKRBKR4270:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 111.76 | P12:138:OKGE:BKRBKR4270:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 113.46 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 107.52 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 113.46 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 107.52 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.14153 | 101.48 | P13:069:OKGE:BKRBKR_3W031:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.14153 | 101.48 | P13:069:OKGE:BKRBKR_3W031:::HV: | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 107.1 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 107.1 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 106.78 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 103.39 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 106.78 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 103.39 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 107.91 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 107.91 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 107.5 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 104.01 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 107.5 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 104.01 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 108.77 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15866 | 108.77 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 108.25 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 104.66 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15275 | 108.25 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15365 | 104.66 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 100.37 | 514870 STNWAL 4 138 514875 OUMED 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 100.37 | 514870 STNWAL 4 138 514875 OUMED 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 103.3 | 514870 STNWAL 4 138 514875 OUMED 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 103.3 | 514870 STNWAL 4 138 514875 OUMED 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 106.43 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16902 | 106.43 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 108.63 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 103.29 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16011 | 108.63 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.16107 | 103.29 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.13074 | 100.67 | 514876 SW134TP4 138 514887 WESTMOR4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.13074 | 100.67 | 514876 SW134TP4 138 514887 WESTMOR4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18831 | 101.04 | 514933 DRAPER 4 138 515003 BARNES 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18831 | 101.04 | 514933 DRAPER 4 138 515003 BARNES 4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18419 | 100.09 | 514933 DRAPER 4 138 515003 BARNES 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18498 | 105.18 | 514933 DRAPER 4 138 515003 BARNES 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18419 | 100.09 | 514933 DRAPER 4 138 515003 BARNES 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.18498 | 105.18 | 514933 DRAPER 4 138 515003 BARNES 4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15427 | 103.47 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15427 | 103.47 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15084 | 103.03 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1516 | 102.67 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15084 | 103.03 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1516 | 102.67 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.13088 | 101.12 | 514961 GM 4 138 515457 AIRDEPT4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.13088 | 101.12 | 514961 GM 4 138 515457 AIRDEPT4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.14551 | 101.24 | 514972 RENO 2 69.0 514980 SUNNYLN2 69.0 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.14551 | 101.24 | 514972 RENO 2 69.0 514980 SUNNYLN2 69.0 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15427 | 102.99 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15427 | 102.99 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | Cumulative Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15084 | 102.55 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1516 | 102.05 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.15084 | 102.55 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 |  | 239 | 0.1516 | 102.05 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 |  | 0.1392 | 113.21 | System Intact | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 |  | 0.1392 | 113.21 | System Intact | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 |  | 0.13596 | 114.61 | System Intact | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 |  | 0.13677 | 112.85 | System Intact | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 |  | 0.13596 | 114.61 | System Intact | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 |  | 0.13677 | 112.85 | System Intact | TDF Impact | Trosper-Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12494 | 108.18 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12494 | 108.18 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12494 | 109.84 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12494 | 109.84 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12494 | 107.53 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12494 | 107.53 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12412 | 106.49 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12412 | 106.49 | P12:138:OKGE:BKRBKR1770:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12412 | 108.12 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12412 | 108.12 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12412 | 105.85 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 |  | 287 | 0.12412 | 105.85 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.12921 | 107.92 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | ERAS-2025-004 and ERAS-2025-010 Model Correction
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.12921 | 107.92 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | ERAS-2025-004 and ERAS-2025-010 Model Correction
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.12921 | 107.92 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.12921 | 107.92 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.77 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | ERAS-2025-004 and ERAS-2025-010 Model Correction
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.77 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | ERAS-2025-004 and ERAS-2025-010 Model Correction
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.77 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.77 | 514941 HSL 4 138 514987 DALE 4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.06 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | ERAS-2025-004 and ERAS-2025-010 Model Correction
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.06 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | ERAS-2025-004 and ERAS-2025-010 Model Correction
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.06 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 |  | 267 | 0.14287 | 104.06 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | Cumulative Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-014 | FROM->TO | 528526 TEAGUE 3 115 528547 S_JAL 3 115 1 |  | 154 | 0.33351 | 106.2 | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-014 | FROM->TO | 528589 DRINKARD 3 115 528603 NA_ENRICH 3 115 1 |  | 175 | 0.44335 | 108.05 | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-014 | FROM->TO | 528602 ANDREWS 3 115 528603 NA_ENRICH 3 115 1 |  | 309 | 0.97167 | 167.14 | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-014 | FROM->TO | 528602 ANDREWS 3 115 528603 NA_ENRICH 3 115 1 |  | 346 | 0.97681 | 124.92 | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-014 | FROM->TO | 528602 ANDREWS 345/115/34.5 kV Transformer |  | 448 | 0.97167 | 115.61 | P12:345:SPS:JXX:1:HOBBS_SIDWNDER___:EHV: | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03297 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03297 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531419 DOBSON3 115 531493 GANO 3 115 1 |  | 228.5 | 0.09306 | 109.19 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-014 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03018 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-016 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03023 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-026 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03065 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-002 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03068 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-024 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03102 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-004 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03323 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-010 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.03323 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-003 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.0339 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-008 | FROM->TO | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 1183 |  | 0.05332 | 102.15 | System Intact | TDF Impact | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-034 | FROM->TO | 547470 JOP145 5 161 547498 STL439 5 161 1 |  | 290 | 0.25981 | 120.85 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Joplin West 7th - Stateline 161 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 00ALL | 1 | 26SP | ERAS-2025-034 | FROM->TO | 547470 JOP145 5 161 547498 STL439 5 161 1 |  | 290 | 0.25347 | 114.48 | 547467 ORO110 5 161 547469 RIV4525 161 1 | TDF Impact | Joplin West 7th - Stateline 161 kV Line (Model Correction)
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-011 | FROM->TO | 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 |  | 1195 | 0.27316 | 115.48 | POI 659105_7 - Potential P4 Event | TDF Impact | Replacement of two disconnect switches at Antelope Valley Station
Thermal | ERAS-2025-001 | 00ALL | 1 | 29WP | ERAS-2025-012 | FROM->TO | 659101 ANTELOPE-BE3 345 659105 LELAND_O-BE3 345 1 |  | 1195 | 0.22853 | 115.48 | POI 659105_7 - Potential P4 Event | TDF Impact | Replacement of two disconnect switches at Antelope Valley Station
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-011 | FROM->TO | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 956 | 956 | 0.11964 | 102.68 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | TDF Impact | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-012 | FROM->TO | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 956 | 956 | 0.09463 | 102.68 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | TDF Impact | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-035 | FROM->TO | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 956 | 956 | 0.03425 | 102.68 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | TDF Impact | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-011 | FROM->TO | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 956 | 956 | 0.11964 | 102.68 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | TDF Impact | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-012 | FROM->TO | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 956 | 956 | 0.09463 | 102.68 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | TDF Impact | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-035 | FROM->TO | 659101 ANTELOPE-BE3 345 659183 CHARL_CK-BE3 345 1 | 956 | 956 | 0.03425 | 102.68 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | TDF Impact | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-034 | FROM->TO | 505488 CARTHAG5 161 997644 CRG X1 69.0 1 | 84 | 84 | 0.03399 | 101.74 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | TDF Impact | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-034 | FROM->TO | 505488 CARTHAG5 161 997643 CRG X2 69.0 1 | 84 | 84 | 0.03377 | 101.14 | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 | TDF Impact | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | FROM->TO | 505488 CARTHAG5 161 997570 CRG X1 69.0 1 | 84 | 84 | 0.03386 | 106.9 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | TDF Impact | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | FROM->TO | 505488 CARTHAG5 161 997569 CRG X2 69.0 1 | 84 | 84 | 0.03364 | 106.26 | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 | TDF Impact | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | TO->FROM | 505490 CARTHG 2 69.0 997570 CRG X1 69.0 1 | 84 | 84 | 0.03386 | 102.22 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | TDF Impact | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | TO->FROM | 505490 CARTHG 2 69.0 997569 CRG X2 69.0 1 | 84 | 84 | 0.03364 | 101.54 | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 | TDF Impact | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-006 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05336 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-007 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05412 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-008 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05897 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.28948 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.03914 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-034 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05967 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.28948 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-013 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05412 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-031 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05536 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-029 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05535 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | FROM->TO | 531449 HOLCOMB7 345 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.03915 | 114.2 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-006 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05336 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-007 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05412 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-008 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05897 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-015 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.28948 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.03914 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-034 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05967 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-017 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.28948 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-013 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05412 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-031 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05536 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-029 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.05535 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 531448 HOLCOMB3 115 997026 HOLCOMB 115 1 | 336 | 358.5 | 0.03915 | 112.01 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-006 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04536 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-007 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04603 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-008 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.051 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-015 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.28187 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.03135 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.05169 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.28187 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-013 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04603 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-031 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04728 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-029 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04727 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | FROM->TO | 531449 HOLCOMB7 345 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.03136 | 113.75 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-006 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04536 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-007 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04603 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-008 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.051 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-015 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.28187 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.03135 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.05169 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-017 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.28187 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-013 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04603 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-031 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04728 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-029 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.04727 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 531448 HOLCOMB3 115 996937 HOLCOMB 115 1 | 336 | 358.5 | 0.03136 | 111.52 | POI 531449_4 | TDF Impact | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2
Non-Converged | ERAS-2025-001 | 01ALL | 0 | 26SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 01ALL | 0 | 29SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 01ALL | 0 | 29WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 02ALL | 0 | 26SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 02ALL | 0 | 29SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Non-Converged | ERAS-2025-001 | 02ALL | 0 | 29WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | ERAS-2025-001 | 01ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | v
Thermal | ERAS-2025-001 | 01ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 01ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 02ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 02ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 02ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 03ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 03ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 03ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 00NR | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 00NR | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | ERAS-2025-001 | 00NR | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 03ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 03ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 03ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-002 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.0371 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-016 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03041 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-018 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03046 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-020 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03211 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-014 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03195 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-021 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03687 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.06375 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-027 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03262 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-028 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03498 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-030 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03143 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.12099 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.06254 | 105.16 | POI 514801_3 | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-002 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.0371 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-016 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03041 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-018 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03046 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-020 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03211 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-014 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03195 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-021 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03687 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.06375 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-027 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03262 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-028 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03498 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-030 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.03143 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.12099 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 241 | 283 | 0.06254 | 105.16 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | 89.8 | 89.8 | 0.0573 | 103.76 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1 | TDF Impact | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | 89.8 | 89.8 | 0.05728 | 103.76 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1 | TDF Impact | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-008 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03779 | 102.63 | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03365 | 102.63 | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-033 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03048 | 102.63 | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03365 | 102.63 | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-006 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.05536 | 101.45 | P23:345:WERE:BENT-345-110:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03841 | 101.45 | P23:345:WERE:BENT-345-110:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03841 | 101.45 | P23:345:WERE:BENT-345-110:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-006 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.05536 | 101.45 | P12:345:WERE:BENT-WICH-345:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03841 | 101.45 | P12:345:WERE:BENT-WICH-345:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | FROM->TO | 533040 EVANS N4 138 533054 MAIZE 4 138 1 | 369 | 382 | 0.03841 | 101.45 | P12:345:WERE:BENT-WICH-345:EHV: | TDF Impact | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 102.9 | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 102.9 | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 102.74 | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 102.74 | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 102.74 | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 102.74 | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 100.97 | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 100.97 | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 100.87 | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59626 | 100.87 | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 107.67 | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 107.67 | P21:115:MIDW:ST.JOHN-HUNTSVILLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 107.51 | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 107.51 | P12:115:MIDW:ST.JOHN-CIRCLE:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 107.51 | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 107.51 | P12:115:WERE:CIRC-MWE-115:HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 105.76 | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 105.76 | 530618 HUNTSVL3 115 530724 CENTENNIAL3 115 1 | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 105.66 | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 105.66 | P21:115:MIDW:HUNTSVILLE-ARK VLY JCT:::HV: | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 100.54 | 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 101 | 101 | 0.59637 | 100.54 | 530724 CENTENNIAL3 115 533412 ARKVALJ3 115 1 | TDF Impact | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-011 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 341 | 341 | 0.03949 | 104.84 | P12:345:OTP:JAMESTN3:CENTER3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-012 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 341 | 341 | 0.04539 | 104.84 | P12:345:OTP:JAMESTN3:CENTER3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-011 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 341 | 341 | 0.03933 | 101.07 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-012 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 341 | 341 | 0.0452 | 101.07 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-020 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | 435 | 435 | 0.03319 | 105.4 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | TDF Impact | Roadrunner 345/115 kV transformer #2 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-014 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | 435 | 435 | 0.03804 | 105.4 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | TDF Impact | Roadrunner 345/115 kV transformer #2 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-020 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | 435 | 435 | 0.03282 | 110.39 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | TDF Impact | Roadrunner 345/115 kV transformer #2 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-014 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | 435 | 435 | 0.03767 | 110.39 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | TDF Impact | Roadrunner 345/115 kV transformer #2 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-020 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | 435 | 435 | 0.03319 | 105.4 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | TDF Impact | Roadrunner 345/115 kV transformer #3 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-014 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | 435 | 435 | 0.03804 | 105.4 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | TDF Impact | Roadrunner 345/115 kV transformer #3 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-020 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | 435 | 435 | 0.03282 | 110.39 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | TDF Impact | Roadrunner 345/115 kV transformer #3 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-014 | FROM->TO | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 3 | 435 | 435 | 0.03767 | 110.39 | 528027 RDRUNNER 7 345 528025 RDRUNNER 3 115 2 | TDF Impact | Roadrunner 345/115 kV transformer #3 Model Correction
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 530565 SEWARD 2 69.0 996957 SEWARD T1 69.0 1 | 40 | 44.8 | 0.23433 | 106.62 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 530565 SEWARD 2 69.0 996957 SEWARD T1 69.0 1 | 40 | 44.8 | 0.23426 | 106.62 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | FROM->TO | 530679 SEWRDMW3 115 996957 SEWARD T1 69.0 1 | 40 | 44.8 | 0.23433 | 104.98 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | FROM->TO | 530679 SEWRDMW3 115 996957 SEWARD T1 69.0 1 | 40 | 44.8 | 0.23426 | 104.98 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-007 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.2649 | 111.87 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.03969 | 111.87 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-033 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.03389 | 111.87 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-034 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.03161 | 111.87 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.03969 | 111.87 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-013 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.2649 | 111.87 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-007 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.2649 | 111.38 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-015 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.03969 | 111.38 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-033 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.03389 | 111.38 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-034 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.03161 | 111.38 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-017 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.03969 | 111.38 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-013 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.2649 | 111.38 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-007 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.12856 | 105.15 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-013 | FROM->TO | 541201 SIBLEY 7 345 996797 SIBLEY11 161 11 | 400 | 440 | 0.12856 | 105.15 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-007 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.12856 | 104.5 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-013 | TO->FROM | 541202 SIBLEY 5 161 996797 SIBLEY11 161 11 | 400 | 440 | 0.12856 | 104.5 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-007 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.2628 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-015 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.04239 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.03249 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-033 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.03729 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.0342 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-017 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.04239 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-013 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.2628 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.03249 | 113.08 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-007 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.2628 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-015 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.04239 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.03249 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-033 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.03729 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-034 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.0342 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-017 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.04239 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-013 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.2628 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.03249 | 112.01 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-007 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.13136 | 110.14 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-013 | FROM->TO | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 400 | 440 | 0.13136 | 110.14 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-007 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.13136 | 109.06 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-013 | TO->FROM | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 400 | 440 | 0.13136 | 109.06 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | TDF Impact | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08284 | 121.85 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08284 | 120.45 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08284 | 118.85 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08284 | 117.24 | 511449 CORNVIL4 138 511502 N29CHIK4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08256 | 116.25 | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07425 | 125.21 | POI 514801_3 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07425 | 125.21 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0743 | 118.55 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07882 | 118.49 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07431 | 117.98 | POI 514801_13 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0743 | 117.75 | POI 514801_6 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0743 | 117.75 | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0743 | 117.55 | POI 514801_12 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0743 | 117.53 | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.0743 | 117.53 | POI 514801_9 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07431 | 117.41 | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07431 | 117.41 | POI 514801_2 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06218 | 113.37 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06218 | 113.37 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07335 | 113.01 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06237 | 112.77 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07363 | 116.94 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07363 | 116.94 | POI 514801_3 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08256 | 114.91 | 511421 VERDEN 4 138 511502 N29CHIK4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08256 | 113.39 | P12:138:AEPW:CORNVIL4:S.W.S.-4::: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07822 | 112.41 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.08256 | 111.8 | 511449 CORNVIL4 138 511502 N29CHIK4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07367 | 110.53 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07369 | 109.99 | POI 514801_13 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07368 | 109.76 | POI 514801_6 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07368 | 109.76 | P42:345:OKGE:SB_MICO7381:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07368 | 109.52 | P42:345:OKGE:SB_MICO7311:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07368 | 109.52 | POI 514801_9 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07368 | 109.5 | POI 514801_12 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07369 | 109.4 | P12:345:OKGE:BKRBKR3670:::EHV: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07368 | 109.37 | POI 514801_2 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06183 | 107.98 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06183 | 107.98 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.07314 | 107.69 | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-025 | FROM->TO | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 136 | 136 | 0.06202 | 107.41 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-032 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 40 | 40 | 0.23457 | 107.08 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 26SP | ERAS-2025-019 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 40 | 40 | 0.2345 | 107.08 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-032 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 40 | 40 | 0.23433 | 119.3 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29SP | ERAS-2025-019 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 40 | 40 | 0.23426 | 119.3 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-032 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 40 | 40 | 0.23474 | 109.1 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
Thermal | ERAS-2025-001 | 00NR | 1 | 29WP | ERAS-2025-019 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 40 | 40 | 0.23467 | 109.1 | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | TDF Impact | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03296 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03296 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03344 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03344 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03568 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-015 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-017 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.03734 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.47247 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.37139 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.36853 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.40212 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.4002 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.47302 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.40566 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.44175 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 |  | 228.5 | 0.09306 | 106.82 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 | 00ALL | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531432 PILE 3 115 531493 GANO 3 115 1 |  | 228.5 | 0.09306 | 108.27 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.3896 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82674 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.20876 | 124.4 | P12:345:OKGE:BKRBKR4290:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.47234 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.37129 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.36843 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.40201 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.40009 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.47232 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.40555 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.44163 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.3895 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82679 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2087 | 124.36 | P42:345:OKGE:SB_BOER:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30025 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.24243 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.24079 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26001 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25891 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28614 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26204 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28268 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25285 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82032 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.1491 | 112.67 | Base Case | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.35374 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28238 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28037 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30408 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30272 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33277 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30658 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33205 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29524 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82337 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.16738 | 105.53 | 515458 BORDER 7 345 526000 CRWFSHDRW7 345 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.34705 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27756 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27559 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29869 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29737 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.34703 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30112 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.32593 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29008 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82113 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.16553 | 104.86 | 275833_Dup1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33395 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26684 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26493 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28723 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28596 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.32347 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28958 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31355 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27892 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80797 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.15937 | 103.78 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30025 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.24243 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.24079 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26001 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25891 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28614 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26204 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28268 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25285 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82032 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.1491 | 102.08 | ERAS-2025-024_POI_511437_Generator_outage | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.30025 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.24243 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.24079 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26001 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25891 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28614 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26204 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28268 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25285 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.82032 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.1491 | 102.07 | 511437 COMANC-4 138 788837 ERA-24 138 1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31113 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25569 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25412 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27254 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27149 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2972 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27449 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29428 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26568 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.81883 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.16632 | 101.69 | POI 515497_26 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31113 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25569 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25412 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27254 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27149 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2972 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27449 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29428 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26568 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.81883 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.16632 | 101.69 | POI 515407_15 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.55 | P42:345:AEPW:MATO CB P000T5 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.55 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.53 | POI 511587_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.5 | POI 511587_1 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.38 | POI 511587_2 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.31 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.33012 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27157 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.26992 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28937 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28826 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31828 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29143 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31233 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.28212 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.80275 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.17677 | 100.31 | P42:345:AEPW:MATO CB P00T2 NBTB+FAULT:::: | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31135 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25591 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25434 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27276 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27171 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29741 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27471 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2945 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2659 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.81904 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.16653 | 100.01 | POI 515375_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.31135 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-016 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25591 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-018 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.25434 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-020 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27276 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-014 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27171 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.29741 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-027 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.27471 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-028 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2945 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-030 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.2659 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.81904 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-036 | FROM->TO | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | 1011 | 1176 | 0.16653 | 100.01 | POI 515407_0 | TDF Impact | COMANC7 TAP to LES 345 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.80018 | 243.17 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.79868 | 241.75 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.70292 | 176.12 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.49237 | 159.1 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43392 | 148.45 | Base Case | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.44469 | 135.46 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.44469 | 135.45 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.44469 | 135.18 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43245 | 132.92 | POI 511468_4 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43885 | 132.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.42397 | 132.7 | POI 511468_0 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43885 | 132.69 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43245 | 132.38 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43245 | 131.83 | POI 500001_1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43245 | 131.83 | POI 500001_0 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43245 | 131.83 | POI 500001_2 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43676 | 130.41 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.42942 | 130.37 | POI 511468_3 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43676 | 130.36 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43676 | 130.19 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43676 | 129.95 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.79963 | 247.45 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.79816 | 246.09 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.70315 | 182.93 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.49204 | 162.04 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.4337 | 151.49 | Base Case | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.44439 | 138.23 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.44439 | 138.23 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.44439 | 137.95 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43857 | 135.04 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43857 | 135.03 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43206 | 134.95 | POI 511468_4 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43206 | 134.34 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43206 | 134.06 | POI 500001_2 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43206 | 134.03 | POI 500001_0 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43206 | 134.03 | POI 500001_1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.42363 | 133.54 | POI 511468_0 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43651 | 132.9 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43651 | 132.85 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.43651 | 132.67 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.4337 | 132.52 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 202 | 235 | 0.4337 | 132.52 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.79903 | 250 | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.79755 | 249.04 | P12:138:AEPW:DUNCAN-4:L.E.S.-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.70235 | 195.31 | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.49176 | 159.69 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43334 | 148.34 | Base Case | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.44413 | 139.03 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.44413 | 139.03 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.44413 | 138.88 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.42329 | 136.63 | POI 511468_0 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43823 | 136.61 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43823 | 136.59 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.4318 | 136.25 | POI 511468_4 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.4318 | 136 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.4318 | 135.75 | POI 500001_2 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.4318 | 135.73 | POI 500001_1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.4318 | 135.73 | POI 500001_0 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43334 | 134.89 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43334 | 134.89 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43617 | 134.72 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43617 | 134.69 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511467 L.E.S.-4 138 1 | 237 | 265 | 0.43617 | 134.63 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.80311 | 245.65 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.50627 | 172.55 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44736 | 163.83 | Base Case | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45948 | 149.53 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45948 | 149.53 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45948 | 149.22 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 138.61 | 511428 LG-YEAR4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45045 | 138.35 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44284 | 137.45 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 137.11 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44284 | 137.08 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45045 | 136.83 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44284 | 136.82 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44284 | 136.79 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45045 | 135.59 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 135.31 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.43928 | 132.84 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.43928 | 132.83 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.80253 | 249.8 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.50574 | 174.83 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44695 | 166.09 | Base Case | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45898 | 151.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45898 | 151.65 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45898 | 151.35 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44627 | 144.79 | POI 511468_4 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44971 | 140.49 | 511428 LG-YEAR4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 140.27 | 511471 LWS-NTP4 138 511509 53CACHE4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.4425 | 139.53 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.4425 | 139.16 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44971 | 139.05 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.4425 | 138.91 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.4425 | 138.88 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 138.78 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 137.51 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44971 | 137.28 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.43899 | 135.18 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.43899 | 135.18 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.45008 | 134.25 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 202 | 235 | 0.44767 | 132.45 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.80194 | 251.91 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.50552 | 170.02 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44666 | 159.67 | Base Case | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.45879 | 149.85 | 511488 112GORE4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.45879 | 149.85 | P12:138:AEPW:112GORE4-2:SNYDER-4-2::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.45879 | 149.68 | 511500 CACHETP4 138 511510 LAIRGST4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44936 | 140.65 | 511439 LWSTAP 4 138 511512 RPPAPER4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44972 | 140.53 | 511509 53CACHE4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44218 | 140.29 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44218 | 140.09 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44218 | 140.02 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44218 | 140 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44972 | 139.78 | 511474 SHERID4 138 511537 ARTVLTP4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44936 | 139.65 | 511439 LWSTAP 4 138 511467 L.E.S.-4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44972 | 137.9 | P12:138:AEPW:L:SHERID4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.43866 | 136.75 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.43866 | 136.75 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44744 | 133.34 | P13:138-13.8:AEPW:COMANC-4_#2:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44666 | 132.8 | P11:13.8:AEPW:COM2-1:::: | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44666 | 132.8 | GEN511852 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511437 COMANC-4 138 511494 COMMTAP4 138 1 | 237 | 265 | 0.44666 | 130.41 | GEN511851 1 | TDF Impact | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 104.82 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 104.43 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 102.07 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 104.82 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 104.43 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 102.07 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 110.96 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 110.59 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 108.23 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 104.72 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 110.96 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 110.59 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 108.23 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511452 DUNCAN-2 69.0 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 104.72 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07033 | 144.39 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04744 | 144.39 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 144.15 | POI 511409_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 144.15 | POI 511409_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 144.05 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 144.05 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 142.38 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 142.38 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 142.38 | POI 511409_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 142.38 | POI 511409_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 142.36 | POI 511409_1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 142.36 | POI 511409_1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 142.21 | POI 511409_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 142.21 | POI 511409_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 142.2 | POI 511409_0 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 142.2 | POI 511409_0 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 142.19 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 142.19 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06058 | 139.52 | POI 511568_3 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03327 | 139.52 | POI 511568_3 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06058 | 139.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03327 | 139.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06058 | 139.47 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03327 | 139.47 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.96 | POI 511568_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.96 | POI 511568_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.96 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.96 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.96 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.96 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.96 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.96 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.96 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.96 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.95 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.95 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 135.95 | POI 511568_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 135.95 | POI 511568_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05331 | 110.72 | Base Case | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 137.11 | POI 511409_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 137.11 | POI 511409_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 137.02 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 137.02 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06872 | 136.96 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04556 | 136.96 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 135.42 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 135.42 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 135.42 | POI 511409_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 135.42 | POI 511409_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 135.41 | POI 511409_1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 135.41 | POI 511409_1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 135.26 | POI 511409_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 135.26 | POI 511409_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 135.21 | POI 511409_0 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 135.21 | POI 511409_0 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 135.21 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 135.21 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05954 | 129.74 | POI 511568_3 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03208 | 129.74 | POI 511568_3 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05954 | 129.68 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03208 | 129.68 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05954 | 129.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03208 | 129.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.58 | POI 511468_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.58 | POI 511468_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 126.36 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 126.36 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 126.36 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 126.36 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 126.36 | POI 511568_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 126.36 | POI 511568_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 126.36 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 126.36 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 126.36 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 126.36 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 126.27 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 126.27 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05249 | 106.47 | Base Case | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05974 | 115.8 | POI 511568_3 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03226 | 115.8 | POI 511568_3 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05974 | 115.73 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03226 | 115.73 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05974 | 115.73 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03226 | 115.73 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.89 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.89 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.89 | POI 511568_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.89 | POI 511568_5 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.89 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.89 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.89 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.89 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.89 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.89 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.82 | POI 511568_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.82 | POI 511568_2 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06935 | 114.81 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04609 | 114.81 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0694 | 114.79 | POI 511409_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04612 | 114.79 | POI 511409_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.78 | POI 511568_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03229 | 114.78 | POI 511568_4 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.75 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03229 | 114.75 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.74 | POI 511568_1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.74 | POI 511568_1 | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 114.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 114.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0694 | 114.65 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04612 | 114.65 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.07327 | 142.91 | Base Case | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03313 | 142.91 | Base Case | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08542 | 129.9 | POI 511568_3 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04771 | 129.9 | POI 511568_3 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08542 | 129.86 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04771 | 129.86 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08542 | 129.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04771 | 129.86 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09553 | 128.47 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06299 | 128.47 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 128.08 | POI 511409_4 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 128.08 | POI 511409_4 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 127.97 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 127.97 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.82 | POI 511568_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.82 | POI 511568_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.81 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.81 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.81 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.81 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.81 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.81 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.81 | POI 511568_5 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.81 | POI 511568_5 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.75 | POI 511568_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.75 | POI 511568_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.75 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.75 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.75 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.75 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 126.63 | POI 511409_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 126.63 | POI 511409_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 126.63 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 126.63 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.07222 | 135.54 | Base Case | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03194 | 135.54 | Base Case | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09344 | 120.53 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 120.53 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 120.49 | POI 511409_4 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 120.49 | POI 511409_4 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 120.42 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 120.42 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08402 | 119.24 | POI 511568_3 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04609 | 119.24 | POI 511568_3 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08402 | 119.2 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04609 | 119.2 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08402 | 119.2 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04609 | 119.2 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.1 | POI 511409_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.1 | POI 511409_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.1 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.1 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.1 | POI 511409_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.1 | POI 511409_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 118.98 | POI 511409_5 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 118.98 | POI 511409_5 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 118.97 | POI 511409_0 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 118.97 | POI 511409_0 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 118.97 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 118.97 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.32 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.32 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.32 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.32 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.32 | POI 511568_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.32 | POI 511568_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.29 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.29 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.29 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.29 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.29 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.29 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.29 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.29 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.07254 | 122.97 | Base Case | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03223 | 122.97 | Base Case | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08415 | 111.9 | POI 511568_3 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0462 | 111.9 | POI 511568_3 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08415 | 111.85 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0462 | 111.85 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08415 | 111.85 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0462 | 111.85 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.12 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.12 | POI 511568_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.12 | POI 511568_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.12 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.08 | POI 511568_5 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.08 | POI 511568_5 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.08 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.08 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.08 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.08 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.08 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.08 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 111.08 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 111.08 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 110.99 | POI 511568_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.99 | POI 511568_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 110.99 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.99 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08419 | 110.99 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.99 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0842 | 110.98 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.98 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0842 | 110.97 | POI 511568_4 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.97 | POI 511568_4 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0842 | 110.36 | POI 760938_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.36 | POI 760938_1 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0842 | 110.34 | POI 760938_0 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.34 | POI 760938_0 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.0842 | 110.32 | POI 760938_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04624 | 110.32 | POI 760938_2 | TDF Impact | Duncan-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 105.34 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 104.95 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 102.59 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 105.34 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 104.95 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997437 DUNCAN 69.0 1 | 71 | 72 | 0.03137 | 102.59 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 111.5 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 111.13 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 108.76 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 105.24 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 111.5 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 111.13 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 108.76 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511453 DUNCAN-4 138 997511 DUNCAN 69.0 1 | 71 | 72 | 0.03178 | 105.24 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07033 | 137.3 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04744 | 137.3 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 137.11 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 137.11 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 137.01 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 137.01 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 135.35 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 135.35 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 135.35 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 135.35 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 135.33 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 135.33 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 135.17 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 135.17 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 135.16 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 135.16 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.07037 | 135.12 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04748 | 135.12 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06058 | 132.44 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03327 | 132.44 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06058 | 132.39 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03327 | 132.39 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06058 | 132.39 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03327 | 132.39 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.89 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.89 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.89 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.89 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.89 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.89 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.89 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.89 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.89 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.89 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.88 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.88 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06061 | 128.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03331 | 128.88 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05331 | 103.7 | Base Case | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 130.15 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 130.15 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 130.06 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 130.06 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06872 | 129.96 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04556 | 129.96 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.47 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.47 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.47 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.47 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.47 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.47 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.31 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.31 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.26 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.26 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 128.26 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 128.26 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05954 | 122.77 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03208 | 122.77 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05954 | 122.71 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03208 | 122.71 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05954 | 122.71 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03208 | 122.71 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06882 | 121.65 | POI 511468_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04565 | 121.65 | POI 511468_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 119.4 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 119.4 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 119.4 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 119.4 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 119.4 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 119.4 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 119.4 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 119.4 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 119.4 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 119.4 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05956 | 119.32 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0321 | 119.32 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05974 | 113.38 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03226 | 113.38 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05974 | 113.31 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03226 | 113.31 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05974 | 113.31 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03226 | 113.31 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.47 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.47 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.47 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.47 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.47 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.47 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.47 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.47 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.47 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.47 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.4 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.4 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.4 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.4 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.4 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.4 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.06935 | 112.4 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04609 | 112.4 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0694 | 112.39 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04612 | 112.39 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.37 | POI 511568_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03229 | 112.37 | POI 511568_4 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.34 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03229 | 112.34 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.33 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.33 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.33 | POI 511568_1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.33 | POI 511568_1 | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.05976 | 112.33 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.03228 | 112.33 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.0694 | 112.25 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 106 | 106 | 0.04612 | 112.25 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Tap 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07033 | 127.8 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04744 | 127.8 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 127.69 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 127.69 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 127.59 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 127.59 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 125.94 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 125.94 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 125.94 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 125.94 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 125.92 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 125.92 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 125.76 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 125.76 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 125.76 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 125.76 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.07037 | 125.75 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04748 | 125.75 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06058 | 122.97 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03327 | 122.97 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06058 | 122.91 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03327 | 122.91 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06058 | 122.91 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03327 | 122.91 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.44 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.44 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.44 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.44 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.44 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.44 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.44 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.44 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.42 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06061 | 119.42 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03331 | 119.42 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 121.07 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 121.07 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 120.98 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 120.98 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06872 | 120.82 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04556 | 120.82 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 119.39 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 119.39 | POI 511409_1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 119.39 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 119.39 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 119.39 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 119.39 | POI 511409_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 119.23 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 119.23 | POI 511409_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 119.19 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 119.19 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 119.19 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 119.19 | POI 511409_0 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05954 | 113.67 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03208 | 113.67 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05954 | 113.61 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03208 | 113.61 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05954 | 113.61 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03208 | 113.61 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06882 | 112.6 | POI 511468_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04565 | 112.6 | POI 511468_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05956 | 110.32 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0321 | 110.32 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05956 | 110.32 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0321 | 110.32 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05956 | 110.32 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0321 | 110.32 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05956 | 110.32 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0321 | 110.32 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05956 | 110.32 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0321 | 110.32 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05956 | 110.24 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0321 | 110.24 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05974 | 107.71 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03226 | 107.71 | POI 511568_3 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05974 | 107.65 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03226 | 107.65 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05974 | 107.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03226 | 107.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.81 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.81 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.81 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.81 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.81 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.81 | POI 511568_5 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.81 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.81 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0694 | 106.77 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04612 | 106.77 | POI 511409_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.75 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.75 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.75 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.75 | POI 511568_2 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.75 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.75 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.06935 | 106.74 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04609 | 106.74 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.71 | POI 511568_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03229 | 106.71 | POI 511568_4 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.68 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03229 | 106.68 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.67 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.67 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.67 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.67 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.05976 | 106.67 | POI 511568_1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.03228 | 106.67 | POI 511568_1 | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.0694 | 106.62 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 106 | 106 | 0.04612 | 106.62 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.7252 | 232.02 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.43928 | 180.44 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.43928 | 180.37 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41105 | 137.94 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41105 | 137.73 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41105 | 134.61 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.43079 | 132.83 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41105 | 130.49 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36867 | 119.4 | POI 511468_4 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.33084 | 117.82 | POI 511468_0 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36867 | 116.23 | POI 500001_2 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36867 | 116.23 | POI 500001_1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36867 | 116.23 | POI 500001_0 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36867 | 116.04 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41105 | 112.43 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.38495 | 108.55 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41105 | 107.92 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.38495 | 105.48 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.38495 | 105.46 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.37409 | 104.01 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.37409 | 101.13 | Base Case | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.72566 | 242.77 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.43899 | 183.61 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.43899 | 183.52 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41113 | 143.88 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41113 | 143.67 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.43132 | 141.04 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41113 | 140.54 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41113 | 136.51 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36865 | 122.55 | POI 511468_4 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36865 | 119.64 | POI 500001_2 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36865 | 119.6 | POI 500001_0 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36865 | 119.58 | POI 500001_1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.36865 | 119.13 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41113 | 118.58 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.33103 | 115.36 | POI 511468_0 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.38547 | 115 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.41113 | 114.24 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.37473 | 112.17 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.37473 | 112.17 | 500001 COMANC7_TAP 345 789744 ERA-2025-26 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.38547 | 111.96 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 156 | 173 | 0.37473 | 109.74 | Base Case | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.72476 | 255.02 | P12:138:AEPW:COMANC-4:L.E.S.-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.43866 | 179.38 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.43866 | 179.3 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.43077 | 148.05 | P12:138:AEPW:COMANC-4:112GORE4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.41073 | 145.67 | P12:138:AEPW:SANTAFE:DUNCAN-4::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.41073 | 145.56 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.41073 | 144.59 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.41073 | 142.38 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.33042 | 132.85 | POI 511468_0 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.41073 | 132.49 | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.36837 | 131.38 | POI 511468_4 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.36837 | 130.5 | POI 500001_2 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.36837 | 130.48 | POI 500001_1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.36837 | 130.47 | POI 500001_0 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.41073 | 130.07 | 511491 RUSHSPT4 138 529307 OMMARLO4 138 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.36837 | 129.94 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.38486 | 128.19 | P13:69-138:AEPW:DUNCAN-2:::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.38486 | 126.4 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2::: | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.38486 | 126.39 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1 | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.37412 | 126.05 | ERAS-2025-026_POI_511494_Generator_outage | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | TO->FROM | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 188 | 202 | 0.37412 | 121.99 | Base Case | TDF Impact | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.07327 | 143.11 | Base Case | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03313 | 143.11 | Base Case | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08542 | 130 | POI 511568_3 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04771 | 130 | POI 511568_3 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08542 | 129.96 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04771 | 129.96 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08542 | 129.96 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04771 | 129.96 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09553 | 128.59 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06299 | 128.59 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 128.21 | POI 511409_4 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 128.21 | POI 511409_4 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 128.13 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 128.13 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.93 | POI 511568_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.93 | POI 511568_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.93 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.93 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.93 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.93 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.92 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.92 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.92 | POI 511568_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.92 | POI 511568_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.92 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.92 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.92 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.92 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.92 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.92 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.85 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.85 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.85 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.85 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08547 | 126.85 | POI 511568_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04776 | 126.85 | POI 511568_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 126.76 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 126.76 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09543 | 126.76 | POI 511409_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06291 | 126.76 | POI 511409_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.07222 | 135.77 | Base Case | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.03194 | 135.77 | Base Case | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09344 | 120.68 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 120.68 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 120.65 | POI 511409_4 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 120.65 | POI 511409_4 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 120.57 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 120.57 | P12:345:OKGE-AEPW:BKRBKR3650:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08402 | 119.37 | POI 511568_3 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04609 | 119.37 | POI 511568_3 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08402 | 119.32 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04609 | 119.32 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08402 | 119.32 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04609 | 119.32 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.26 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.26 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.26 | POI 511409_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.26 | POI 511409_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.25 | POI 511409_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.25 | POI 511409_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.13 | POI 511409_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.13 | POI 511409_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.13 | POI 511409_0 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.13 | POI 511409_0 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.09343 | 119.12 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.06054 | 119.12 | P12:345:AEPW-OKGE:L.E.S.-7:TREASILD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.45 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.45 | POI 511568_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.45 | POI 511568_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.45 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.42 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.42 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.42 | POI 511568_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.42 | POI 511568_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.08405 | 116.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 | 171 | 0.04612 | 116.42 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.07254 | 105.02 | Base Case | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.03223 | 105.02 | Base Case | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08415 | 103.56 | POI 511568_3 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0462 | 103.56 | POI 511568_3 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08415 | 103.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0462 | 103.52 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08415 | 103.52 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0462 | 103.52 | P12:345:OKGE-AEPW:BKRBKR0250:::EHV: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.85 | POI 511568_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.85 | POI 511568_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.85 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.85 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.85 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.85 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.81 | POI 511568_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.81 | POI 511568_5 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.81 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.81 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.81 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.81 | P52:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.81 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.81 | P55:345:AEPW:NR4TERRYRD7:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.72 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.72 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.72 | POI 511568_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.72 | POI 511568_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.08419 | 102.72 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.72 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB:::: | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0842 | 102.72 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.72 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0842 | 102.7 | POI 511568_4 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.7 | POI 511568_4 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0842 | 102.14 | POI 760938_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.14 | POI 760938_1 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0842 | 102.13 | POI 760938_0 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.13 | POI 760938_0 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-024 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.0842 | 102.11 | POI 760938_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-026 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 142 | 185 | 0.04624 | 102.11 | POI 760938_2 | TDF Impact | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514840 138 514941 HSL 4 138 1 | 379 | 382 | 0.26627 | 100.4 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514840 138 514941 HSL 4 138 1 | 379 | 382 | 0.26627 | 100.4 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514840 JONESTP4 138 514941 HSL 4 138 1 | 379 | 382 | 0.26627 | 100.29 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514840 JONESTP4 138 514941 HSL 4 138 1 | 379 | 382 | 0.26627 | 100.29 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 105.7 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 105.7 | 514907 ARCADIA4 138 515461 RNDBARN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.17831 | 105.36 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.17831 | 105.36 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.17831 | 105.27 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.17831 | 105.27 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 105.18 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 105.18 | 514510 BURGETT4 138 515461 RNDBARN4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.1598 | 104.6 | POI 514908_3 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-003 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.06774 | 104.6 | POI 514908_3 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.1598 | 104.6 | POI 514908_3 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.17831 | 104.57 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.17831 | 104.57 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 104.5 | P12:138:OKGE:BKRBKR1060:::HV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 104.5 | P12:138:OKGE:BKRBKR1060:::HV: | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 103.91 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514840 JONESTP4 138 515459 ACORN 4 138 1 | 382 | 382 | 0.15063 | 103.91 | 514510 BURGETT4 138 514833 DANFRTH4 138 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 122.39 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 122.39 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.19132 | 122.33 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.19132 | 122.33 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.1635 | 122 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.1635 | 122 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 120.7 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 120.7 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 120.17 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 120.17 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 119.77 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 119.77 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 119.7 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 119.7 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 118.76 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16796 | 118.76 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 116.25 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 116.25 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16507 | 112.3 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16507 | 112.3 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15559 | 109.92 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15559 | 109.92 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15559 | 109.85 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15559 | 109.85 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14586 | 109.85 | POI 514908_3 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-003 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.03646 | 109.85 | POI 514908_3 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14586 | 109.85 | POI 514908_3 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15559 | 109.44 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15559 | 109.44 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15273 | 106.1 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15273 | 106.1 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15273 | 105.81 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15273 | 105.81 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16539 | 105.38 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16539 | 105.38 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15543 | 105.28 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15543 | 105.28 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14579 | 104.37 | P13:069:OKGE:BKRBKR_3W030:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14579 | 104.37 | P13:069:OKGE:BKRBKR_3W030:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14579 | 104.27 | P12:069:OKGE:BKRBKR3290:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14579 | 104.27 | P12:069:OKGE:BKRBKR3290:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.19186 | 126.92 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.19186 | 126.92 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 125.47 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 125.47 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16348 | 125.44 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16348 | 125.44 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 123.87 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 123.87 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 123.34 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 123.34 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 122.88 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 122.88 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 122.67 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 122.67 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 121.95 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16769 | 121.95 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 118.92 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17001 | 118.92 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16506 | 114.93 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16506 | 114.93 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15557 | 112 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15557 | 112 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15557 | 111.92 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15557 | 111.92 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15557 | 111.51 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15557 | 111.51 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16602 | 109 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16602 | 109 | P12:138:OKGE:BKRBKR3270:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15276 | 107.94 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15276 | 107.94 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15276 | 107.66 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15276 | 107.66 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15548 | 106.93 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15548 | 106.93 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14583 | 106.75 | P13:069:OKGE:BKRBKR_3W030:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14583 | 106.75 | P13:069:OKGE:BKRBKR_3W030:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14583 | 106.65 | P12:069:OKGE:BKRBKR3290:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14583 | 106.65 | P12:069:OKGE:BKRBKR3290:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.13426 | 105.69 | P12:138:OKGE:BKRBKR1930:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.13426 | 105.69 | P12:138:OKGE:BKRBKR1930:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14064 | 101.64 | Base Case | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.14064 | 101.64 | Base Case | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17146 | 111.98 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17146 | 111.98 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.19349 | 111.53 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.19349 | 111.53 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16499 | 111.19 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16499 | 111.19 | P12:138:OKGE:BKRBKR1920:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17146 | 109.54 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17146 | 109.54 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 109.31 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 109.31 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 108.86 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 108.86 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 108.46 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 108.46 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 107.65 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16918 | 107.65 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17146 | 106.31 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.17146 | 106.31 | 514964 NE10TH 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16646 | 102.84 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.16646 | 102.84 | P12:138:OKGE:BKRBKR1780:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15681 | 101.44 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15681 | 101.44 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15681 | 101.34 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15681 | 101.34 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15681 | 100.81 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | 287 | 287 | 0.15681 | 100.81 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Dunjee - Reno 138 kV Ckt 1 Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03282 | 116.12 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03282 | 116.12 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03282 | 116.02 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03282 | 116.02 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03282 | 115.4 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03282 | 115.4 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03399 | 114.98 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03399 | 114.98 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03399 | 114.42 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03399 | 114.42 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03432 | 114.3 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03432 | 114.3 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03247 | 114.3 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03247 | 114.3 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03247 | 114.17 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03247 | 114.17 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03493 | 114.04 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03493 | 114.04 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03247 | 113.8 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03247 | 113.8 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 112.03 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 112.03 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 111.98 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 111.98 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 111.5 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 111.5 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 111.04 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03106 | 111.04 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03288 | 114.43 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03288 | 114.43 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03288 | 114.32 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03288 | 114.32 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03288 | 113.69 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03288 | 113.69 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03507 | 113.16 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03507 | 113.16 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03253 | 111.82 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03253 | 111.82 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03408 | 111.74 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03408 | 111.74 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03253 | 111.69 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03253 | 111.69 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03253 | 111.32 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03253 | 111.32 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03408 | 111.19 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03408 | 111.19 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03441 | 110.97 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03441 | 110.97 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 110.35 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 110.35 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 110.3 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 110.3 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 109.82 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 109.82 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 109.37 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.0311 | 109.37 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03021 | 107.8 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03021 | 107.8 | P12:138:OKGE:BKRBKR1760:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03021 | 107.57 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514927 HSLEAST2 69.0 514937 HSLWEST2 69.0 1 | 67 | 76 | 0.03021 | 107.57 | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13496 | 105.28 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13496 | 105.28 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13496 | 104.64 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13496 | 104.64 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13496 | 103.94 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13496 | 103.94 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13495 | 108.04 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13495 | 108.04 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13495 | 107.39 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13495 | 107.39 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13495 | 106.67 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514966 MIDWAY 4 138 1 | 268 | 287 | 0.13495 | 106.67 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.1263 | 114.1 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.1263 | 114.1 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.1263 | 113.49 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.1263 | 113.49 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.1263 | 112.9 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.1263 | 112.9 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12652 | 105.4 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12652 | 105.4 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12652 | 104.77 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12652 | 104.77 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12652 | 104.18 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12652 | 104.18 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12666 | 115.63 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12666 | 115.63 | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12666 | 114.81 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12666 | 114.81 | P12:138:OKGE-WFEC:BKRBKR1790:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12666 | 114.04 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 514987 DALE 4 138 1 | 191 | 191 | 0.12666 | 114.04 | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.12713 | 109.39 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.12713 | 109.39 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11317 | 109 | Base Case | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11317 | 109 | Base Case | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14115 | 104.14 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14115 | 104.14 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14115 | 103.42 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14115 | 103.42 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11144 | 102.28 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11144 | 102.28 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.12701 | 105.75 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.12701 | 105.75 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11308 | 105.07 | Base Case | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11308 | 105.07 | Base Case | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11316 | 109.56 | Base Case | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11316 | 109.56 | Base Case | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.12709 | 108.69 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.12709 | 108.69 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14123 | 104.92 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14123 | 104.92 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14123 | 104.3 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.14123 | 104.3 | 514987 DALE 4 138 515059 SQUIRCK4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11135 | 101.16 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.11135 | 101.16 | 515059 SQUIRCK4 138 515060 INGLEWD4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.10767 | 100.77 | 520913 FRANKLN4 138 520917 FRNKLNS4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | FROM->TO | 514941 HSL 4 138 515046 HAMMTAP4 138 1 | 213 | 266 | 0.10767 | 100.77 | 520913 FRANKLN4 138 520917 FRNKLNS4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 119.67 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 119.67 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 108.58 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 108.58 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.18046 | 107.59 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.18046 | 107.59 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.14028 | 107.33 | Base Case | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.14028 | 107.33 | Base Case | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 104.02 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 104.02 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 103.96 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 103.96 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 103.24 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 103.24 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 103.16 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 103.16 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 102.35 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.15972 | 102.35 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 102.34 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.16973 | 102.34 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.14657 | 100.96 | POI 514908_3 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-003 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.04789 | 100.96 | POI 514908_3 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.14657 | 100.96 | POI 514908_3 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 123.39 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 123.39 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 112.57 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 112.57 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.18068 | 111.56 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.18068 | 111.56 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.14006 | 109.79 | Base Case | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.14006 | 109.79 | Base Case | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 107.2 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 107.2 | 514875 OUMED 4 138 515963 GATEWAY4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 106.48 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 106.48 | 514840 JONESTP4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 106.42 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 106.42 | P12:138:OKGE:BKRBKR1092:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 106.33 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 106.33 | P12:138:OKGE:BKRBKR1380:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 105.63 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 105.63 | 514839 BRYANT 4 138 515459 ACORN 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 104.84 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1592 | 104.84 | 514835 MEMRIAL4 138 514839 BRYANT 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 101.28 | 514870 STNWAL 4 138 514875 OUMED 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1696 | 101.28 | 514870 STNWAL 4 138 514875 OUMED 4 138 1 | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.17126 | 110.96 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.17126 | 110.96 | P12:138:OKGE:BKRBKR4260:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1414 | 102.87 | Base Case | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.1414 | 102.87 | Base Case | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.18235 | 101.77 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.18235 | 101.77 | P12:138:OKGE:BKRBKR1093:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-010 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.17126 | 101.46 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29WP | ERAS-2025-004 | TO->FROM | 514963 TROSPER4 138 514973 RENO 4 138 1 | 191 | 239 | 0.17126 | 101.46 | P12:138:OKGE:BKRBKR4270:::HV: | TDF Impact | Trosper - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.1242 | 108.4 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.1242 | 108.4 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.1242 | 106.76 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.1242 | 106.76 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.1242 | 106.13 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.1242 | 106.13 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.12402 | 112.1 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.12402 | 112.1 | 514884 DUNJEE 4 138 514941 HSL 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.12402 | 110.42 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.12402 | 110.42 | P12:138:OKGE:BKRBKR1770:::HV: | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.12402 | 109.77 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 514964 NE10TH 4 138 514973 RENO 4 138 1 | 268 | 287 | 0.12402 | 109.77 | 514884 DUNJEE 4 138 514973 RENO 4 138 1 | TDF Impact | NE 10th - Reno 138 kV Line Rebuild
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 233 | 267 | 0.12713 | 105.59 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 233 | 267 | 0.12713 | 105.59 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 233 | 267 | 0.14115 | 100.42 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 233 | 267 | 0.14115 | 100.42 | 514941 HSL 4 138 514987 DALE 4 138 1 | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-010 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 233 | 267 | 0.12701 | 101.92 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-004 | FROM->TO | 515046 HAMMTAP4 138 515442 LINCOLN4 138 1 | 233 | 267 | 0.12701 | 101.92 | P12:138:OKGE-WFEC:BKRBKR1800:::HV: | TDF Impact | Multi - Horseshoe Lake Reconfiguration
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03381 | 100.67 | POI 511468_3 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03223 | 100.67 | POI 511468_3 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03305 | 100.67 | POI 511468_3 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.0338 | 100.28 | POI 511468_0 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03222 | 100.28 | POI 511468_0 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03304 | 100.28 | POI 511468_0 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03371 | 100.23 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03214 | 100.23 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03295 | 100.23 | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-002 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03371 | 100.12 | POI 511468_4 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-021 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03214 | 100.12 | POI 511468_4 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 26SP | ERAS-2025-026 | TO->FROM | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 96 | 106 | 0.03295 | 100.12 | POI 511468_4 | TDF Impact | Comanche 345 kV New Substation
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-015 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.15578 | 113.41 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.15578 | 113.41 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-015 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 98.4 | 98.4 | 0.05052 | 100.41 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 98.4 | 98.4 | 0.05052 | 100.41 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-015 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 211.7 | 228.5 | 0.15578 | 111.04 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-017 | FROM->TO | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 211.7 | 228.5 | 0.15578 | 111.04 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-015 | TO->FROM | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.15578 | 112.49 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-017 | TO->FROM | 531432 PILE 3 115 531493 GANO 3 115 1 | 211.7 | 228.5 | 0.15578 | 112.49 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-015 | TO->FROM | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.10194 | 104.66 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | ERAS-2025-001 CF | 00NR | 1 | 29SP | ERAS-2025-017 | TO->FROM | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 195.4 | 195.4 | 0.10194 | 104.66 | POI 531449_4 | TDF Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-002 |  | Non-Converged |  |  | 0.27192 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-016 |  | Non-Converged |  |  | 0.21695 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-018 |  | Non-Converged |  |  | 0.2154 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-020 |  | Non-Converged |  |  | 0.23366 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-014 |  | Non-Converged |  |  | 0.23262 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-021 |  | Non-Converged |  |  | 0.25577 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-027 |  | Non-Converged |  |  | 0.23559 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-028 |  | Non-Converged |  |  | 0.25522 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-030 |  | Non-Converged |  |  | 0.22686 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-026 |  | Non-Converged |  |  | 0.86341 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-036 |  | Non-Converged |  |  | 0.12836 |  | POI 511468_4 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-002 |  | Non-Converged |  |  | 0.27192 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-016 |  | Non-Converged |  |  | 0.21695 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-018 |  | Non-Converged |  |  | 0.2154 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-020 |  | Non-Converged |  |  | 0.23366 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-014 |  | Non-Converged |  |  | 0.23262 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-021 |  | Non-Converged |  |  | 0.25577 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-027 |  | Non-Converged |  |  | 0.23559 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-028 |  | Non-Converged |  |  | 0.25522 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-030 |  | Non-Converged |  |  | 0.22686 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-026 |  | Non-Converged |  |  | 0.86341 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-036 |  | Non-Converged |  |  | 0.12836 |  | POI 511468_0 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-002 |  | Non-Converged |  |  | 0.27192 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-016 |  | Non-Converged |  |  | 0.21695 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-018 |  | Non-Converged |  |  | 0.2154 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-020 |  | Non-Converged |  |  | 0.23366 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-014 |  | Non-Converged |  |  | 0.23262 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-021 |  | Non-Converged |  |  | 0.25577 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-027 |  | Non-Converged |  |  | 0.23559 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-028 |  | Non-Converged |  |  | 0.25522 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-030 |  | Non-Converged |  |  | 0.22686 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-026 |  | Non-Converged |  |  | 0.86341 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-036 |  | Non-Converged |  |  | 0.12836 |  | 500001 COMANC7_TAP 345 511468 L.E.S.-7 345 1 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-002 |  | Non-Converged |  |  | 0.27192 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-016 |  | Non-Converged |  |  | 0.21695 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-018 |  | Non-Converged |  |  | 0.2154 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-020 |  | Non-Converged |  |  | 0.23366 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-014 |  | Non-Converged |  |  | 0.23262 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-021 |  | Non-Converged |  |  | 0.25577 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-027 |  | Non-Converged |  |  | 0.23559 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-028 |  | Non-Converged |  |  | 0.25522 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-030 |  | Non-Converged |  |  | 0.22686 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-026 |  | Non-Converged |  |  | 0.86341 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Non-Converged | ERAS-2025-001 CF | 00NR | 0 | 26SP | ERAS-2025-036 |  | Non-Converged |  |  | 0.12836 |  | POI 511468_3 | TDF Impact | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP)
Thermal | JTIQ Expanded Scope | 00ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 00ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 00ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 01ALL | 1 | 26SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 01ALL | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 01ALL | 1 | 29SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 01ALL | 1 | 29WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 02ALL | 1 | 26SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 02ALL | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 02ALL | 1 | 29SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 02ALL | 1 | 29WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 03ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 03ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 03ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 03ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 04ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 04ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 05ALL | 1 | 26SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 05ALL | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 05ALL | 1 | 29SP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 05ALL | 1 | 29WP | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 01NR | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 02NR | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 03NR | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 04NR | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 05NR | 1 | 29L | N/A | " | N/A |  |  |  |  | N/A |  | N/A
Thermal | JTIQ Expanded Scope | 00NR | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 00NR | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | JTIQ Expanded Scope | 00NR | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | ERAS-2025-001 CF | 00ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 00ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 00ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 00NR | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 00NR | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 00NR | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 01ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 01ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 01ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 01ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 01ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 01ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 01ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 01ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 01ALL | 2 | 26SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | ERAS-2025-001 | 01ALL | 2 | 29SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | ERAS-2025-001 | 01ALL | 2 | 29WP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | ERAS-2025-001 | 01NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 01NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 02ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 02ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 02ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 02ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 02ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 02ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 02ALL | 2 | 26SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | ERAS-2025-001 | 02ALL | 2 | 29SP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | ERAS-2025-001 | 02ALL | 2 | 29WP | N/A | N/A | [7 empty] | N/A | N/A
Voltage | ERAS-2025-001 | 02NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 02NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 03ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 03ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 03ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 03NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 03NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 04NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 04NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 05ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 05ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 05NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 CF | 05NR | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8694 | 0.7905 | -0.0789 | 0.9018 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8815 | 0.8037 | -0.0778 | 0.9135 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8472 | 0.8044 | -0.0428 | 0.9018 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8558 | 0.8103 | -0.0455 | 0.9018 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8558 | 0.8103 | -0.0455 | 0.9018 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.8918 | 0.815 | -0.0768 | 0.9232 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8744 | 0.8157 | -0.0587 | 0.9018 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8597 | 0.8177 | -0.042 | 0.9135 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.8946 | 0.8181 | -0.0765 | 0.926 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8681 | 0.8234 | -0.0447 | 0.9135 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8681 | 0.8234 | -0.0447 | 0.9135 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.905 | 0.8266 | -0.0784 | 0.9402 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.9056 | 0.8274 | -0.0782 | 0.9406 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.9062 | 0.8276 | -0.0786 | 0.9414 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.906 | 0.8277 | -0.0783 | 0.9411 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.9065 | 0.8284 | -0.0781 | 0.9415 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.9039 | 0.8284 | -0.0755 | 0.9348 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8865 | 0.8287 | -0.0578 | 0.9135 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.8704 | 0.8292 | -0.0412 | 0.9232 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.907 | 0.8295 | -0.0775 | 0.9418 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9096 | 0.8307 | -0.0789 | 0.9449 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9093 | 0.832 | -0.0773 | 0.944 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.8732 | 0.8322 | -0.041 | 0.926 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9105 | 0.8327 | -0.0778 | 0.9454 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.8786 | 0.8348 | -0.0438 | 0.9232 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.8786 | 0.8348 | -0.0438 | 0.9232 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9127 | 0.8357 | -0.077 | 0.9472 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.8815 | 0.8378 | -0.0437 | 0.926 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.8815 | 0.8378 | -0.0437 | 0.926 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.8967 | 0.84 | -0.0567 | 0.9232 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.8828 | 0.8424 | -0.0404 | 0.9348 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.8995 | 0.843 | -0.0565 | 0.926 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.9214 | 0.846 | -0.0754 | 0.9554 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655836 OAKDALE -MK7 | 0.92 | 0.8464 | -0.0736 | 0.9503 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.9219 | 0.8465 | -0.0754 | 0.9558 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.8909 | 0.8479 | -0.043 | 0.9348 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.8909 | 0.8479 | -0.043 | 0.9348 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.9093 | 0.8499 | -0.0594 | 0.9402 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.9098 | 0.8506 | -0.0592 | 0.9406 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.9105 | 0.8509 | -0.0596 | 0.9414 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.9103 | 0.8509 | -0.0594 | 0.9411 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.9108 | 0.8516 | -0.0592 | 0.9415 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.9112 | 0.8525 | -0.0587 | 0.9418 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.9087 | 0.853 | -0.0557 | 0.9348 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9139 | 0.8541 | -0.0598 | 0.9449 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9135 | 0.8549 | -0.0586 | 0.944 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9148 | 0.8558 | -0.059 | 0.9454 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655884 DEMCKSLK-MK7 | 0.9296 | 0.8572 | -0.0724 | 0.9624 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.8973 | 0.8583 | -0.039 | 0.9402 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9169 | 0.8585 | -0.0584 | 0.9472 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.8979 | 0.8589 | -0.039 | 0.9406 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.8985 | 0.8593 | -0.0392 | 0.9414 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.8983 | 0.8593 | -0.039 | 0.9411 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.8989 | 0.8599 | -0.039 | 0.9415 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655836 OAKDALE -MK7 | 0.8995 | 0.8602 | -0.0393 | 0.9503 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.8994 | 0.8607 | -0.0387 | 0.9418 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655865 STATION8-MK7 | 0.9343 | 0.8624 | -0.0719 | 0.9669 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655864 GRAIL -MK7 | 0.9342 | 0.8624 | -0.0718 | 0.9668 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9018 | 0.8625 | -0.0393 | 0.9449 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9017 | 0.8631 | -0.0386 | 0.944 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.9049 | 0.8634 | -0.0415 | 0.9402 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.9049 | 0.8634 | -0.0415 | 0.9402 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655853 BEARCREK-MK7 | 0.9353 | 0.8638 | -0.0715 | 0.9647 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.9054 | 0.8641 | -0.0413 | 0.9406 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.9054 | 0.8641 | -0.0413 | 0.9406 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9029 | 0.8641 | -0.0388 | 0.9454 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.9058 | 0.8644 | -0.0414 | 0.9411 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.9058 | 0.8644 | -0.0414 | 0.9411 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.906 | 0.8645 | -0.0415 | 0.9414 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.906 | 0.8645 | -0.0415 | 0.9414 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.9063 | 0.865 | -0.0413 | 0.9415 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.9063 | 0.865 | -0.0413 | 0.9415 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655836 OAKDALE -MK7 | 0.9074 | 0.8656 | -0.0418 | 0.9503 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655836 OAKDALE -MK7 | 0.9074 | 0.8656 | -0.0418 | 0.9503 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.9068 | 0.8658 | -0.041 | 0.9418 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.9068 | 0.8658 | -0.041 | 0.9418 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655832 BLUEBUTE-MK7 | 0.9376 | 0.866 | -0.0716 | 0.9701 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9051 | 0.8668 | -0.0383 | 0.9472 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9094 | 0.8677 | -0.0417 | 0.9449 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9094 | 0.8677 | -0.0417 | 0.9449 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.9045 | 0.8677 | -0.0368 | 0.9402 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9091 | 0.8682 | -0.0409 | 0.944 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9091 | 0.8682 | -0.0409 | 0.944 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.9256 | 0.8683 | -0.0573 | 0.9554 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.905 | 0.8683 | -0.0367 | 0.9406 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.9055 | 0.8687 | -0.0368 | 0.9411 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.926 | 0.8688 | -0.0572 | 0.9558 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.9057 | 0.8688 | -0.0369 | 0.9414 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655883 GALAXY -MK7 | 0.9403 | 0.8689 | -0.0714 | 0.9727 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9103 | 0.8692 | -0.0411 | 0.9454 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9103 | 0.8692 | -0.0411 | 0.9454 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.906 | 0.8693 | -0.0367 | 0.9415 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655849 VEEDER -MK7 | 0.941 | 0.8697 | -0.0713 | 0.9733 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655882 GALAXYTP-MK7 | 0.941 | 0.8697 | -0.0713 | 0.9734 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.9064 | 0.87 | -0.0364 | 0.9418 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655836 OAKDALE -MK7 | 0.9247 | 0.8705 | -0.0542 | 0.9503 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655897 COYOTCHR-MK7 | 0.9424 | 0.8712 | -0.0712 | 0.9747 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655880 SCHAFR_T-MK7 | 0.9428 | 0.8717 | -0.0711 | 0.9751 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9125 | 0.8718 | -0.0407 | 0.9472 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9125 | 0.8718 | -0.0407 | 0.9472 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655890 WERNER -MK7 | 0.9422 | 0.8719 | -0.0703 | 0.9712 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.909 | 0.872 | -0.037 | 0.9449 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655894 HALLIDAY-MK7 | 0.9423 | 0.872 | -0.0703 | 0.9713 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655899 FNCYBTAP-MK7 | 0.9432 | 0.8722 | -0.071 | 0.9755 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9087 | 0.8724 | -0.0363 | 0.944 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.91 | 0.8734 | -0.0366 | 0.9454 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655893 DUNNCNTR-MK7 | 0.9437 | 0.8736 | -0.0701 | 0.9727 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655881 DAP_____-MK7 | 0.9463 | 0.8755 | -0.0708 | 0.9784 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659388 KUMMERDG-MK7 | 0.9465 | 0.8758 | -0.0707 | 0.9787 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9121 | 0.876 | -0.0361 | 0.9472 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.914 | 0.8764 | -0.0376 | 0.9554 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.9145 | 0.8769 | -0.0376 | 0.9558 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655853 BEARCREK-MK7 | 0.9153 | 0.8773 | -0.038 | 0.9647 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655884 DEMCKSLK-MK7 | 0.9335 | 0.8785 | -0.055 | 0.9624 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659385 ROUNDUP_-MK7 | 0.9488 | 0.8791 | -0.0697 | 0.9775 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.9213 | 0.8813 | -0.04 | 0.9554 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.9213 | 0.8813 | -0.04 | 0.9554 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.9217 | 0.8818 | -0.0399 | 0.9558 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.9217 | 0.8818 | -0.0399 | 0.9558 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655853 BEARCREK-MK7 | 0.923 | 0.8825 | -0.0405 | 0.9647 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655853 BEARCREK-MK7 | 0.923 | 0.8825 | -0.0405 | 0.9647 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655865 STATION8-MK7 | 0.9383 | 0.8836 | -0.0547 | 0.9669 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655864 GRAIL -MK7 | 0.9382 | 0.8836 | -0.0546 | 0.9668 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655894 HALLIDAY-MK7 | 0.9227 | 0.8853 | -0.0374 | 0.9713 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655890 WERNER -MK7 | 0.9226 | 0.8853 | -0.0373 | 0.9712 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.9209 | 0.8854 | -0.0355 | 0.9554 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659143 BLAISDEL-BE4 | 0.9636 | 0.8856 | -0.078 | 1.0074 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.9213 | 0.8859 | -0.0354 | 0.9558 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655891 KILLDEER-MK7 | 0.9403 | 0.8862 | -0.0541 | 0.9692 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655884 DEMCKSLK-MK7 | 0.9224 | 0.8863 | -0.0361 | 0.9624 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 652419 KILDEER7 | 0.9408 | 0.8867 | -0.0541 | 0.9696 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655893 DUNNCNTR-MK7 | 0.9241 | 0.8869 | -0.0372 | 0.9727 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655832 BLUEBUTE-MK7 | 0.9415 | 0.8871 | -0.0544 | 0.9701 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655853 BEARCREK-MK7 | 0.9399 | 0.8873 | -0.0526 | 0.9647 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659387 KUMMERDG-BE3 | 0.9575 | 0.8891 | -0.0684 | 0.9888 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659248 HALLIDAY-UM7 | 0.9359 | 0.8899 | -0.046 | 0.9631 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655883 GALAXY -MK7 | 0.9443 | 0.89 | -0.0543 | 0.9727 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655890 WERNER -MK7 | 0.9301 | 0.8903 | -0.0398 | 0.9712 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655890 WERNER -MK7 | 0.9301 | 0.8903 | -0.0398 | 0.9712 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655894 HALLIDAY-MK7 | 0.9302 | 0.8904 | -0.0398 | 0.9713 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655894 HALLIDAY-MK7 | 0.9302 | 0.8904 | -0.0398 | 0.9713 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655882 GALAXYTP-MK7 | 0.945 | 0.8907 | -0.0543 | 0.9734 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655849 VEEDER -MK7 | 0.9449 | 0.8907 | -0.0542 | 0.9733 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655891 KILLDEER-MK7 | 0.9216 | 0.8908 | -0.0308 | 0.9692 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655884 DEMCKSLK-MK7 | 0.9294 | 0.891 | -0.0384 | 0.9624 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655884 DEMCKSLK-MK7 | 0.9294 | 0.891 | -0.0384 | 0.9624 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655864 GRAIL -MK7 | 0.9272 | 0.8912 | -0.036 | 0.9668 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 652419 KILDEER7 | 0.922 | 0.8912 | -0.0308 | 0.9696 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655865 STATION8-MK7 | 0.9272 | 0.8913 | -0.0359 | 0.9669 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655893 DUNNCNTR-MK7 | 0.9317 | 0.8919 | -0.0398 | 0.9727 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655893 DUNNCNTR-MK7 | 0.9317 | 0.8919 | -0.0398 | 0.9727 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655897 COYOTCHR-MK7 | 0.9463 | 0.8922 | -0.0541 | 0.9747 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659385 ROUNDUP_-MK7 | 0.9293 | 0.8924 | -0.0369 | 0.9775 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655880 SCHAFR_T-MK7 | 0.9467 | 0.8926 | -0.0541 | 0.9751 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655899 FNCYBTAP-MK7 | 0.9472 | 0.8931 | -0.0541 | 0.9755 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655832 BLUEBUTE-MK7 | 0.9305 | 0.8948 | -0.0357 | 0.9701 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655884 DEMCKSLK-MK7 | 0.929 | 0.8949 | -0.0341 | 0.9624 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655890 WERNER -MK7 | 0.9467 | 0.895 | -0.0517 | 0.9712 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655894 HALLIDAY-MK7 | 0.9468 | 0.8951 | -0.0517 | 0.9713 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655662 ROSEGLEN-CP7 | 0.9416 | 0.8954 | -0.0462 | 0.9949 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655864 GRAIL -MK7 | 0.9341 | 0.8959 | -0.0382 | 0.9668 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655864 GRAIL -MK7 | 0.9341 | 0.8959 | -0.0382 | 0.9668 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655663 RAUB TAP-CP7 | 0.942 | 0.8959 | -0.0461 | 0.9952 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655865 STATION8-MK7 | 0.9341 | 0.896 | -0.0381 | 0.9669 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655865 STATION8-MK7 | 0.9341 | 0.896 | -0.0381 | 0.9669 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655881 DAP_____-MK7 | 0.9502 | 0.8964 | -0.0538 | 0.9784 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659388 KUMMERDG-MK7 | 0.9504 | 0.8966 | -0.0538 | 0.9787 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655893 DUNNCNTR-MK7 | 0.9482 | 0.8966 | -0.0516 | 0.9727 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655891 KILLDEER-MK7 | 0.9302 | 0.8968 | -0.0334 | 0.9692 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655891 KILLDEER-MK7 | 0.9302 | 0.8968 | -0.0334 | 0.9692 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 652419 KILDEER7 | 0.9306 | 0.8973 | -0.0333 | 0.9696 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 652419 KILDEER7 | 0.9306 | 0.8973 | -0.0333 | 0.9696 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659385 ROUNDUP_-MK7 | 0.9368 | 0.8974 | -0.0394 | 0.9775 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659385 ROUNDUP_-MK7 | 0.9368 | 0.8974 | -0.0394 | 0.9775 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655870 TBGARDEN-MK7 | 0.9592 | 0.8974 | -0.0618 | 0.9893 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655883 GALAXY -MK7 | 0.9333 | 0.8976 | -0.0357 | 0.9727 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659384 ROUNDUP_-BE3 | 0.9646 | 0.8979 | -0.0667 | 0.9924 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655849 VEEDER -MK7 | 0.934 | 0.8983 | -0.0357 | 0.9733 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655882 GALAXYTP-MK7 | 0.934 | 0.8984 | -0.0356 | 0.9734 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655869 TWINVLLY-MK7 | 0.9602 | 0.8984 | -0.0618 | 0.9902 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655867 TWNVLYTP-MK7 | 0.9607 | 0.8989 | -0.0618 | 0.9906 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655832 BLUEBUTE-MK7 | 0.9374 | 0.8994 | -0.038 | 0.9701 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655832 BLUEBUTE-MK7 | 0.9374 | 0.8994 | -0.038 | 0.9701 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655864 GRAIL -MK7 | 0.9337 | 0.8998 | -0.0339 | 0.9668 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655897 COYOTCHR-MK7 | 0.9353 | 0.8998 | -0.0355 | 0.9747 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655865 STATION8-MK7 | 0.9338 | 0.8999 | -0.0339 | 0.9669 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8694 | 0.7905 | -0.0789 | 0.9018 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8815 | 0.8037 | -0.0778 | 0.9135 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8472 | 0.8044 | -0.0428 | 0.9018 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8558 | 0.8103 | -0.0455 | 0.9018 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8558 | 0.8103 | -0.0455 | 0.9018 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.8918 | 0.815 | -0.0768 | 0.9232 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8744 | 0.8157 | -0.0587 | 0.9018 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8597 | 0.8177 | -0.042 | 0.9135 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.8946 | 0.8181 | -0.0765 | 0.926 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8681 | 0.8234 | -0.0447 | 0.9135 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8681 | 0.8234 | -0.0447 | 0.9135 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.905 | 0.8266 | -0.0784 | 0.9402 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.9056 | 0.8274 | -0.0782 | 0.9406 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.9062 | 0.8276 | -0.0786 | 0.9414 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.906 | 0.8277 | -0.0783 | 0.9411 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.9065 | 0.8284 | -0.0781 | 0.9415 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.9039 | 0.8284 | -0.0755 | 0.9348 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8865 | 0.8287 | -0.0578 | 0.9135 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.8704 | 0.8292 | -0.0412 | 0.9232 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.907 | 0.8295 | -0.0775 | 0.9418 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9096 | 0.8307 | -0.0789 | 0.9449 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9093 | 0.832 | -0.0773 | 0.944 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.8732 | 0.8322 | -0.041 | 0.926 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9105 | 0.8327 | -0.0778 | 0.9454 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.8786 | 0.8348 | -0.0438 | 0.9232 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.8786 | 0.8348 | -0.0438 | 0.9232 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9127 | 0.8357 | -0.077 | 0.9472 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.8815 | 0.8378 | -0.0437 | 0.926 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.8815 | 0.8378 | -0.0437 | 0.926 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.8967 | 0.84 | -0.0567 | 0.9232 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.8828 | 0.8424 | -0.0404 | 0.9348 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.8995 | 0.843 | -0.0565 | 0.926 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.9214 | 0.846 | -0.0754 | 0.9554 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655836 OAKDALE -MK7 | 0.92 | 0.8464 | -0.0736 | 0.9503 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.9219 | 0.8465 | -0.0754 | 0.9558 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.8909 | 0.8479 | -0.043 | 0.9348 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.8909 | 0.8479 | -0.043 | 0.9348 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.9093 | 0.8499 | -0.0594 | 0.9402 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.9098 | 0.8506 | -0.0592 | 0.9406 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.9105 | 0.8509 | -0.0596 | 0.9414 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.9103 | 0.8509 | -0.0594 | 0.9411 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.9108 | 0.8516 | -0.0592 | 0.9415 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.9112 | 0.8525 | -0.0587 | 0.9418 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.9087 | 0.853 | -0.0557 | 0.9348 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9139 | 0.8541 | -0.0598 | 0.9449 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9135 | 0.8549 | -0.0586 | 0.944 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9148 | 0.8558 | -0.059 | 0.9454 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655884 DEMCKSLK-MK7 | 0.9296 | 0.8572 | -0.0724 | 0.9624 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.8973 | 0.8583 | -0.039 | 0.9402 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9169 | 0.8585 | -0.0584 | 0.9472 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.8979 | 0.8589 | -0.039 | 0.9406 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.8985 | 0.8593 | -0.0392 | 0.9414 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.8983 | 0.8593 | -0.039 | 0.9411 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.8989 | 0.8599 | -0.039 | 0.9415 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655836 OAKDALE -MK7 | 0.8995 | 0.8602 | -0.0393 | 0.9503 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.8994 | 0.8607 | -0.0387 | 0.9418 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655865 STATION8-MK7 | 0.9343 | 0.8624 | -0.0719 | 0.9669 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655864 GRAIL -MK7 | 0.9342 | 0.8624 | -0.0718 | 0.9668 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9018 | 0.8625 | -0.0393 | 0.9449 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9017 | 0.8631 | -0.0386 | 0.944 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.9049 | 0.8634 | -0.0415 | 0.9402 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.9049 | 0.8634 | -0.0415 | 0.9402 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655853 BEARCREK-MK7 | 0.9353 | 0.8638 | -0.0715 | 0.9647 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.9054 | 0.8641 | -0.0413 | 0.9406 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.9054 | 0.8641 | -0.0413 | 0.9406 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9029 | 0.8641 | -0.0388 | 0.9454 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.9058 | 0.8644 | -0.0414 | 0.9411 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.9058 | 0.8644 | -0.0414 | 0.9411 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.906 | 0.8645 | -0.0415 | 0.9414 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.906 | 0.8645 | -0.0415 | 0.9414 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.9063 | 0.865 | -0.0413 | 0.9415 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.9063 | 0.865 | -0.0413 | 0.9415 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655836 OAKDALE -MK7 | 0.9074 | 0.8656 | -0.0418 | 0.9503 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655836 OAKDALE -MK7 | 0.9074 | 0.8656 | -0.0418 | 0.9503 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.9068 | 0.8658 | -0.041 | 0.9418 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.9068 | 0.8658 | -0.041 | 0.9418 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655832 BLUEBUTE-MK7 | 0.9376 | 0.866 | -0.0716 | 0.9701 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9051 | 0.8668 | -0.0383 | 0.9472 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9094 | 0.8677 | -0.0417 | 0.9449 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9094 | 0.8677 | -0.0417 | 0.9449 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.9045 | 0.8677 | -0.0368 | 0.9402 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9091 | 0.8682 | -0.0409 | 0.944 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9091 | 0.8682 | -0.0409 | 0.944 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.9256 | 0.8683 | -0.0573 | 0.9554 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.905 | 0.8683 | -0.0367 | 0.9406 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.9055 | 0.8687 | -0.0368 | 0.9411 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.926 | 0.8688 | -0.0572 | 0.9558 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.9057 | 0.8688 | -0.0369 | 0.9414 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655883 GALAXY -MK7 | 0.9403 | 0.8689 | -0.0714 | 0.9727 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9103 | 0.8692 | -0.0411 | 0.9454 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9103 | 0.8692 | -0.0411 | 0.9454 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.906 | 0.8693 | -0.0367 | 0.9415 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655849 VEEDER -MK7 | 0.941 | 0.8697 | -0.0713 | 0.9733 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655882 GALAXYTP-MK7 | 0.941 | 0.8697 | -0.0713 | 0.9734 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.9064 | 0.87 | -0.0364 | 0.9418 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655836 OAKDALE -MK7 | 0.9247 | 0.8705 | -0.0542 | 0.9503 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655897 COYOTCHR-MK7 | 0.9424 | 0.8712 | -0.0712 | 0.9747 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655880 SCHAFR_T-MK7 | 0.9428 | 0.8717 | -0.0711 | 0.9751 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9125 | 0.8718 | -0.0407 | 0.9472 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9125 | 0.8718 | -0.0407 | 0.9472 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655890 WERNER -MK7 | 0.9422 | 0.8719 | -0.0703 | 0.9712 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.909 | 0.872 | -0.037 | 0.9449 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655894 HALLIDAY-MK7 | 0.9423 | 0.872 | -0.0703 | 0.9713 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655899 FNCYBTAP-MK7 | 0.9432 | 0.8722 | -0.071 | 0.9755 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9087 | 0.8724 | -0.0363 | 0.944 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.91 | 0.8734 | -0.0366 | 0.9454 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655893 DUNNCNTR-MK7 | 0.9437 | 0.8736 | -0.0701 | 0.9727 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655881 DAP_____-MK7 | 0.9463 | 0.8755 | -0.0708 | 0.9784 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659388 KUMMERDG-MK7 | 0.9465 | 0.8758 | -0.0707 | 0.9787 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9121 | 0.876 | -0.0361 | 0.9472 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.914 | 0.8764 | -0.0376 | 0.9554 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.9145 | 0.8769 | -0.0376 | 0.9558 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655853 BEARCREK-MK7 | 0.9153 | 0.8773 | -0.038 | 0.9647 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655884 DEMCKSLK-MK7 | 0.9335 | 0.8785 | -0.055 | 0.9624 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659385 ROUNDUP_-MK7 | 0.9488 | 0.8791 | -0.0697 | 0.9775 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.9213 | 0.8813 | -0.04 | 0.9554 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.9213 | 0.8813 | -0.04 | 0.9554 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.9217 | 0.8818 | -0.0399 | 0.9558 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.9217 | 0.8818 | -0.0399 | 0.9558 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655853 BEARCREK-MK7 | 0.923 | 0.8825 | -0.0405 | 0.9647 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655853 BEARCREK-MK7 | 0.923 | 0.8825 | -0.0405 | 0.9647 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655865 STATION8-MK7 | 0.9383 | 0.8836 | -0.0547 | 0.9669 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655864 GRAIL -MK7 | 0.9382 | 0.8836 | -0.0546 | 0.9668 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655894 HALLIDAY-MK7 | 0.9227 | 0.8853 | -0.0374 | 0.9713 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655890 WERNER -MK7 | 0.9226 | 0.8853 | -0.0373 | 0.9712 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.9209 | 0.8854 | -0.0355 | 0.9554 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659143 BLAISDEL-BE4 | 0.9636 | 0.8856 | -0.078 | 1.0074 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.9213 | 0.8859 | -0.0354 | 0.9558 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655891 KILLDEER-MK7 | 0.9403 | 0.8862 | -0.0541 | 0.9692 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655884 DEMCKSLK-MK7 | 0.9224 | 0.8863 | -0.0361 | 0.9624 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 652419 KILDEER7 | 0.9408 | 0.8867 | -0.0541 | 0.9696 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655893 DUNNCNTR-MK7 | 0.9241 | 0.8869 | -0.0372 | 0.9727 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655832 BLUEBUTE-MK7 | 0.9415 | 0.8871 | -0.0544 | 0.9701 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655853 BEARCREK-MK7 | 0.9399 | 0.8873 | -0.0526 | 0.9647 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659387 KUMMERDG-BE3 | 0.9575 | 0.8891 | -0.0684 | 0.9888 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659248 HALLIDAY-UM7 | 0.9359 | 0.8899 | -0.046 | 0.9631 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655883 GALAXY -MK7 | 0.9443 | 0.89 | -0.0543 | 0.9727 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655890 WERNER -MK7 | 0.9301 | 0.8903 | -0.0398 | 0.9712 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655890 WERNER -MK7 | 0.9301 | 0.8903 | -0.0398 | 0.9712 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655894 HALLIDAY-MK7 | 0.9302 | 0.8904 | -0.0398 | 0.9713 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655894 HALLIDAY-MK7 | 0.9302 | 0.8904 | -0.0398 | 0.9713 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655882 GALAXYTP-MK7 | 0.945 | 0.8907 | -0.0543 | 0.9734 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655849 VEEDER -MK7 | 0.9449 | 0.8907 | -0.0542 | 0.9733 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655891 KILLDEER-MK7 | 0.9216 | 0.8908 | -0.0308 | 0.9692 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655884 DEMCKSLK-MK7 | 0.9294 | 0.891 | -0.0384 | 0.9624 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655884 DEMCKSLK-MK7 | 0.9294 | 0.891 | -0.0384 | 0.9624 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655864 GRAIL -MK7 | 0.9272 | 0.8912 | -0.036 | 0.9668 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 652419 KILDEER7 | 0.922 | 0.8912 | -0.0308 | 0.9696 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655865 STATION8-MK7 | 0.9272 | 0.8913 | -0.0359 | 0.9669 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655893 DUNNCNTR-MK7 | 0.9317 | 0.8919 | -0.0398 | 0.9727 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655893 DUNNCNTR-MK7 | 0.9317 | 0.8919 | -0.0398 | 0.9727 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655897 COYOTCHR-MK7 | 0.9463 | 0.8922 | -0.0541 | 0.9747 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659385 ROUNDUP_-MK7 | 0.9293 | 0.8924 | -0.0369 | 0.9775 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655880 SCHAFR_T-MK7 | 0.9467 | 0.8926 | -0.0541 | 0.9751 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655899 FNCYBTAP-MK7 | 0.9472 | 0.8931 | -0.0541 | 0.9755 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655832 BLUEBUTE-MK7 | 0.9305 | 0.8948 | -0.0357 | 0.9701 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655884 DEMCKSLK-MK7 | 0.929 | 0.8949 | -0.0341 | 0.9624 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655890 WERNER -MK7 | 0.9467 | 0.895 | -0.0517 | 0.9712 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655894 HALLIDAY-MK7 | 0.9468 | 0.8951 | -0.0517 | 0.9713 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655662 ROSEGLEN-CP7 | 0.9416 | 0.8954 | -0.0462 | 0.9949 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655864 GRAIL -MK7 | 0.9341 | 0.8959 | -0.0382 | 0.9668 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655864 GRAIL -MK7 | 0.9341 | 0.8959 | -0.0382 | 0.9668 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655663 RAUB TAP-CP7 | 0.942 | 0.8959 | -0.0461 | 0.9952 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655865 STATION8-MK7 | 0.9341 | 0.896 | -0.0381 | 0.9669 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655865 STATION8-MK7 | 0.9341 | 0.896 | -0.0381 | 0.9669 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655881 DAP_____-MK7 | 0.9502 | 0.8964 | -0.0538 | 0.9784 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659388 KUMMERDG-MK7 | 0.9504 | 0.8966 | -0.0538 | 0.9787 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655893 DUNNCNTR-MK7 | 0.9482 | 0.8966 | -0.0516 | 0.9727 | 0.9 | 1.05 | 0.05462 | P12:345.0:UMZ:# N-1 #:: LINE LELAND_O-BE3-CRANECRK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655891 KILLDEER-MK7 | 0.9302 | 0.8968 | -0.0334 | 0.9692 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655891 KILLDEER-MK7 | 0.9302 | 0.8968 | -0.0334 | 0.9692 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 652419 KILDEER7 | 0.9306 | 0.8973 | -0.0333 | 0.9696 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 652419 KILDEER7 | 0.9306 | 0.8973 | -0.0333 | 0.9696 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659385 ROUNDUP_-MK7 | 0.9368 | 0.8974 | -0.0394 | 0.9775 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659385 ROUNDUP_-MK7 | 0.9368 | 0.8974 | -0.0394 | 0.9775 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655870 TBGARDEN-MK7 | 0.9592 | 0.8974 | -0.0618 | 0.9893 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655883 GALAXY -MK7 | 0.9333 | 0.8976 | -0.0357 | 0.9727 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659384 ROUNDUP_-BE3 | 0.9646 | 0.8979 | -0.0667 | 0.9924 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655849 VEEDER -MK7 | 0.934 | 0.8983 | -0.0357 | 0.9733 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655882 GALAXYTP-MK7 | 0.934 | 0.8984 | -0.0356 | 0.9734 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655869 TWINVLLY-MK7 | 0.9602 | 0.8984 | -0.0618 | 0.9902 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655867 TWNVLYTP-MK7 | 0.9607 | 0.8989 | -0.0618 | 0.9906 | 0.9 | 1.05 | 0.13913 | POI 659105_7 -Potential P4 Event | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655832 BLUEBUTE-MK7 | 0.9374 | 0.8994 | -0.038 | 0.9701 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655832 BLUEBUTE-MK7 | 0.9374 | 0.8994 | -0.038 | 0.9701 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655864 GRAIL -MK7 | 0.9337 | 0.8998 | -0.0339 | 0.9668 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655897 COYOTCHR-MK7 | 0.9353 | 0.8998 | -0.0355 | 0.9747 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655865 STATION8-MK7 | 0.9338 | 0.8999 | -0.0339 | 0.9669 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3707 #:: RP IN ND. BREAKER FAULT ROUND UP (896):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8624 | 0.8327 | -0.0297 | 0.9018 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8746 | 0.8454 | -0.0292 | 0.9135 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.8879 | 0.8593 | -0.0286 | 0.926 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.885 | 0.8564 | -0.0286 | 0.9232 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.8972 | 0.8691 | -0.0281 | 0.9348 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655857 MOCCASIN-MK7 | 0.8864 | 0.8603 | -0.0261 | 0.9018 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655831 J12_____-MK7 | 0.8983 | 0.8726 | -0.0257 | 0.9135 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9144 | 0.8845 | -0.0299 | 0.9449 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.911 | 0.8812 | -0.0298 | 0.9414 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.9098 | 0.8801 | -0.0297 | 0.9402 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.9108 | 0.8811 | -0.0297 | 0.9411 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.9113 | 0.8816 | -0.0297 | 0.9415 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.9103 | 0.8807 | -0.0296 | 0.9406 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9152 | 0.8857 | -0.0295 | 0.9454 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.9117 | 0.8823 | -0.0294 | 0.9418 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.914 | 0.8846 | -0.0294 | 0.944 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9174 | 0.8882 | -0.0292 | 0.9472 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659248 HALLIDAY-UM7 | 0.9261 | 0.8974 | -0.0287 | 0.9631 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659248 HALLIDAY-UM7 | 0.9261 | 0.8974 | -0.0287 | 0.9631 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655873 BBCOMPTP-MK7 | 0.9265 | 0.8978 | -0.0287 | 0.9558 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655874 BBCMPRSS-MK7 | 0.926 | 0.8974 | -0.0286 | 0.9554 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655836 OAKDALE -MK7 | 0.9135 | 0.8861 | -0.0274 | 0.9503 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 659248 HALLIDAY-UM7 | 0.9179 | 0.8914 | -0.0265 | 0.9631 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655851 BIGGULCH-MK7 | 0.9083 | 0.8831 | -0.0252 | 0.9232 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655852 L11_____-MK7 | 0.911 | 0.8859 | -0.0251 | 0.926 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655830 MOUNTAIN-MK7 | 0.9201 | 0.8953 | -0.0248 | 0.9348 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655837 ELMTREE -MK7 | 0.9157 | 0.8933 | -0.0224 | 0.9449 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655859 CHARLSON-MK7 | 0.9123 | 0.89 | -0.0223 | 0.9414 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655854 SANDCREK-MK7 | 0.9111 | 0.8889 | -0.0222 | 0.9402 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655866 SNDCRKTP-MK7 | 0.9121 | 0.8899 | -0.0222 | 0.9411 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655847 SWENSON -MK7 | 0.9126 | 0.8904 | -0.0222 | 0.9415 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655896 KEENECRN-MK7 | 0.9116 | 0.8895 | -0.0221 | 0.9406 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655885 NRTHFORK-MK7 | 0.913 | 0.891 | -0.022 | 0.9418 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655886 KEENE -MK7 | 0.9153 | 0.8933 | -0.022 | 0.944 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655858 TABLEBUT-MK7 | 0.9165 | 0.8945 | -0.022 | 0.9454 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-011 | 655848 BERG -MK7 | 0.9187 | 0.8968 | -0.0219 | 0.9472 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8624 | 0.8327 | -0.0297 | 0.9018 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8746 | 0.8454 | -0.0292 | 0.9135 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.8879 | 0.8593 | -0.0286 | 0.926 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.885 | 0.8564 | -0.0286 | 0.9232 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.8972 | 0.8691 | -0.0281 | 0.9348 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655857 MOCCASIN-MK7 | 0.8864 | 0.8603 | -0.0261 | 0.9018 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655831 J12_____-MK7 | 0.8983 | 0.8726 | -0.0257 | 0.9135 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9144 | 0.8845 | -0.0299 | 0.9449 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.911 | 0.8812 | -0.0298 | 0.9414 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.9098 | 0.8801 | -0.0297 | 0.9402 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.9108 | 0.8811 | -0.0297 | 0.9411 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.9113 | 0.8816 | -0.0297 | 0.9415 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.9103 | 0.8807 | -0.0296 | 0.9406 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9152 | 0.8857 | -0.0295 | 0.9454 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.9117 | 0.8823 | -0.0294 | 0.9418 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.914 | 0.8846 | -0.0294 | 0.944 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9174 | 0.8882 | -0.0292 | 0.9472 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659248 HALLIDAY-UM7 | 0.9261 | 0.8974 | -0.0287 | 0.9631 | 0.9 | 1.05 | 0.0872 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659248 HALLIDAY-UM7 | 0.9261 | 0.8974 | -0.0287 | 0.9631 | 0.9 | 1.05 | 0.0872 | P23:345:UMZB:# 3706 #:: RP IN ND. BREAKER FAULT ROUND UP (496):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655873 BBCOMPTP-MK7 | 0.9265 | 0.8978 | -0.0287 | 0.9558 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655874 BBCMPRSS-MK7 | 0.926 | 0.8974 | -0.0286 | 0.9554 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655836 OAKDALE -MK7 | 0.9135 | 0.8861 | -0.0274 | 0.9503 | 0.9 | 1.05 | 0.06941 | P23:345:UMZB:# 3048 #:: CCR IN ND. BREAKER FAULT CHARLIE CREEK (3696):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 659248 HALLIDAY-UM7 | 0.9179 | 0.8914 | -0.0265 | 0.9631 | 0.9 | 1.05 | 0.0872 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655851 BIGGULCH-MK7 | 0.9083 | 0.8831 | -0.0252 | 0.9232 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655852 L11_____-MK7 | 0.911 | 0.8859 | -0.0251 | 0.926 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655830 MOUNTAIN-MK7 | 0.9201 | 0.8953 | -0.0248 | 0.9348 | 0.9 | 1.05 | 0.07546 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-CHARL_CK-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655837 ELMTREE -MK7 | 0.9157 | 0.8933 | -0.0224 | 0.9449 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655859 CHARLSON-MK7 | 0.9123 | 0.89 | -0.0223 | 0.9414 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655854 SANDCREK-MK7 | 0.9111 | 0.8889 | -0.0222 | 0.9402 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655866 SNDCRKTP-MK7 | 0.9121 | 0.8899 | -0.0222 | 0.9411 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655847 SWENSON -MK7 | 0.9126 | 0.8904 | -0.0222 | 0.9415 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655896 KEENECRN-MK7 | 0.9116 | 0.8895 | -0.0221 | 0.9406 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655885 NRTHFORK-MK7 | 0.913 | 0.891 | -0.022 | 0.9418 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655886 KEENE -MK7 | 0.9153 | 0.8933 | -0.022 | 0.944 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655858 TABLEBUT-MK7 | 0.9165 | 0.8945 | -0.022 | 0.9454 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank
Voltage | ERAS-2025-001 | 00ALL | 2 | 29WP | ERAS-2025-012 | 655848 BERG -MK7 | 0.9187 | 0.8968 | -0.0219 | 0.9472 | 0.9 | 1.05 | 0.01779 | P12:345.0:UMZ:# N-1 #:: LINE ROUNDUP_-BE3-KUMMERDG-BE3-1 :EHV: | Kummer Ridge 345 kV Capacitor Bank

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
ERAS-2025-003 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.7896 | 8.8122 | 0.0226
ERAS-2025-003 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.6092 | 21.786 | 0.1768
ERAS-2025-003 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 21.3937 | 21.567 | 0.1733
ERAS-2025-003 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.9625 | 23.9711 | 0.0086
ERAS-2025-003 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.2799 | 24.2808 | 0.0009
ERAS-2025-003 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.6164 | 10.617 | 0.0006
ERAS-2025-003 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.5247 | 9.5252 | 0.0005
ERAS-2025-003 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.6981 | 13.6988 | 0.0007
ERAS-2025-003 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 12.9075 | 12.9083 | 0.0008
ERAS-2025-003 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.876 | 12.8774 | 0.0014
ERAS-2025-003 | 04 SOUTHEAST | 509727 | OAKS W4 | 138 | 15.1906 | 15.1937 | 0.0031
ERAS-2025-003 | 04 SOUTHEAST | 509732 | ORU W4 | 138 | 24.4586 | 24.4667 | 0.0081
ERAS-2025-003 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.849 | 18.8529 | 0.0039
ERAS-2025-003 | 04 SOUTHEAST | 509738 | ORU E4 | 138 | 25.852 | 25.8614 | 0.0094
ERAS-2025-003 | 04 SOUTHEAST | 509739 | CARSN-T4 | 138 | 34.0657 | 34.0799 | 0.0142
ERAS-2025-003 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 22.1212 | 22.1305 | 0.0093
ERAS-2025-003 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.8965 | 18.9002 | 0.0037
ERAS-2025-003 | 04 SOUTHEAST | 509748 | DENVR-W4 | 138 | 10.0218 | 10.0233 | 0.0015
ERAS-2025-003 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 45.0252 | 45.0551 | 0.0299
ERAS-2025-003 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.1779 | 23.2009 | 0.023
ERAS-2025-003 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 34.4238 | 34.4416 | 0.0178
ERAS-2025-003 | 04 SOUTHEAST | 509758 | PRATTV-4 | 138 | 20.6428 | 20.6491 | 0.0063
ERAS-2025-003 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.622 | 26.6326 | 0.0106
ERAS-2025-003 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.6796 | 16.683 | 0.0034
ERAS-2025-003 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 19.5643 | 19.5684 | 0.0041
ERAS-2025-003 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 20.5083 | 20.5125 | 0.0042
ERAS-2025-003 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 53.4064 | 53.4529 | 0.0465
ERAS-2025-003 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 31.3087 | 31.3224 | 0.0137
ERAS-2025-003 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.7801 | 33.8639 | 0.0838
ERAS-2025-003 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 64.704 | 64.7653 | 0.0613
ERAS-2025-003 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 19.471 | 19.4749 | 0.0039
ERAS-2025-003 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 25.3887 | 25.394 | 0.0053
ERAS-2025-003 | 04 SOUTHEAST | 509788 | T.P.S.-4 | 138 | 41.381 | 41.4015 | 0.0205
ERAS-2025-003 | 04 SOUTHEAST | 509804 | E 11TH ST 4 | 138 | 31.4166 | 31.4222 | 0.0056
ERAS-2025-003 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 51.9983 | 52.0251 | 0.0268
ERAS-2025-003 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 32.1299 | 32.1546 | 0.0247
ERAS-2025-003 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 27.1075 | 27.1182 | 0.0107
ERAS-2025-003 | 04 SOUTHEAST | 509813 | SHILETP4 | 138 | 29.3183 | 29.3297 | 0.0114
ERAS-2025-003 | 04 SOUTHEAST | 509814 | S HILLWT4 | 138 | 22.2626 | 22.2694 | 0.0068
ERAS-2025-003 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 30.0005 | 30.0137 | 0.0132
ERAS-2025-003 | 04 SOUTHEAST | 509821 | HWY20-T4 | 138 | 4.9159 | 4.9163 | 0.0004
ERAS-2025-003 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 20.04 | 20.0459 | 0.0059
ERAS-2025-003 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 31.2097 | 31.2803 | 0.0706
ERAS-2025-003 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 32.0234 | 32.0479 | 0.0245
ERAS-2025-003 | 04 SOUTHEAST | 509846 | OAKS--E4 | 138 | 14.2597 | 14.2624 | 0.0027
ERAS-2025-003 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 23.3672 | 23.3745 | 0.0073
ERAS-2025-003 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 35.8807 | 35.8987 | 0.018
ERAS-2025-003 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 28.3544 | 28.3645 | 0.0101
ERAS-2025-003 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 16.3126 | 16.3157 | 0.0031
ERAS-2025-003 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 26.6589 | 26.6772 | 0.0183
ERAS-2025-003 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 31.4011 | 31.4144 | 0.0133
ERAS-2025-003 | 04 SOUTHEAST | 509858 | WARNTAP4 | 138 | 30.2183 | 30.2307 | 0.0124
ERAS-2025-003 | 04 SOUTHEAST | 509859 | S HILLW4 | 138 | 16.6231 | 16.6269 | 0.0038
ERAS-2025-003 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 18.479 | 18.4824 | 0.0034
ERAS-2025-003 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.849 | 23.8813 | 0.0323
ERAS-2025-003 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.3935 | 34.4116 | 0.0181
ERAS-2025-003 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 54.3813 | 54.4289 | 0.0476
ERAS-2025-003 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.5072 | 24.5152 | 0.008
ERAS-2025-003 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 16.5832 | 16.586 | 0.0028
ERAS-2025-003 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 24.2943 | 24.3002 | 0.0059
ERAS-2025-003 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 46.173 | 46.1899 | 0.0169
ERAS-2025-003 | 04 SOUTHEAST | 509902 | KMCLKHP4 | 138 | 30.1477 | 30.1604 | 0.0127
ERAS-2025-003 | 04 SOUTHEAST | 509904 | AVERYDR4 | 138 | 28.9294 | 28.9397 | 0.0103
ERAS-2025-003 | 04 SOUTHEAST | 509915 | ANTHEM7 | 345 | 13.9382 | 13.9406 | 0.0024
ERAS-2025-003 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 11.6754 | 11.6759 | 0.0005
ERAS-2025-003 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.9941 | 11.9956 | 0.0015
ERAS-2025-003 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 18.4829 | 18.489 | 0.0061
ERAS-2025-003 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 12.3669 | 12.3694 | 0.0025
ERAS-2025-003 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 10.5789 | 10.5807 | 0.0018
ERAS-2025-003 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.2606 | 15.2779 | 0.0173
ERAS-2025-003 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 13.714 | 13.7168 | 0.0028
ERAS-2025-003 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.2224 | 15.2236 | 0.0012
ERAS-2025-003 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 14.9749 | 14.9916 | 0.0167
ERAS-2025-003 | 04 SOUTHEAST | 510931 | KELCO 4 | 138 | 11.0134 | 11.0153 | 0.0019
ERAS-2025-003 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.2668 | 14.2709 | 0.0041
ERAS-2025-003 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.9557 | 8.9595 | 0.0038
ERAS-2025-003 | 04 SOUTHEAST | 510957 | EC HEN-4T | 138 | 9.7511 | 9.7528 | 0.0017
ERAS-2025-003 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.3182 | 16.3378 | 0.0196
ERAS-2025-003 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.737 | 10.7457 | 0.0087
ERAS-2025-003 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.5693 | 10.5773 | 0.008
ERAS-2025-003 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 7.3121 | 7.3138 | 0.0017
ERAS-2025-003 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 11.3527 | 11.3587 | 0.006
ERAS-2025-003 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 7.0932 | 7.0971 | 0.0039
ERAS-2025-003 | 04 SOUTHEAST | 511587 | MATO 7 | 345 | 10.1409 | 10.1475 | 0.0066
ERAS-2025-003 | 04 SOUTHEAST | 511877 | G16133G16146 | 345 | 33.7801 | 33.8639 | 0.0838
ERAS-2025-003 | 04 SOUTHEAST | 511878 | G16133_765TN | 765 | 9.7535 | 9.7668 | 0.0133
ERAS-2025-003 | 04 SOUTHEAST | 511879 | G16133_765R1 | 765 | 9.7535 | 9.7668 | 0.0133
ERAS-2025-003 | 04 SOUTHEAST | 511880 | G16133_765R2 | 765 | 4.4956 | 4.4976 | 0.002
ERAS-2025-003 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 20.2562 | 20.2746 | 0.0184
ERAS-2025-003 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 18.0068 | 18.0118 | 0.005
ERAS-2025-003 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.3552 | 23.6266 | 0.2714
ERAS-2025-003 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.9592 | 11.9626 | 0.0034
ERAS-2025-003 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 20.6304 | 20.6486 | 0.0182
ERAS-2025-003 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 17.7047 | 17.7177 | 0.013
ERAS-2025-003 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 22.161 | 22.1826 | 0.0216
ERAS-2025-003 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 21.3103 | 21.3763 | 0.066
ERAS-2025-003 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.4837 | 8.4911 | 0.0074
ERAS-2025-003 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 20.1339 | 20.1422 | 0.0083
ERAS-2025-003 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.7793 | 7.7807 | 0.0014
ERAS-2025-003 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 25.1903 | 25.3499 | 0.1596
ERAS-2025-003 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.7918 | 33.8059 | 0.0141
ERAS-2025-003 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.8471 | 30.9102 | 0.0631
ERAS-2025-003 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.378 | 16.3829 | 0.0049
ERAS-2025-003 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4184 | 11.4237 | 0.0053
ERAS-2025-003 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.8943 | 7.8969 | 0.0026
ERAS-2025-003 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.7856 | 17.8191 | 0.0335
ERAS-2025-003 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.396 | 19.4334 | 0.0374
ERAS-2025-003 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 16.6666 | 16.6884 | 0.0218
ERAS-2025-003 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.8079 | 18.9021 | 0.0942
ERAS-2025-003 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 29.6587 | 29.9231 | 0.2644
ERAS-2025-003 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.8888 | 12.926 | 0.0372
ERAS-2025-003 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.6773 | 9.6912 | 0.0139
ERAS-2025-003 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.39 | 15.4569 | 0.0669
ERAS-2025-003 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 28.4055 | 28.6854 | 0.2799
ERAS-2025-003 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 30.5588 | 30.8416 | 0.2828
ERAS-2025-003 | 04 SOUTHEAST | 514840 | JONESTP4 | 138 | 29.9671 | 30.1722 | 0.2051
ERAS-2025-003 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.6161 | 21.7691 | 0.153
ERAS-2025-003 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 31.9785 | 32.2258 | 0.2473
ERAS-2025-003 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 35.4046 | 35.6906 | 0.286
ERAS-2025-003 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 39.0375 | 39.3284 | 0.2909
ERAS-2025-003 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 33.8625 | 34.1545 | 0.292
ERAS-2025-003 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 23.2545 | 23.3709 | 0.1164
ERAS-2025-003 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.3245 | 28.4587 | 0.1342
ERAS-2025-003 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.959 | 24.1027 | 0.1437
ERAS-2025-003 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 34.0651 | 34.3719 | 0.3068
ERAS-2025-003 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 47.7278 | 48.3831 | 0.6553
ERAS-2025-003 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.3228 | 35.3427 | 1.0199
ERAS-2025-003 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.3967 | 24.7907 | 0.394
ERAS-2025-003 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 24.4692 | 24.5421 | 0.0729
ERAS-2025-003 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 32.3044 | 32.4235 | 0.1191
ERAS-2025-003 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 30.7109 | 30.8217 | 0.1108
ERAS-2025-003 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.3083 | 20.3506 | 0.0423
ERAS-2025-003 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.0496 | 47.3554 | 0.3058
ERAS-2025-003 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 38.5892 | 39.3748 | 0.7856
ERAS-2025-003 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 33.4556 | 33.5344 | 0.0788
ERAS-2025-003 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.7726 | 21.9523 | 0.1797
ERAS-2025-003 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 39.3352 | 40.5791 | 1.2439
ERAS-2025-003 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 24.4015 | 26.993 | 2.5915
ERAS-2025-003 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 23.4047 | 26.3113 | 2.9066
ERAS-2025-003 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 41.6663 | 41.8293 | 0.163
ERAS-2025-003 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 45.573 | 45.792 | 0.219
ERAS-2025-003 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.6432 | 27.86 | 0.2168
ERAS-2025-003 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 11.1624 | 11.1686 | 0.0062
ERAS-2025-003 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 53.0398 | 53.3611 | 0.3213
ERAS-2025-003 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 36.0916 | 36.2091 | 0.1175
ERAS-2025-003 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 24.2243 | 24.2739 | 0.0496
ERAS-2025-003 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 23.3689 | 23.4174 | 0.0485
ERAS-2025-003 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 21.0968 | 21.1422 | 0.0454
ERAS-2025-003 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 28.9322 | 29.0283 | 0.0961
ERAS-2025-003 | 04 SOUTHEAST | 514971 | GRNPAST4 | 138 | 21.9441 | 22.007 | 0.0629
ERAS-2025-003 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 15.1153 | 15.1365 | 0.0212
ERAS-2025-003 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 30.8358 | 30.9238 | 0.088
ERAS-2025-003 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 24.611 | 24.6794 | 0.0684
ERAS-2025-003 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 24.2828 | 24.3484 | 0.0656
ERAS-2025-003 | 04 SOUTHEAST | 515035 | BRISTOW4 | 138 | 10.7847 | 10.7875 | 0.0028
ERAS-2025-003 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 47.3788 | 47.5227 | 0.1439
ERAS-2025-003 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.4045 | 30.6432 | 0.2387
ERAS-2025-003 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 18.4619 | 18.4932 | 0.0313
ERAS-2025-003 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 11.4452 | 11.449 | 0.0038
ERAS-2025-003 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 22.0731 | 22.1032 | 0.0301
ERAS-2025-003 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.9405 | 14.9573 | 0.0168
ERAS-2025-003 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 10.1065 | 10.1126 | 0.0061
ERAS-2025-003 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 9.1021 | 9.1039 | 0.0018
ERAS-2025-003 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 11.0593 | 11.0648 | 0.0055
ERAS-2025-003 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.6579 | 8.6606 | 0.0027
ERAS-2025-003 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.8116 | 16.8198 | 0.0082
ERAS-2025-003 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.6381 | 6.6396 | 0.0015
ERAS-2025-003 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.1781 | 12.1834 | 0.0053
ERAS-2025-003 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 14.147 | 14.1559 | 0.0089
ERAS-2025-003 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 17.6963 | 17.7099 | 0.0136
ERAS-2025-003 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 33.3757 | 33.3987 | 0.023
ERAS-2025-003 | 04 SOUTHEAST | 515227 | 5TRIBES2 | 69 | 14.8964 | 14.8974 | 0.001
ERAS-2025-003 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 16.3369 | 16.3395 | 0.0026
ERAS-2025-003 | 04 SOUTHEAST | 515229 | AGENCY 2 | 69 | 14.1683 | 14.1691 | 0.0008
ERAS-2025-003 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.8062 | 14.8081 | 0.0019
ERAS-2025-003 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 14.3996 | 14.4022 | 0.0026
ERAS-2025-003 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.6363 | 21.6411 | 0.0048
ERAS-2025-003 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 24.7304 | 24.7471 | 0.0167
ERAS-2025-003 | 04 SOUTHEAST | 515247 | BEELINE4 | 138 | 23.0959 | 23.104 | 0.0081
ERAS-2025-003 | 04 SOUTHEAST | 515248 | EXPLGLN4 | 138 | 25.0602 | 25.0697 | 0.0095
ERAS-2025-003 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 6.031 | 6.0317 | 0.0007
ERAS-2025-003 | 04 SOUTHEAST | 515250 | HANCOK-5 | 161 | 14.9278 | 14.9297 | 0.0019
ERAS-2025-003 | 04 SOUTHEAST | 515251 | EUCLID 5 | 161 | 14.4755 | 14.4772 | 0.0017
ERAS-2025-003 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 25.9086 | 25.9099 | 0.0013
ERAS-2025-003 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 14.5512 | 14.5524 | 0.0012
ERAS-2025-003 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 10.4156 | 10.4163 | 0.0007
ERAS-2025-003 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.8655 | 14.9266 | 0.0611
ERAS-2025-003 | 04 SOUTHEAST | 515374 | CHISHOM4 | 138 | 31.3816 | 31.6419 | 0.2603
ERAS-2025-003 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 21.5227 | 21.5608 | 0.0381
ERAS-2025-003 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.6455 | 26.6627 | 0.0172
ERAS-2025-003 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.3193 | 10.3338 | 0.0145
ERAS-2025-003 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.3835 | 9.3854 | 0.0019
ERAS-2025-003 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 10.1416 | 10.1439 | 0.0023
ERAS-2025-003 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.3541 | 18.4401 | 0.086
ERAS-2025-003 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8462 | 11.854 | 0.0078
ERAS-2025-003 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 20.1436 | 20.152 | 0.0084
ERAS-2025-003 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 25.0862 | 25.2444 | 0.1582
ERAS-2025-003 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.7096 | 12.7498 | 0.0402
ERAS-2025-003 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 7.988 | 7.9905 | 0.0025
ERAS-2025-003 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 37.6706 | 38.7942 | 1.1236
ERAS-2025-003 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.5142 | 21.7777 | 0.2635
ERAS-2025-003 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 23.5677 | 23.7326 | 0.1649
ERAS-2025-003 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 25.5165 | 25.5263 | 0.0098
ERAS-2025-003 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.5302 | 14.5503 | 0.0201
ERAS-2025-003 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 14.5067 | 14.5268 | 0.0201
ERAS-2025-003 | 04 SOUTHEAST | 515481 | STHLAKE4 | 138 | 23.0889 | 23.1319 | 0.043
ERAS-2025-003 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 37.869 | 38.8788 | 1.0098
ERAS-2025-003 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.2837 | 14.2927 | 0.009
ERAS-2025-003 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 13.0266 | 13.0396 | 0.013
ERAS-2025-003 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.5739 | 15.6296 | 0.0557
ERAS-2025-003 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.3671 | 15.3743 | 0.0072
ERAS-2025-003 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.8383 | 8.857 | 0.0187
ERAS-2025-003 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.343 | 14.3942 | 0.0512
ERAS-2025-003 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.691 | 12.7508 | 0.0598
ERAS-2025-003 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 14.3399 | 14.4163 | 0.0764
ERAS-2025-003 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 19.4673 | 19.6246 | 0.1573
ERAS-2025-003 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 13.1838 | 13.1885 | 0.0047
ERAS-2025-003 | 04 SOUTHEAST | 515707 | HSL13 4 | 138 | 44.2416 | 44.4574 | 0.2158
ERAS-2025-003 | 04 SOUTHEAST | 515778 | GRIFFIN7 | 345 | 23.9065 | 23.9204 | 0.0139
ERAS-2025-003 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.3111 | 20.3573 | 0.0462
ERAS-2025-003 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 35.8092 | 35.8327 | 0.0235
ERAS-2025-003 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.7656 | 9.7727 | 0.0071
ERAS-2025-003 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.8507 | 14.8612 | 0.0105
ERAS-2025-003 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.6015 | 15.6055 | 0.004
ERAS-2025-003 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 19.3636 | 19.485 | 0.1214
ERAS-2025-003 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 19.3588 | 19.4801 | 0.1213
ERAS-2025-003 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.5637 | 13.5747 | 0.011
ERAS-2025-003 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.9585 | 10.9842 | 0.0257
ERAS-2025-003 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.7207 | 11.7313 | 0.0106
ERAS-2025-003 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 13.3733 | 13.3872 | 0.0139
ERAS-2025-003 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 6.0971 | 6.0995 | 0.0024
ERAS-2025-003 | 04 SOUTHEAST | 515975 | G15-066T | 345 | 20.2357 | 20.2598 | 0.0241
ERAS-2025-003 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 45.1398 | 45.2699 | 0.1301
ERAS-2025-003 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 5.7698 | 5.7729 | 0.0031
ERAS-2025-003 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.3513 | 8.3538 | 0.0025
ERAS-2025-003 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 18.1282 | 18.1608 | 0.0326
ERAS-2025-003 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 18.0629 | 18.0953 | 0.0324
ERAS-2025-003 | 04 SOUTHEAST | 516036 | TRAV3WD7 | 345 | 8.8563 | 8.8801 | 0.0238
ERAS-2025-003 | 04 SOUTHEAST | 516045 | TRAV2WD7 | 345 | 7.5887 | 7.6011 | 0.0124
ERAS-2025-003 | 04 SOUTHEAST | 516054 | TRAV1WD7 | 345 | 7.0155 | 7.0256 | 0.0101
ERAS-2025-003 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 11.3311 | 11.3371 | 0.006
ERAS-2025-003 | 04 SOUTHEAST | 516086 | TRAV3WZ7 | 345 | 8.1825 | 8.2025 | 0.02
ERAS-2025-003 | 04 SOUTHEAST | 516087 | TRAV22Z7 | 345 | 7.1026 | 7.1134 | 0.0108
ERAS-2025-003 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 18.1675 | 18.1789 | 0.0114
ERAS-2025-003 | 04 SOUTHEAST | 516092 | OKTAHA 5 | 161 | 11.2389 | 11.2408 | 0.0019
ERAS-2025-003 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.6837 | 28.9331 | 0.2494
ERAS-2025-003 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.4369 | 44.6228 | 0.1859
ERAS-2025-003 | 04 SOUTHEAST | 516100 | HORIZON4 | 138 | 6.9922 | 6.9983 | 0.0061
ERAS-2025-003 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 15.778 | 15.7931 | 0.0151
ERAS-2025-003 | 04 SOUTHEAST | 516107 | TRAV21Z7 | 345 | 7.106 | 7.1167 | 0.0107
ERAS-2025-003 | 04 SOUTHEAST | 516108 | TRAV11Z7 | 345 | 6.6086 | 6.6174 | 0.0088
ERAS-2025-003 | 04 SOUTHEAST | 516109 | TRAV12Z7 | 345 | 6.6078 | 6.6166 | 0.0088
ERAS-2025-003 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 15.7491 | 15.7641 | 0.015
ERAS-2025-003 | 04 SOUTHEAST | 516192 | WAGNWTIE7 | 345 | 15.6728 | 15.7406 | 0.0678
ERAS-2025-003 | 04 SOUTHEAST | 516207 | GADWALL7 | 345 | 15.6728 | 15.7406 | 0.0678
ERAS-2025-003 | 04 SOUTHEAST | 516210 | RAVEN 7 | 345 | 20.2119 | 20.2284 | 0.0165
ERAS-2025-003 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.4837 | 8.4911 | 0.0074
ERAS-2025-003 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 9.9959 | 10.0074 | 0.0115
ERAS-2025-003 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.5106 | 11.5125 | 0.0019
ERAS-2025-003 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.8273 | 17.8284 | 0.0011
ERAS-2025-003 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 16.1774 | 16.1837 | 0.0063
ERAS-2025-003 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 34.4238 | 34.4416 | 0.0178
ERAS-2025-003 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 5.453 | 5.4558 | 0.0028
ERAS-2025-003 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.7278 | 12.7376 | 0.0098
ERAS-2025-003 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 19.7324 | 19.7481 | 0.0157
ERAS-2025-003 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.2119 | 20.2284 | 0.0165
ERAS-2025-003 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 16.2665 | 16.277 | 0.0105
ERAS-2025-003 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.871 | 4.9346 | 0.0636
ERAS-2025-003 | 04 SOUTHEAST | 760152 | TNOXF2 | 138 | 46.1183 | 46.1352 | 0.0169
ERAS-2025-003 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.903 | 1.9031 | 0.0001
ERAS-2025-003 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.8901 | 1.8902 | 0.0001
ERAS-2025-003 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.9232 | 3.9238 | 0.0006
ERAS-2025-003 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 24.2811 | 24.429 | 0.1479
ERAS-2025-003 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 24.3303 | 24.4788 | 0.1485
ERAS-2025-003 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 12.2553 | 12.2763 | 0.021
ERAS-2025-003 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.4699 | 8.4798 | 0.0099
ERAS-2025-003 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 19.5632 | 19.5787 | 0.0155
ERAS-2025-003 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 53.0195 | 53.3406 | 0.3211
ERAS-2025-003 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 17.4087 | 17.4167 | 0.008
ERAS-2025-003 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.8371 | 9.8441 | 0.007
ERAS-2025-003 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 18.8335 | 18.8626 | 0.0291
ERAS-2025-003 | 04 SOUTHEAST | 778734 | ERA-10 | 138 | 44.3546 | 44.573 | 0.2184
ERAS-2025-003 | 04 SOUTHEAST | 788714 | ERA-04-1 | 138 | 38.1444 | 38.3022 | 0.1578
ERAS-2025-003 | 04 SOUTHEAST | 788716 | ERA-04-2 | 138 | 37.7653 | 37.9217 | 0.1564
ERAS-2025-003 | 04 SOUTHEAST | 788833 | ERA-23 | 345 | 18.3723 | 18.3784 | 0.0061
ERAS-2025-004 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.7735 | 8.8445 | 0.071
ERAS-2025-004 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.4772 | 22.0422 | 0.565
ERAS-2025-004 | 04 SOUTHEAST | 300834 | 2CARNEY | 69 | 5.1817 | 5.1856 | 0.0039
ERAS-2025-004 | 04 SOUTHEAST | 300839 | 2MERIDAN | 69 | 5.3845 | 5.3909 | 0.0064
ERAS-2025-004 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.8505 | 6.8624 | 0.0119
ERAS-2025-004 | 04 SOUTHEAST | 300915 | 4WARWICK | 138 | 4.9559 | 4.9735 | 0.0176
ERAS-2025-004 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.763 | 8.8337 | 0.0707
ERAS-2025-004 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 21.2643 | 21.818 | 0.5537
ERAS-2025-004 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.855 | 33.9837 | 0.1287
ERAS-2025-004 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.2714 | 15.3026 | 0.0312
ERAS-2025-004 | 04 SOUTHEAST | 514501 | KELLYAV4 | 138 | 30.5016 | 31.1634 | 0.6618
ERAS-2025-004 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.4944 | 24.0239 | 0.5295
ERAS-2025-004 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 22.1765 | 22.2132 | 0.0367
ERAS-2025-004 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.4884 | 8.5016 | 0.0132
ERAS-2025-004 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.8611 | 19.0376 | 0.1765
ERAS-2025-004 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.9088 | 12.9792 | 0.0704
ERAS-2025-004 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.6836 | 9.7109 | 0.0273
ERAS-2025-004 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.4196 | 15.5533 | 0.1337
ERAS-2025-004 | 04 SOUTHEAST | 514832 | EASTERN4 | 138 | 26.3095 | 26.7921 | 0.4826
ERAS-2025-004 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 28.4895 | 29.0939 | 0.6044
ERAS-2025-004 | 04 SOUTHEAST | 514835 | MEMRIAL4 | 138 | 40.7309 | 41.8798 | 1.1489
ERAS-2025-004 | 04 SOUTHEAST | 514837 | TENESTP4 | 138 | 34.4372 | 35.1923 | 0.7551
ERAS-2025-004 | 04 SOUTHEAST | 514839 | BRYANT 4 | 138 | 31.6735 | 32.4639 | 0.7904
ERAS-2025-004 | 04 SOUTHEAST | 514840 | JONESTP4 | 138 | 29.4459 | 30.4691 | 1.0232
ERAS-2025-004 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.466 | 21.9903 | 0.5243
ERAS-2025-004 | 04 SOUTHEAST | 514844 | BELISLE4 | 138 | 30.7327 | 31.2606 | 0.5279
ERAS-2025-004 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 36.2451 | 37.0833 | 0.8382
ERAS-2025-004 | 04 SOUTHEAST | 514868 | DOUGLTP4 | 138 | 34.5578 | 35.1074 | 0.5496
ERAS-2025-004 | 04 SOUTHEAST | 514869 | WESTERN4 | 138 | 34.2227 | 34.8703 | 0.6476
ERAS-2025-004 | 04 SOUTHEAST | 514870 | STNWAL 4 | 138 | 31.5541 | 32.2147 | 0.6606
ERAS-2025-004 | 04 SOUTHEAST | 514874 | REMNGPK4 | 138 | 34.2436 | 35.1508 | 0.9072
ERAS-2025-004 | 04 SOUTHEAST | 514875 | OUMED 4 | 138 | 24.6619 | 25.0777 | 0.4158
ERAS-2025-004 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 48.0955 | 49.3473 | 1.2518
ERAS-2025-004 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.1825 | 36.8966 | 1.7141
ERAS-2025-004 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.7291 | 25.3715 | 0.6424
ERAS-2025-004 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 23.9519 | 24.6467 | 0.6948
ERAS-2025-004 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 39.2144 | 40.5458 | 1.3314
ERAS-2025-004 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.6384 | 22.2127 | 0.5743
ERAS-2025-004 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 40.1897 | 42.4858 | 2.2961
ERAS-2025-004 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 26.8624 | 31.7606 | 4.8982
ERAS-2025-004 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.1981 | 31.9114 | 5.7133
ERAS-2025-004 | 04 SOUTHEAST | 514923 | LIGHTCK4 | 138 | 27.4328 | 27.8068 | 0.374
ERAS-2025-004 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 10.2858 | 10.3602 | 0.0744
ERAS-2025-004 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 22.6855 | 22.7974 | 0.1119
ERAS-2025-004 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 45.5157 | 46.1081 | 0.5924
ERAS-2025-004 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.7383 | 28.1741 | 0.4358
ERAS-2025-004 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 11.0889 | 11.1775 | 0.0886
ERAS-2025-004 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 48.9799 | 53.8254 | 4.8455
ERAS-2025-004 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 36.0628 | 36.3783 | 0.3155
ERAS-2025-004 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 25.3374 | 25.4712 | 0.1338
ERAS-2025-004 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 24.2184 | 24.3451 | 0.1267
ERAS-2025-004 | 04 SOUTHEAST | 514951 | LITTLAX2 | 69 | 3.3994 | 3.4038 | 0.0044
ERAS-2025-004 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 37.1535 | 37.4875 | 0.334
ERAS-2025-004 | 04 SOUTHEAST | 514956 | MACOCTP2 | 69 | 3.3617 | 3.3658 | 0.0041
ERAS-2025-004 | 04 SOUTHEAST | 514959 | FOSTER 4 | 138 | 28.3387 | 28.6988 | 0.3601
ERAS-2025-004 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 21.0667 | 21.2076 | 0.1409
ERAS-2025-004 | 04 SOUTHEAST | 514963 | TROSPER4 | 138 | 32.4544 | 33.0479 | 0.5935
ERAS-2025-004 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 28.4486 | 29.2148 | 0.7662
ERAS-2025-004 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 27.9003 | 29.1662 | 1.2659
ERAS-2025-004 | 04 SOUTHEAST | 514969 | NE30TH 2 | 138 | 30.6483 | 31.3735 | 0.7252
ERAS-2025-004 | 04 SOUTHEAST | 514971 | GRNPAST4 | 138 | 21.5474 | 22.0976 | 0.5502
ERAS-2025-004 | 04 SOUTHEAST | 514972 | RENO 2 | 69 | 13.4943 | 13.5471 | 0.0528
ERAS-2025-004 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 37.1337 | 38.2256 | 1.0919
ERAS-2025-004 | 04 SOUTHEAST | 514979 | 44&SUNL2 | 69 | 11.5835 | 11.617 | 0.0335
ERAS-2025-004 | 04 SOUTHEAST | 514980 | SUNNYLN2 | 69 | 11.8126 | 11.8487 | 0.0361
ERAS-2025-004 | 04 SOUTHEAST | 514981 | TINKER32 | 69 | 9.0216 | 9.0433 | 0.0217
ERAS-2025-004 | 04 SOUTHEAST | 514983 | LTLRLKT2 | 69 | 2.7913 | 2.7952 | 0.0039
ERAS-2025-004 | 04 SOUTHEAST | 514985 | TXSTELA2 | 69 | 3.9216 | 3.9291 | 0.0075
ERAS-2025-004 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 25.1195 | 25.6641 | 0.5446
ERAS-2025-004 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.9248 | 15.1667 | 0.2419
ERAS-2025-004 | 04 SOUTHEAST | 514989 | TXPLSTE2 | 69 | 3.019 | 3.0235 | 0.0045
ERAS-2025-004 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 24.2741 | 24.7776 | 0.5035
ERAS-2025-004 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 20.9069 | 21.2347 | 0.3278
ERAS-2025-004 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 24.0277 | 24.4427 | 0.415
ERAS-2025-004 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 47.428 | 47.7291 | 0.3011
ERAS-2025-004 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.5624 | 30.9883 | 0.4259
ERAS-2025-004 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 18.1301 | 18.538 | 0.4079
ERAS-2025-004 | 04 SOUTHEAST | 515047 | WARWICK4 | 138 | 10.8734 | 10.9265 | 0.0531
ERAS-2025-004 | 04 SOUTHEAST | 515051 | JACKTWN4 | 138 | 10.3134 | 10.3962 | 0.0828
ERAS-2025-004 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 22.0399 | 22.1463 | 0.1064
ERAS-2025-004 | 04 SOUTHEAST | 515056 | WOLVERN4 | 138 | 8.9203 | 8.9793 | 0.059
ERAS-2025-004 | 04 SOUTHEAST | 515057 | MOBIL 4 | 138 | 8.9998 | 9.0596 | 0.0598
ERAS-2025-004 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.9785 | 15.138 | 0.1595
ERAS-2025-004 | 04 SOUTHEAST | 515060 | INGLEWD4 | 138 | 10.9476 | 11.0329 | 0.0853
ERAS-2025-004 | 04 SOUTHEAST | 515061 | STGREG 4 | 138 | 9.6993 | 9.7668 | 0.0675
ERAS-2025-004 | 04 SOUTHEAST | 515062 | NE45TAP4 | 138 | 9.376 | 9.4396 | 0.0636
ERAS-2025-004 | 04 SOUTHEAST | 515065 | MCLOUD 2 | 69 | 4.9642 | 4.9778 | 0.0136
ERAS-2025-004 | 04 SOUTHEAST | 515068 | SHAWNEE2 | 69 | 8.4387 | 8.4611 | 0.0224
ERAS-2025-004 | 04 SOUTHEAST | 515072 | SINCPAN2 | 69 | 6.0815 | 6.095 | 0.0135
ERAS-2025-004 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.9117 | 11.9467 | 0.035
ERAS-2025-004 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.8593 | 14.9812 | 0.1219
ERAS-2025-004 | 04 SOUTHEAST | 515156 | WASHPRK4 | 138 | 23.9504 | 24.3676 | 0.4172
ERAS-2025-004 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 14.8007 | 14.9452 | 0.1445
ERAS-2025-004 | 04 SOUTHEAST | 515366 | WFROSST4 | 138 | 13.051 | 13.1665 | 0.1155
ERAS-2025-004 | 04 SOUTHEAST | 515369 | BELLCOW4 | 138 | 6.96 | 6.976 | 0.016
ERAS-2025-004 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.8951 | 15.0145 | 0.1194
ERAS-2025-004 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.3275 | 10.3544 | 0.0269
ERAS-2025-004 | 04 SOUTHEAST | 515387 | NEWDOMI4 | 138 | 29.8181 | 30.278 | 0.4599
ERAS-2025-004 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 15.9947 | 16.2023 | 0.2076
ERAS-2025-004 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 21.498 | 21.6468 | 0.1488
ERAS-2025-004 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 27.6295 | 28.3463 | 0.7168
ERAS-2025-004 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 38.4382 | 40.5091 | 2.0709
ERAS-2025-004 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.5934 | 22.1631 | 0.5697
ERAS-2025-004 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 38.7384 | 40.4054 | 1.667
ERAS-2025-004 | 04 SOUTHEAST | 515502 | LITLAXT2 | 69 | 3.4041 | 3.4086 | 0.0045
ERAS-2025-004 | 04 SOUTHEAST | 515504 | MCLOUDT2 | 69 | 4.9871 | 5.0008 | 0.0137
ERAS-2025-004 | 04 SOUTHEAST | 515516 | TXPLSTP2 | 69 | 3.0227 | 3.0272 | 0.0045
ERAS-2025-004 | 04 SOUTHEAST | 515532 | WOLVRNT4 | 138 | 8.996 | 9.0559 | 0.0599
ERAS-2025-004 | 04 SOUTHEAST | 515642 | SINCPNT2 | 69 | 6.1163 | 6.1299 | 0.0136
ERAS-2025-004 | 04 SOUTHEAST | 515675 | TRYON 4 | 138 | 9.6323 | 9.6523 | 0.02
ERAS-2025-004 | 04 SOUTHEAST | 515707 | HSL13 4 | 138 | 41.4708 | 44.7682 | 3.2974
ERAS-2025-004 | 04 SOUTHEAST | 515806 | TINKER64 | 138 | 20.3997 | 20.7172 | 0.3175
ERAS-2025-004 | 04 SOUTHEAST | 515851 | CROSTWN4 | 138 | 27.8633 | 28.2391 | 0.3758
ERAS-2025-004 | 04 SOUTHEAST | 515959 | TINKER74 | 138 | 20.6175 | 20.9593 | 0.3418
ERAS-2025-004 | 04 SOUTHEAST | 515963 | GATEWAY4 | 138 | 23.2426 | 23.6221 | 0.3795
ERAS-2025-004 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.8137 | 29.295 | 0.4813
ERAS-2025-004 | 04 SOUTHEAST | 516100 | HORIZON4 | 138 | 6.9956 | 7.007 | 0.0114
ERAS-2025-004 | 04 SOUTHEAST | 516210 | RAVEN 7 | 345 | 20.2235 | 20.2519 | 0.0284
ERAS-2025-004 | 04 SOUTHEAST | 520449 | STERLNG4 | 138 | 11.9664 | 12.0609 | 0.0945
ERAS-2025-004 | 04 SOUTHEAST | 520464 | MEEKER 4 | 138 | 9.4803 | 9.5319 | 0.0516
ERAS-2025-004 | 04 SOUTHEAST | 520526 | GRDGVTP4 | 138 | 7.3835 | 7.4078 | 0.0243
ERAS-2025-004 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 31.2585 | 31.4809 | 0.2224
ERAS-2025-004 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 15.078 | 15.3599 | 0.2819
ERAS-2025-004 | 04 SOUTHEAST | 520994 | MEEKRSW4 | 138 | 8.7482 | 8.7853 | 0.0371
ERAS-2025-004 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.4884 | 8.5016 | 0.0132
ERAS-2025-004 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.0024 | 10.024 | 0.0216
ERAS-2025-004 | 04 SOUTHEAST | 521097 | WREDHIL4 | 138 | 7.5693 | 7.5947 | 0.0254
ERAS-2025-004 | 04 SOUTHEAST | 521107 | RSSVILE4 | 138 | 13.051 | 13.1665 | 0.1155
ERAS-2025-004 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9316 | 5.0274 | 0.0958
ERAS-2025-004 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 48.9626 | 53.8044 | 4.8418
ERAS-2025-004 | 04 SOUTHEAST | 778734 | ERA-10 | 138 | 41.5466 | 44.888 | 3.3414
ERAS-2025-004 | 04 SOUTHEAST | 788714 | ERA-04-1 | 138 | 34.7852 | 38.5292 | 3.744
ERAS-2025-004 | 04 SOUTHEAST | 788716 | ERA-04-2 | 138 | 34.7852 | 38.147 | 3.3618
ERAS-2025-005 | 04 SOUTHEAST | 337900 | 3OLA AR | 115 | 5.1826 | 5.268 | 0.0854
ERAS-2025-005 | 04 SOUTHEAST | 337901 | 3DANVLE AR | 115 | 6.4111 | 6.6034 | 0.1923
ERAS-2025-005 | 04 SOUTHEAST | 337902 | 5DANVLE AR! | 161 | 7.4179 | 7.9416 | 0.5237
ERAS-2025-005 | 04 SOUTHEAST | 337903 | 5DARDANELLE | 161 | 10.825 | 11.0953 | 0.2703
ERAS-2025-005 | 04 SOUTHEAST | 337904 | 5RUSSELVL.S | 161 | 11.8049 | 12.0035 | 0.1986
ERAS-2025-005 | 04 SOUTHEAST | 337905 | 5RUSSELVL.E! | 161 | 12.2857 | 12.4284 | 0.1427
ERAS-2025-005 | 04 SOUTHEAST | 338110 | 5HILLTOP% | 161 | 8.6506 | 8.659 | 0.0084
ERAS-2025-005 | 04 SOUTHEAST | 338737 | 3NIMROD# | 115 | 4.9417 | 4.9911 | 0.0494
ERAS-2025-005 | 04 SOUTHEAST | 338743 | 3HOLLIS# | 115 | 5.2137 | 5.2493 | 0.0356
ERAS-2025-005 | 04 SOUTHEAST | 504172 | BOONEVIL 2 | 69 | 6.5359 | 6.631 | 0.0951
ERAS-2025-005 | 04 SOUTHEAST | 504175 | BIGPINEY2 | 69 | 5.9328 | 5.9501 | 0.0173
ERAS-2025-005 | 04 SOUTHEAST | 504192 | GRANDPR5 | 161 | 7.8516 | 8.1411 | 0.2895
ERAS-2025-005 | 04 SOUTHEAST | 505507 | SWPINEY5 | 161 | 6.3478 | 6.3964 | 0.0486
ERAS-2025-005 | 04 SOUTHEAST | 505508 | DARDANE5 | 161 | 12.0085 | 12.2741 | 0.2656
ERAS-2025-005 | 04 SOUTHEAST | 505511 | CLRKSVL2 | 69 | 6.9173 | 6.948 | 0.0307
ERAS-2025-005 | 04 SOUTHEAST | 505514 | CLARKSV5 | 161 | 7.9893 | 8.0912 | 0.1019
ERAS-2025-005 | 04 SOUTHEAST | 505516 | OZARK H5 | 161 | 11.174 | 11.2989 | 0.1249
ERAS-2025-005 | 04 SOUTHEAST | 507183 | BOONVIL2 | 69 | 6.1585 | 6.2409 | 0.0824
ERAS-2025-005 | 04 SOUTHEAST | 507185 | REVESRD5 | 161 | 12.082 | 12.206 | 0.124
ERAS-2025-005 | 04 SOUTHEAST | 507188 | NHUNTNT2 | 69 | 10.0306 | 10.1015 | 0.0709
ERAS-2025-005 | 04 SOUTHEAST | 507189 | NHUNTNT5 | 161 | 8.1763 | 8.3093 | 0.133
ERAS-2025-005 | 04 SOUTHEAST | 507190 | NMAGZIN5 | 161 | 8.1716 | 8.9544 | 0.7828
ERAS-2025-005 | 04 SOUTHEAST | 507192 | WBOONVL5 | 161 | 6.7435 | 7.0329 | 0.2894
ERAS-2025-005 | 04 SOUTHEAST | 507195 | MAGZREC5 | 161 | 7.2077 | 8.2855 | 1.0778
ERAS-2025-005 | 04 SOUTHEAST | 507198 | WBOONVL2 | 69 | 6.6692 | 6.7687 | 0.0995
ERAS-2025-005 | 04 SOUTHEAST | 515313 | BRANCH 2 | 69 | 8.2662 | 8.3902 | 0.124
ERAS-2025-005 | 04 SOUTHEAST | 515316 | BRANCH 5 | 161 | 8.7737 | 9.2184 | 0.4447
ERAS-2025-005 | 04 SOUTHEAST | 515317 | PENDER 2 | 69 | 6.9801 | 7.0374 | 0.0573
ERAS-2025-005 | 04 SOUTHEAST | 515319 | LSPADRA5 | 161 | 7.8662 | 7.9717 | 0.1055
ERAS-2025-005 | 04 SOUTHEAST | 515339 | VBI 5 | 161 | 18.8196 | 19.0417 | 0.2221
ERAS-2025-005 | 04 SOUTHEAST | 515358 | SHORTMT5 | 161 | 6.9811 | 7.1849 | 0.2038
ERAS-2025-005 | 04 SOUTHEAST | 515440 | SUBIACT5 | 161 | 6.7499 | 6.9092 | 0.1593
ERAS-2025-005 | 04 SOUTHEAST | 515524 | GRNDPRT5 | 161 | 8.0581 | 8.3634 | 0.3053
ERAS-2025-005 | 04 SOUTHEAST | 516229 | FLYGAP 5 | 161 | 8.7194 | 9.1581 | 0.4387
ERAS-2025-005 | 04 SOUTHEAST | 788718 | ERAS-05 | 161 | 7.0033 | 8.2252 | 1.2219
ERAS-2025-005 | 04 SOUTHEAST | 788938 | ERAS-05-TAP | 161 | 7.0395 | 8.2601 | 1.2206
ERAS-2025-009 | 04 SOUTHEAST | 300069 | 5CHOTEAU1 | 161 | 43.0084 | 43.4997 | 0.4913
ERAS-2025-009 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.7804 | 15.7941 | 0.0137
ERAS-2025-009 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 24.935 | 25.2895 | 0.3545
ERAS-2025-009 | 04 SOUTHEAST | 300741 | 5SPORTSMAN | 161 | 41.3597 | 41.813 | 0.4533
ERAS-2025-009 | 04 SOUTHEAST | 300795 | 4OOLOGAHKAMO | 138 | 21.8527 | 21.8798 | 0.0271
ERAS-2025-009 | 04 SOUTHEAST | 300949 | 7JASPER | 345 | 12.8454 | 12.8526 | 0.0072
ERAS-2025-009 | 04 SOUTHEAST | 300950 | 5JASPER | 161 | 13.2783 | 13.2811 | 0.0028
ERAS-2025-009 | 04 SOUTHEAST | 300955 | 2COWETA | 69 | 2.6187 | 2.6197 | 0.001
ERAS-2025-009 | 04 SOUTHEAST | 300958 | 2HIGHLND | 69 | 2.0128 | 2.0134 | 0.0006
ERAS-2025-009 | 04 SOUTHEAST | 300960 | 2LOWERY | 69 | 4.7593 | 4.777 | 0.0177
ERAS-2025-009 | 04 SOUTHEAST | 300962 | 2PEGGS | 69 | 6.0344 | 6.0686 | 0.0342
ERAS-2025-009 | 04 SOUTHEAST | 300972 | 2WAGNERW | 69 | 4.8153 | 4.8188 | 0.0035
ERAS-2025-009 | 04 SOUTHEAST | 300974 | 2WHITHRN | 69 | 3.3745 | 3.3762 | 0.0017
ERAS-2025-009 | 04 SOUTHEAST | 300993 | 5ELMCRK | 161 | 14.5658 | 14.6061 | 0.0403
ERAS-2025-009 | 04 SOUTHEAST | 300997 | 5KETONVL | 161 | 12.3914 | 12.4273 | 0.0359
ERAS-2025-009 | 04 SOUTHEAST | 301307 | 5PARK | 161 | 8.358 | 8.3799 | 0.0219
ERAS-2025-009 | 04 SOUTHEAST | 301344 | 5CDRCRST | 161 | 10.708 | 10.7677 | 0.0597
ERAS-2025-009 | 04 SOUTHEAST | 301345 | 2CDRCRST | 69 | 7.579 | 7.6466 | 0.0676
ERAS-2025-009 | 04 SOUTHEAST | 301348 | 5CHOTEAU2 | 161 | 43.0084 | 43.4997 | 0.4913
ERAS-2025-009 | 04 SOUTHEAST | 301451 | 2GRAY TP | 69 | 7.8974 | 7.9045 | 0.0071
ERAS-2025-009 | 04 SOUTHEAST | 301618 | 2FTGIBSNKAMO | 69 | 8.5416 | 8.5541 | 0.0125
ERAS-2025-009 | 04 SOUTHEAST | 301728 | 5BRIGGSTAP | 161 | 7.7786 | 7.7974 | 0.0188
ERAS-2025-009 | 04 SOUTHEAST | 504201 | GENTRY 5 | 161 | 27.8604 | 27.907 | 0.0466
ERAS-2025-009 | 04 SOUTHEAST | 504202 | SILOAMSP 5 | 161 | 20.388 | 20.412 | 0.024
ERAS-2025-009 | 04 SOUTHEAST | 505552 | GORE 5 | 161 | 12.0393 | 12.0471 | 0.0078
ERAS-2025-009 | 04 SOUTHEAST | 505558 | MUSKTAP5 | 161 | 14.7199 | 14.7473 | 0.0274
ERAS-2025-009 | 04 SOUTHEAST | 505560 | FT GIB 5 | 161 | 10.9919 | 11.0181 | 0.0262
ERAS-2025-009 | 04 SOUTHEAST | 506934 | FLINTCR5 | 161 | 35.051 | 35.1252 | 0.0742
ERAS-2025-009 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 16.1485 | 16.1973 | 0.0488
ERAS-2025-009 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 22.9114 | 22.9553 | 0.0439
ERAS-2025-009 | 04 SOUTHEAST | 506957 | TONTITN5 | 161 | 23.1809 | 23.2034 | 0.0225
ERAS-2025-009 | 04 SOUTHEAST | 506979 | SHIPERD7 | 345 | 10.7701 | 10.7903 | 0.0202
ERAS-2025-009 | 04 SOUTHEAST | 506980 | SHIPERD5 | 161 | 15.9982 | 16.0156 | 0.0174
ERAS-2025-009 | 04 SOUTHEAST | 509722 | SPNKY CK4 | 138 | 30.0718 | 30.1583 | 0.0865
ERAS-2025-009 | 04 SOUTHEAST | 509752 | INOLATP4 | 138 | 10.1116 | 10.1243 | 0.0127
ERAS-2025-009 | 04 SOUTHEAST | 509771 | LLAN ET4 | 138 | 26.1096 | 26.1636 | 0.054
ERAS-2025-009 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 39.6264 | 39.7852 | 0.1588
ERAS-2025-009 | 04 SOUTHEAST | 509799 | CATOOSA2 | 69 | 11.0313 | 11.0371 | 0.0058
ERAS-2025-009 | 04 SOUTHEAST | 509804 | E 11TH ST 4 | 138 | 31.3467 | 31.4304 | 0.0837
ERAS-2025-009 | 04 SOUTHEAST | 509835 | TERNITP4 | 138 | 17.4849 | 17.5094 | 0.0245
ERAS-2025-009 | 04 SOUTHEAST | 509841 | PCATSAT4 | 138 | 19.0332 | 19.0642 | 0.031
ERAS-2025-009 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 26.6313 | 26.7032 | 0.0719
ERAS-2025-009 | 04 SOUTHEAST | 509887 | OWAS88_4 | 138 | 18.8774 | 18.9001 | 0.0227
ERAS-2025-009 | 04 SOUTHEAST | 509915 | ANTHEM7 | 345 | 13.8978 | 13.9441 | 0.0463
ERAS-2025-009 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.9911 | 11.9977 | 0.0066
ERAS-2025-009 | 04 SOUTHEAST | 510393 | CHOUTEA2 | 69 | 6.0602 | 6.0689 | 0.0087
ERAS-2025-009 | 04 SOUTHEAST | 510408 | PCP-TAP2 | 69 | 8.5018 | 8.5195 | 0.0177
ERAS-2025-009 | 04 SOUTHEAST | 510416 | HUNTAP-2 | 69 | 9.742 | 9.7671 | 0.0251
ERAS-2025-009 | 04 SOUTHEAST | 510423 | L GROVE3 | 115 | 18.3504 | 18.4803 | 0.1299
ERAS-2025-009 | 04 SOUTHEAST | 512622 | PRYORC32 | 69 | 9.8787 | 9.9028 | 0.0241
ERAS-2025-009 | 04 SOUTHEAST | 512623 | CATSAGD4 | 138 | 39.6264 | 39.7852 | 0.1588
ERAS-2025-009 | 04 SOUTHEAST | 512624 | CENTLFT2 | 69 | 12.0424 | 12.06 | 0.0176
ERAS-2025-009 | 04 SOUTHEAST | 512625 | MAIDTP2 | 69 | 12.3242 | 12.3764 | 0.0522
ERAS-2025-009 | 04 SOUTHEAST | 512626 | MAID 2 | 69 | 15.0852 | 15.1638 | 0.0786
ERAS-2025-009 | 04 SOUTHEAST | 512627 | COLINS 5 | 161 | 13.4893 | 13.5249 | 0.0356
ERAS-2025-009 | 04 SOUTHEAST | 512628 | PENSA 2 | 69 | 13.8944 | 13.9181 | 0.0237
ERAS-2025-009 | 04 SOUTHEAST | 512629 | DRYGULCH5 | 161 | 16.1907 | 16.3874 | 0.1967
ERAS-2025-009 | 04 SOUTHEAST | 512632 | AFTON 5 | 161 | 8.8266 | 8.8447 | 0.0181
ERAS-2025-009 | 04 SOUTHEAST | 512634 | KERR GR3 | 115 | 19.5007 | 19.6498 | 0.1491
ERAS-2025-009 | 04 SOUTHEAST | 512635 | KERR GR5 | 161 | 30.4717 | 31.1465 | 0.6748
ERAS-2025-009 | 04 SOUTHEAST | 512636 | CATSAGR4 | 138 | 39.6264 | 39.7852 | 0.1588
ERAS-2025-009 | 04 SOUTHEAST | 512637 | 412SUB 5 | 161 | 12.2725 | 12.3353 | 0.0628
ERAS-2025-009 | 04 SOUTHEAST | 512638 | CATSAGR5 | 161 | 27.8999 | 28.0428 | 0.1429
ERAS-2025-009 | 04 SOUTHEAST | 512639 | PRY0RC22 | 69 | 10.2082 | 10.2354 | 0.0272
ERAS-2025-009 | 04 SOUTHEAST | 512640 | OKAYGR 5 | 161 | 10.3291 | 10.362 | 0.0329
ERAS-2025-009 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 15.3825 | 15.4158 | 0.0333
ERAS-2025-009 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 20.7375 | 20.7806 | 0.0431
ERAS-2025-009 | 04 SOUTHEAST | 512646 | OKAYGR 2 | 69 | 12.6132 | 12.6342 | 0.021
ERAS-2025-009 | 04 SOUTHEAST | 512647 | TAHLQH 2 | 69 | 11.8699 | 11.8931 | 0.0232
ERAS-2025-009 | 04 SOUTHEAST | 512648 | MAID 5 | 161 | 46.5884 | 48.7876 | 2.1992
ERAS-2025-009 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 27.4316 | 27.8815 | 0.4499
ERAS-2025-009 | 04 SOUTHEAST | 512651 | CLARMR 5 | 161 | 14.0721 | 14.1307 | 0.0586
ERAS-2025-009 | 04 SOUTHEAST | 512654 | PENSA 5 | 161 | 13.5935 | 13.6812 | 0.0877
ERAS-2025-009 | 04 SOUTHEAST | 512655 | TAHLQH 5 | 161 | 9.2667 | 9.2937 | 0.027
ERAS-2025-009 | 04 SOUTHEAST | 512656 | GRDA1 5 | 161 | 46.0473 | 48.575 | 2.5277
ERAS-2025-009 | 04 SOUTHEAST | 512661 | CPPTAP 2 | 69 | 13.4859 | 13.5448 | 0.0589
ERAS-2025-009 | 04 SOUTHEAST | 512669 | KETCHUM5 | 161 | 11.021 | 11.0707 | 0.0497
ERAS-2025-009 | 04 SOUTHEAST | 512671 | HUNT 2 | 69 | 14.0522 | 14.1112 | 0.059
ERAS-2025-009 | 04 SOUTHEAST | 512679 | CLARMR 2 | 69 | 13.5005 | 13.5226 | 0.0221
ERAS-2025-009 | 04 SOUTHEAST | 512681 | AMERCAST S2 | 69 | 13.8179 | 13.8813 | 0.0634
ERAS-2025-009 | 04 SOUTHEAST | 512683 | AMERCAST N2 | 69 | 8.6726 | 8.6987 | 0.0261
ERAS-2025-009 | 04 SOUTHEAST | 512685 | CASTING TAP2 | 69 | 9.6694 | 9.7017 | 0.0323
ERAS-2025-009 | 04 SOUTHEAST | 512686 | SALINA 5 | 161 | 18.6901 | 18.913 | 0.2229
ERAS-2025-009 | 04 SOUTHEAST | 512687 | AIRPROD2 | 69 | 13.4239 | 13.4799 | 0.056
ERAS-2025-009 | 04 SOUTHEAST | 512690 | WAGNRTP2 | 69 | 7.592 | 7.6004 | 0.0084
ERAS-2025-009 | 04 SOUTHEAST | 512692 | CLEORTP2 | 69 | 7.7869 | 7.7927 | 0.0058
ERAS-2025-009 | 04 SOUTHEAST | 512693 | WHITETP 2 | 69 | 6.8857 | 6.8926 | 0.0069
ERAS-2025-009 | 04 SOUTHEAST | 512695 | ADARNEO2 | 69 | 4.9038 | 4.9067 | 0.0029
ERAS-2025-009 | 04 SOUTHEAST | 512697 | WAGNOR 2 | 69 | 7.4775 | 7.4859 | 0.0084
ERAS-2025-009 | 04 SOUTHEAST | 512698 | REDDEN 2 | 69 | 11.0638 | 11.1059 | 0.0421
ERAS-2025-009 | 04 SOUTHEAST | 512699 | PRYORCHEM2 | 69 | 13.3877 | 13.4445 | 0.0568
ERAS-2025-009 | 04 SOUTHEAST | 512700 | WAGNOR 5 | 161 | 10.0448 | 10.0916 | 0.0468
ERAS-2025-009 | 04 SOUTHEAST | 512705 | COLLINS4 | 138 | 8.5431 | 8.5519 | 0.0088
ERAS-2025-009 | 04 SOUTHEAST | 512707 | CLARMR 4 | 138 | 14.2568 | 14.2824 | 0.0256
ERAS-2025-009 | 04 SOUTHEAST | 512714 | KANSATP5 | 161 | 12.1273 | 12.1643 | 0.037
ERAS-2025-009 | 04 SOUTHEAST | 512716 | KANSAS 5 | 161 | 11.4888 | 11.522 | 0.0332
ERAS-2025-009 | 04 SOUTHEAST | 512725 | CHELSGR2 | 69 | 4.6161 | 4.6188 | 0.0027
ERAS-2025-009 | 04 SOUTHEAST | 512727 | GRDA1 2 | 69 | 12.7216 | 12.7811 | 0.0595
ERAS-2025-009 | 04 SOUTHEAST | 512742 | WMAIN ST5 | 161 | 29.0708 | 29.9834 | 0.9126
ERAS-2025-009 | 04 SOUTHEAST | 512750 | TONECE7 | 345 | 15.8821 | 15.9347 | 0.0526
ERAS-2025-009 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.9299 | 15.9543 | 0.0244
ERAS-2025-009 | 04 SOUTHEAST | 512753 | TONNEC2 | 69 | 5.5331 | 5.5341 | 0.001
ERAS-2025-009 | 04 SOUTHEAST | 512756 | TONECESTR2 | 69 | 4.3339 | 4.3345 | 0.0006
ERAS-2025-009 | 04 SOUTHEAST | 512757 | NWMAID5 | 161 | 28.8102 | 29.6944 | 0.8842
ERAS-2025-009 | 04 SOUTHEAST | 512759 | WAGCTY22 | 69 | 6.0247 | 6.0301 | 0.0054
ERAS-2025-009 | 04 SOUTHEAST | 512760 | GERALDGAY5 | 161 | 30.1666 | 31.1147 | 0.9481
ERAS-2025-009 | 04 SOUTHEAST | 512770 | KERR BRK1 5 | 161 | 30.4717 | 31.1465 | 0.6748
ERAS-2025-009 | 04 SOUTHEAST | 512771 | KERR BRK4 5 | 161 | 30.4717 | 31.1465 | 0.6748
ERAS-2025-009 | 04 SOUTHEAST | 512785 | GEN-2017-061 | 161 | 21.3173 | 21.7407 | 0.4234
ERAS-2025-009 | 04 SOUTHEAST | 512801 | WAGCTY12 | 69 | 5.6369 | 5.6417 | 0.0048
ERAS-2025-009 | 04 SOUTHEAST | 512805 | SALNCRK5 | 161 | 19.3642 | 19.6065 | 0.2423
ERAS-2025-009 | 04 SOUTHEAST | 512812 | ARMIN 2 | 69 | 11.5 | 11.5395 | 0.0395
ERAS-2025-009 | 04 SOUTHEAST | 512820 | SILMCTY2 | 69 | 13.9399 | 13.9478 | 0.0079
ERAS-2025-009 | 04 SOUTHEAST | 512828 | UNARCO 2 | 69 | 7.6111 | 7.6195 | 0.0084
ERAS-2025-009 | 04 SOUTHEAST | 512858 | GEN-2017-073 | 161 | 15.0325 | 15.2018 | 0.1693
ERAS-2025-009 | 04 SOUTHEAST | 512865 | GREC TAP7 | 345 | 26.1513 | 26.5392 | 0.3879
ERAS-2025-009 | 04 SOUTHEAST | 512870 | COLNSGR2 | 69 | 10.8689 | 10.8756 | 0.0067
ERAS-2025-009 | 04 SOUTHEAST | 513008 | CLARMTP 2 | 69 | 11.0878 | 11.1027 | 0.0149
ERAS-2025-009 | 04 SOUTHEAST | 513010 | CLARCTY1 2 | 69 | 5.5981 | 5.6018 | 0.0037
ERAS-2025-009 | 04 SOUTHEAST | 513012 | CLARCTY2 2 | 69 | 9.4265 | 9.4373 | 0.0108
ERAS-2025-009 | 04 SOUTHEAST | 513014 | CLARCTY4 2 | 69 | 6.3009 | 6.3056 | 0.0047
ERAS-2025-009 | 04 SOUTHEAST | 513050 | LOCSTGV 5 | 161 | 13.9163 | 14.0531 | 0.1368
ERAS-2025-009 | 04 SOUTHEAST | 513053 | FTGIBTAP 2 | 69 | 8.5999 | 8.6126 | 0.0127
ERAS-2025-009 | 04 SOUTHEAST | 513056 | PERKTAP 2 | 69 | 8.3258 | 8.339 | 0.0132
ERAS-2025-009 | 04 SOUTHEAST | 513065 | SWAGONER 2 | 69 | 8.0542 | 8.0634 | 0.0092
ERAS-2025-009 | 04 SOUTHEAST | 513071 | GREENLF 2 | 69 | 7.0077 | 7.0094 | 0.0017
ERAS-2025-009 | 04 SOUTHEAST | 513074 | MUSKSW 2 | 69 | 6.37 | 6.3723 | 0.0023
ERAS-2025-009 | 04 SOUTHEAST | 513077 | SALBRN 2 | 69 | 5.967 | 5.969 | 0.002
ERAS-2025-009 | 04 SOUTHEAST | 513124 | OOLOGAH 4 | 138 | 21.8535 | 21.8806 | 0.0271
ERAS-2025-009 | 04 SOUTHEAST | 513129 | SEQUOYA 2 | 69 | 7.2466 | 7.2529 | 0.0063
ERAS-2025-009 | 04 SOUTHEAST | 513570 | CHOUTEAUCRK5 | 161 | 21.3185 | 21.7419 | 0.4234
ERAS-2025-009 | 04 SOUTHEAST | 513591 | HERRON 5 | 161 | 17.3173 | 17.3858 | 0.0685
ERAS-2025-009 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.5103 | 17.5803 | 0.07
ERAS-2025-009 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.5103 | 17.5803 | 0.07
ERAS-2025-009 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.5713 | 20.7844 | 0.2131
ERAS-2025-009 | 04 SOUTHEAST | 515222 | MUSKOGE5 | 161 | 16.9151 | 16.945 | 0.0299
ERAS-2025-009 | 04 SOUTHEAST | 515956 | 7CLANS 5 | 161 | 9.0894 | 9.1135 | 0.0241
ERAS-2025-009 | 04 SOUTHEAST | 532777 | NRSS7 | 345 | 12.0161 | 12.0197 | 0.0036
ERAS-2025-009 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 19.2234 | 19.2285 | 0.0051
ERAS-2025-009 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.8204 | 17.8299 | 0.0095
ERAS-2025-009 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 18.6129 | 18.6185 | 0.0056
ERAS-2025-009 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 18.0612 | 18.0635 | 0.0023
ERAS-2025-009 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 16.0122 | 16.0138 | 0.0016
ERAS-2025-009 | 04 SOUTHEAST | 532939 | N345 4 5 | 161 | 22.4607 | 22.4674 | 0.0067
ERAS-2025-009 | 04 SOUTHEAST | 533023 | N345 3 4 | 138 | 26.1358 | 26.1429 | 0.0071
ERAS-2025-009 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 24.7472 | 24.748 | 0.0008
ERAS-2025-009 | 04 SOUTHEAST | 542981 | LACYGNE7 | 345 | 26.96 | 26.9614 | 0.0014
ERAS-2025-009 | 04 SOUTHEAST | 547504 | GENTRY | 161 | 21.173 | 21.1994 | 0.0264
ERAS-2025-009 | 04 SOUTHEAST | 549984 | BROOKLINE 7 | 345 | 12.257 | 12.2611 | 0.0041
ERAS-2025-009 | 04 SOUTHEAST | 580555 | MONETT345 | 345 | 9.7002 | 9.7055 | 0.0053
ERAS-2025-009 | 04 SOUTHEAST | 709500 | GI-95_POI | 345 | 11.6481 | 11.6522 | 0.0041
ERAS-2025-009 | 04 SOUTHEAST | 762999 | GEN-2018-064 | 69 | 4.2282 | 4.2287 | 0.0005
ERAS-2025-009 | 04 SOUTHEAST | 763472 | GEN-2019-002 | 161 | 43.1296 | 45.0101 | 1.8805
ERAS-2025-009 | 04 SOUTHEAST | 788732 | ERAS-09 | 161 | 46.0473 | 48.575 | 2.5277
ERAS-2025-009 | 04 SOUTHEAST | 800102 | NBRAN345 | 345 | 6.9137 | 6.9155 | 0.0018
ERAS-2025-010 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.7891 | 8.8445 | 0.0554
ERAS-2025-010 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.6004 | 22.0422 | 0.4418
ERAS-2025-010 | 04 SOUTHEAST | 300834 | 2CARNEY | 69 | 5.1825 | 5.1856 | 0.0031
ERAS-2025-010 | 04 SOUTHEAST | 300839 | 2MERIDAN | 69 | 5.3858 | 5.3909 | 0.0051
ERAS-2025-010 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.853 | 6.8624 | 0.0094
ERAS-2025-010 | 04 SOUTHEAST | 300915 | 4WARWICK | 138 | 4.9598 | 4.9735 | 0.0137
ERAS-2025-010 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.7785 | 8.8337 | 0.0552
ERAS-2025-010 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 21.3851 | 21.818 | 0.4329
ERAS-2025-010 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.8586 | 33.9837 | 0.1251
ERAS-2025-010 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.274 | 15.3026 | 0.0286
ERAS-2025-010 | 04 SOUTHEAST | 514501 | KELLYAV4 | 138 | 30.6612 | 31.1634 | 0.5022
ERAS-2025-010 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.5474 | 24.0239 | 0.4765
ERAS-2025-010 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 22.1789 | 22.2132 | 0.0343
ERAS-2025-010 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.4895 | 8.5016 | 0.0121
ERAS-2025-010 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.8775 | 19.0376 | 0.1601
ERAS-2025-010 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.9157 | 12.9792 | 0.0635
ERAS-2025-010 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.6866 | 9.7109 | 0.0243
ERAS-2025-010 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.4346 | 15.5533 | 0.1187
ERAS-2025-010 | 04 SOUTHEAST | 514832 | EASTERN4 | 138 | 26.3932 | 26.7921 | 0.3989
ERAS-2025-010 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 28.5679 | 29.0939 | 0.526
ERAS-2025-010 | 04 SOUTHEAST | 514835 | MEMRIAL4 | 138 | 40.9723 | 41.8798 | 0.9075
ERAS-2025-010 | 04 SOUTHEAST | 514837 | TENESTP4 | 138 | 34.5973 | 35.1923 | 0.595
ERAS-2025-010 | 04 SOUTHEAST | 514839 | BRYANT 4 | 138 | 31.8576 | 32.4639 | 0.6063
ERAS-2025-010 | 04 SOUTHEAST | 514840 | JONESTP4 | 138 | 29.7339 | 30.4691 | 0.7352
ERAS-2025-010 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.5869 | 21.9903 | 0.4034
ERAS-2025-010 | 04 SOUTHEAST | 514844 | BELISLE4 | 138 | 30.8525 | 31.2606 | 0.4081
ERAS-2025-010 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 36.4003 | 37.0833 | 0.683
ERAS-2025-010 | 04 SOUTHEAST | 514868 | DOUGLTP4 | 138 | 34.6893 | 35.1074 | 0.4181
ERAS-2025-010 | 04 SOUTHEAST | 514869 | WESTERN4 | 138 | 34.3826 | 34.8703 | 0.4877
ERAS-2025-010 | 04 SOUTHEAST | 514870 | STNWAL 4 | 138 | 31.7335 | 32.2147 | 0.4812
ERAS-2025-010 | 04 SOUTHEAST | 514874 | REMNGPK4 | 138 | 34.5007 | 35.1508 | 0.6501
ERAS-2025-010 | 04 SOUTHEAST | 514875 | OUMED 4 | 138 | 24.7787 | 25.0777 | 0.299
ERAS-2025-010 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 48.2107 | 49.3473 | 1.1366
ERAS-2025-010 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.2467 | 36.8966 | 1.6499
ERAS-2025-010 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.7538 | 25.3715 | 0.6177
ERAS-2025-010 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 24.186 | 24.6467 | 0.4607
ERAS-2025-010 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 39.2787 | 40.5458 | 1.2671
ERAS-2025-010 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.7636 | 22.2127 | 0.4491
ERAS-2025-010 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 40.3455 | 42.4858 | 2.1403
ERAS-2025-010 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 26.9147 | 31.7606 | 4.8459
ERAS-2025-010 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.2435 | 31.9114 | 5.6679
ERAS-2025-010 | 04 SOUTHEAST | 514923 | LIGHTCK4 | 138 | 27.5299 | 27.8068 | 0.2769
ERAS-2025-010 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 10.3125 | 10.3602 | 0.0477
ERAS-2025-010 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 22.7053 | 22.7974 | 0.0921
ERAS-2025-010 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 45.6264 | 46.1081 | 0.4817
ERAS-2025-010 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.7871 | 28.1741 | 0.387
ERAS-2025-010 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 11.1208 | 11.1775 | 0.0567
ERAS-2025-010 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 50.6543 | 53.8254 | 3.1711
ERAS-2025-010 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 36.1215 | 36.3783 | 0.2568
ERAS-2025-010 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 25.3607 | 25.4712 | 0.1105
ERAS-2025-010 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 24.2407 | 24.3451 | 0.1044
ERAS-2025-010 | 04 SOUTHEAST | 514951 | LITTLAX2 | 69 | 3.4009 | 3.4038 | 0.0029
ERAS-2025-010 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 37.2135 | 37.4875 | 0.274
ERAS-2025-010 | 04 SOUTHEAST | 514956 | MACOCTP2 | 69 | 3.3631 | 3.3658 | 0.0027
ERAS-2025-010 | 04 SOUTHEAST | 514959 | FOSTER 4 | 138 | 28.4309 | 28.6988 | 0.2679
ERAS-2025-010 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 21.097 | 21.2076 | 0.1106
ERAS-2025-010 | 04 SOUTHEAST | 514963 | TROSPER4 | 138 | 32.618 | 33.0479 | 0.4299
ERAS-2025-010 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 28.6962 | 29.2148 | 0.5186
ERAS-2025-010 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 28.3435 | 29.1662 | 0.8227
ERAS-2025-010 | 04 SOUTHEAST | 514969 | NE30TH 2 | 138 | 30.8593 | 31.3735 | 0.5142
ERAS-2025-010 | 04 SOUTHEAST | 514971 | GRNPAST4 | 138 | 21.73 | 22.0976 | 0.3676
ERAS-2025-010 | 04 SOUTHEAST | 514972 | RENO 2 | 69 | 13.5096 | 13.5471 | 0.0375
ERAS-2025-010 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 37.4628 | 38.2256 | 0.7628
ERAS-2025-010 | 04 SOUTHEAST | 514979 | 44&SUNL2 | 69 | 11.5928 | 11.617 | 0.0242
ERAS-2025-010 | 04 SOUTHEAST | 514980 | SUNNYLN2 | 69 | 11.8228 | 11.8487 | 0.0259
ERAS-2025-010 | 04 SOUTHEAST | 514981 | TINKER32 | 69 | 9.0277 | 9.0433 | 0.0156
ERAS-2025-010 | 04 SOUTHEAST | 514983 | LTLRLKT2 | 69 | 2.7926 | 2.7952 | 0.0026
ERAS-2025-010 | 04 SOUTHEAST | 514985 | TXSTELA2 | 69 | 3.9242 | 3.9291 | 0.0049
ERAS-2025-010 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 25.2938 | 25.6641 | 0.3703
ERAS-2025-010 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 15.0093 | 15.1667 | 0.1574
ERAS-2025-010 | 04 SOUTHEAST | 514989 | TXPLSTE2 | 69 | 3.0206 | 3.0235 | 0.0029
ERAS-2025-010 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 24.4355 | 24.7776 | 0.3421
ERAS-2025-010 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 21.0092 | 21.2347 | 0.2255
ERAS-2025-010 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 24.1557 | 24.4427 | 0.287
ERAS-2025-010 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 47.4661 | 47.7291 | 0.263
ERAS-2025-010 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.5949 | 30.9883 | 0.3934
ERAS-2025-010 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 18.2745 | 18.538 | 0.2635
ERAS-2025-010 | 04 SOUTHEAST | 515047 | WARWICK4 | 138 | 10.891 | 10.9265 | 0.0355
ERAS-2025-010 | 04 SOUTHEAST | 515051 | JACKTWN4 | 138 | 10.3419 | 10.3962 | 0.0543
ERAS-2025-010 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 22.0653 | 22.1463 | 0.081
ERAS-2025-010 | 04 SOUTHEAST | 515056 | WOLVERN4 | 138 | 8.9405 | 8.9793 | 0.0388
ERAS-2025-010 | 04 SOUTHEAST | 515057 | MOBIL 4 | 138 | 9.0202 | 9.0596 | 0.0394
ERAS-2025-010 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 15.0319 | 15.138 | 0.1061
ERAS-2025-010 | 04 SOUTHEAST | 515060 | INGLEWD4 | 138 | 10.9763 | 11.0329 | 0.0566
ERAS-2025-010 | 04 SOUTHEAST | 515061 | STGREG 4 | 138 | 9.7222 | 9.7668 | 0.0446
ERAS-2025-010 | 04 SOUTHEAST | 515062 | NE45TAP4 | 138 | 9.3976 | 9.4396 | 0.042
ERAS-2025-010 | 04 SOUTHEAST | 515065 | MCLOUD 2 | 69 | 4.969 | 4.9778 | 0.0088
ERAS-2025-010 | 04 SOUTHEAST | 515068 | SHAWNEE2 | 69 | 8.4462 | 8.4611 | 0.0149
ERAS-2025-010 | 04 SOUTHEAST | 515072 | SINCPAN2 | 69 | 6.0861 | 6.095 | 0.0089
ERAS-2025-010 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.923 | 11.9467 | 0.0237
ERAS-2025-010 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.8986 | 14.9812 | 0.0826
ERAS-2025-010 | 04 SOUTHEAST | 515156 | WASHPRK4 | 138 | 24.0725 | 24.3676 | 0.2951
ERAS-2025-010 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 14.8486 | 14.9452 | 0.0966
ERAS-2025-010 | 04 SOUTHEAST | 515366 | WFROSST4 | 138 | 13.0905 | 13.1665 | 0.076
ERAS-2025-010 | 04 SOUTHEAST | 515369 | BELLCOW4 | 138 | 6.9652 | 6.976 | 0.0108
ERAS-2025-010 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.9077 | 15.0145 | 0.1068
ERAS-2025-010 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.33 | 10.3544 | 0.0244
ERAS-2025-010 | 04 SOUTHEAST | 515387 | NEWDOMI4 | 138 | 29.9418 | 30.278 | 0.3362
ERAS-2025-010 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 16.0664 | 16.2023 | 0.1359
ERAS-2025-010 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 21.5304 | 21.6468 | 0.1164
ERAS-2025-010 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 27.8141 | 28.3463 | 0.5322
ERAS-2025-010 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 38.5806 | 40.5091 | 1.9285
ERAS-2025-010 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6672 | 22.1631 | 0.4959
ERAS-2025-010 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 38.7946 | 40.4054 | 1.6108
ERAS-2025-010 | 04 SOUTHEAST | 515502 | LITLAXT2 | 69 | 3.4056 | 3.4086 | 0.003
ERAS-2025-010 | 04 SOUTHEAST | 515504 | MCLOUDT2 | 69 | 4.9919 | 5.0008 | 0.0089
ERAS-2025-010 | 04 SOUTHEAST | 515516 | TXPLSTP2 | 69 | 3.0243 | 3.0272 | 0.0029
ERAS-2025-010 | 04 SOUTHEAST | 515532 | WOLVRNT4 | 138 | 9.0164 | 9.0559 | 0.0395
ERAS-2025-010 | 04 SOUTHEAST | 515642 | SINCPNT2 | 69 | 6.1209 | 6.1299 | 0.009
ERAS-2025-010 | 04 SOUTHEAST | 515675 | TRYON 4 | 138 | 9.6382 | 9.6523 | 0.0141
ERAS-2025-010 | 04 SOUTHEAST | 515707 | HSL13 4 | 138 | 42.6235 | 44.7682 | 2.1447
ERAS-2025-010 | 04 SOUTHEAST | 515806 | TINKER64 | 138 | 20.4992 | 20.7172 | 0.218
ERAS-2025-010 | 04 SOUTHEAST | 515851 | CROSTWN4 | 138 | 27.9591 | 28.2391 | 0.28
ERAS-2025-010 | 04 SOUTHEAST | 515959 | TINKER74 | 138 | 20.7259 | 20.9593 | 0.2334
ERAS-2025-010 | 04 SOUTHEAST | 515963 | GATEWAY4 | 138 | 23.3514 | 23.6221 | 0.2707
ERAS-2025-010 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.8615 | 29.295 | 0.4335
ERAS-2025-010 | 04 SOUTHEAST | 516100 | HORIZON4 | 138 | 6.9967 | 7.007 | 0.0103
ERAS-2025-010 | 04 SOUTHEAST | 516210 | RAVEN 7 | 345 | 20.2255 | 20.2519 | 0.0264
ERAS-2025-010 | 04 SOUTHEAST | 520449 | STERLNG4 | 138 | 11.9977 | 12.0609 | 0.0632
ERAS-2025-010 | 04 SOUTHEAST | 520464 | MEEKER 4 | 138 | 9.4975 | 9.5319 | 0.0344
ERAS-2025-010 | 04 SOUTHEAST | 520526 | GRDGVTP4 | 138 | 7.3914 | 7.4078 | 0.0164
ERAS-2025-010 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 31.3003 | 31.4809 | 0.1806
ERAS-2025-010 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 15.178 | 15.3599 | 0.1819
ERAS-2025-010 | 04 SOUTHEAST | 520994 | MEEKRSW4 | 138 | 8.7603 | 8.7853 | 0.025
ERAS-2025-010 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.4895 | 8.5016 | 0.0121
ERAS-2025-010 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.0044 | 10.024 | 0.0196
ERAS-2025-010 | 04 SOUTHEAST | 521097 | WREDHIL4 | 138 | 7.5774 | 7.5947 | 0.0173
ERAS-2025-010 | 04 SOUTHEAST | 521107 | RSSVILE4 | 138 | 13.0905 | 13.1665 | 0.076
ERAS-2025-010 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9328 | 5.0274 | 0.0946
ERAS-2025-010 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 50.6358 | 53.8044 | 3.1686
ERAS-2025-010 | 04 SOUTHEAST | 778734 | ERA-10 | 138 | 41.8289 | 44.888 | 3.0591
ERAS-2025-010 | 04 SOUTHEAST | 788714 | ERA-04-1 | 138 | 36.9505 | 38.5292 | 1.5787
ERAS-2025-010 | 04 SOUTHEAST | 788716 | ERA-04-2 | 138 | 36.5811 | 38.147 | 1.5659
ERAS-2025-022 | 04 SOUTHEAST | 505596 | EXPLOR 4 | 138 | 5.7526 | 5.7822 | 0.0296
ERAS-2025-022 | 04 SOUTHEAST | 505598 | ALLEN 4 | 138 | 5.7865 | 5.8485 | 0.062
ERAS-2025-022 | 04 SOUTHEAST | 505600 | TUPELO 4 | 138 | 11.8673 | 12.3978 | 0.5305
ERAS-2025-022 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 9.2371 | 9.2708 | 0.0337
ERAS-2025-022 | 04 SOUTHEAST | 505604 | DENISON4 | 138 | 3.3247 | 3.329 | 0.0043
ERAS-2025-022 | 04 SOUTHEAST | 505650 | GERTY 4 | 138 | 4.2677 | 4.3011 | 0.0334
ERAS-2025-022 | 04 SOUTHEAST | 505665 | CENTRATAP4 | 138 | 11.637 | 12.1697 | 0.5327
ERAS-2025-022 | 04 SOUTHEAST | 505666 | CENTRAHOMA4 | 138 | 6.3269 | 6.4588 | 0.1319
ERAS-2025-022 | 04 SOUTHEAST | 505671 | UNION VLY4 | 138 | 5.8359 | 6.3994 | 0.5635
ERAS-2025-022 | 04 SOUTHEAST | 505672 | AHLOSO4 | 138 | 5.1947 | 5.6354 | 0.4407
ERAS-2025-022 | 04 SOUTHEAST | 505674 | MONTE VISTA4 | 138 | 3.9943 | 4.5867 | 0.5924
ERAS-2025-022 | 04 SOUTHEAST | 510880 | COALGTP4 | 138 | 6.8769 | 7.0118 | 0.1349
ERAS-2025-022 | 04 SOUTHEAST | 510881 | ALLENGT4 | 138 | 11.4805 | 11.9719 | 0.4914
ERAS-2025-022 | 04 SOUTHEAST | 510916 | ALLEN--4 | 138 | 5.7801 | 5.8419 | 0.0618
ERAS-2025-022 | 04 SOUTHEAST | 510935 | EXPCOLT4 | 138 | 8.2402 | 8.4903 | 0.2501
ERAS-2025-022 | 04 SOUTHEAST | 510949 | WAPANUCKA 4 | 138 | 8.5513 | 8.7902 | 0.2389
ERAS-2025-022 | 04 SOUTHEAST | 515157 | BROWN 4 | 138 | 9.1922 | 9.2253 | 0.0331
ERAS-2025-022 | 04 SOUTHEAST | 515159 | COLBRTP4 | 138 | 6.9428 | 6.9614 | 0.0186
ERAS-2025-022 | 04 SOUTHEAST | 515192 | LULA 4 | 138 | 10.0805 | 10.3508 | 0.2703
ERAS-2025-022 | 04 SOUTHEAST | 520406 | TUPELO 4 | 138 | 10.8069 | 11.2302 | 0.4233
ERAS-2025-022 | 04 SOUTHEAST | 520448 | BOGYDPT4 | 138 | 5.631 | 5.711 | 0.08
ERAS-2025-022 | 04 SOUTHEAST | 520539 | TCPECTP4 | 138 | 8.1046 | 8.3089 | 0.2043
ERAS-2025-022 | 04 SOUTHEAST | 520963 | KRSEY2_4 | 138 | 5.9618 | 5.9757 | 0.0139
ERAS-2025-022 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 12.0685 | 12.0905 | 0.022
ERAS-2025-022 | 04 SOUTHEAST | 521049 | SCLMNJC4 | 138 | 7.7046 | 7.726 | 0.0214
ERAS-2025-022 | 04 SOUTHEAST | 521071 | STNWLSW4 | 138 | 11.5281 | 11.981 | 0.4529
ERAS-2025-022 | 04 SOUTHEAST | 521074 | BOGGY4 | 138 | 9.6816 | 10.0035 | 0.3219
ERAS-2025-022 | 04 SOUTHEAST | 521075 | STNWLTP4 | 138 | 9.9132 | 10.2235 | 0.3103
ERAS-2025-022 | 04 SOUTHEAST | 788828 | ERA-22 | 138 | 3.9186 | 4.5128 | 0.5942
ERAS-2025-023 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 16.0198 | 16.0387 | 0.0189
ERAS-2025-023 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 25.5579 | 25.5822 | 0.0243
ERAS-2025-023 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 18.2153 | 18.2331 | 0.0178
ERAS-2025-023 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.7735 | 15.7941 | 0.0206
ERAS-2025-023 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 25.2612 | 25.2895 | 0.0283
ERAS-2025-023 | 04 SOUTHEAST | 300741 | 5SPORTSMAN | 161 | 41.79 | 41.813 | 0.023
ERAS-2025-023 | 04 SOUTHEAST | 300927 | 2CLEVLND | 69 | 10.889 | 10.8913 | 0.0023
ERAS-2025-023 | 04 SOUTHEAST | 300949 | 7JASPER | 345 | 12.8429 | 12.8526 | 0.0097
ERAS-2025-023 | 04 SOUTHEAST | 300950 | 5JASPER | 161 | 13.2774 | 13.2811 | 0.0037
ERAS-2025-023 | 04 SOUTHEAST | 301640 | 4HOMNYTP | 138 | 9.8529 | 9.8565 | 0.0036
ERAS-2025-023 | 04 SOUTHEAST | 504202 | SILOAMSP 5 | 161 | 20.407 | 20.412 | 0.005
ERAS-2025-023 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.4709 | 7.4759 | 0.005
ERAS-2025-023 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.9365 | 23.9834 | 0.0469
ERAS-2025-023 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.2734 | 24.2821 | 0.0087
ERAS-2025-023 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.6128 | 10.6179 | 0.0051
ERAS-2025-023 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 22.9488 | 22.9553 | 0.0065
ERAS-2025-023 | 04 SOUTHEAST | 506957 | TONTITN5 | 161 | 23.1964 | 23.2034 | 0.007
ERAS-2025-023 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.5221 | 9.5257 | 0.0036
ERAS-2025-023 | 04 SOUTHEAST | 506992 | WEDINGTON | 161 | 16.8908 | 16.8948 | 0.004
ERAS-2025-023 | 04 SOUTHEAST | 509714 | CIP 4 | 138 | 25.9316 | 26.017 | 0.0854
ERAS-2025-023 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.8644 | 12.8794 | 0.015
ERAS-2025-023 | 04 SOUTHEAST | 509726 | OWASO1_4 | 138 | 15.0364 | 15.0573 | 0.0209
ERAS-2025-023 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.8274 | 18.8584 | 0.031
ERAS-2025-023 | 04 SOUTHEAST | 509743 | DENVR-E4 | 138 | 8.7581 | 8.7695 | 0.0114
ERAS-2025-023 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 22.0789 | 22.1438 | 0.0649
ERAS-2025-023 | 04 SOUTHEAST | 509746 | DENVTAP4 | 138 | 10.3737 | 10.3897 | 0.016
ERAS-2025-023 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.8754 | 18.9054 | 0.03
ERAS-2025-023 | 04 SOUTHEAST | 509753 | 116JENK4 | 138 | 44.9863 | 45.0978 | 0.1115
ERAS-2025-023 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.079 | 23.2338 | 0.1548
ERAS-2025-023 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 34.3644 | 34.467 | 0.1026
ERAS-2025-023 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.606 | 26.6478 | 0.0418
ERAS-2025-023 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.6675 | 16.6878 | 0.0203
ERAS-2025-023 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 19.541 | 19.5744 | 0.0334
ERAS-2025-023 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 20.4813 | 20.5186 | 0.0373
ERAS-2025-023 | 04 SOUTHEAST | 509770 | LLAN WT4 | 138 | 28.7378 | 28.7954 | 0.0576
ERAS-2025-023 | 04 SOUTHEAST | 509772 | FORD---4 | 138 | 19.1058 | 19.1342 | 0.0284
ERAS-2025-023 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 53.3552 | 53.5193 | 0.1641
ERAS-2025-023 | 04 SOUTHEAST | 509775 | 136YALE4 | 138 | 31.286 | 31.342 | 0.056
ERAS-2025-023 | 04 SOUTHEAST | 509780 | MAYO--S4 | 138 | 22.2429 | 22.2787 | 0.0358
ERAS-2025-023 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.7409 | 33.9837 | 0.2428
ERAS-2025-023 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 64.6274 | 64.8529 | 0.2255
ERAS-2025-023 | 04 SOUTHEAST | 509784 | A.A.---4 | 138 | 23.7601 | 23.8178 | 0.0577
ERAS-2025-023 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 19.4512 | 19.4806 | 0.0294
ERAS-2025-023 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 25.3441 | 25.4015 | 0.0574
ERAS-2025-023 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 39.6885 | 39.7852 | 0.0967
ERAS-2025-023 | 04 SOUTHEAST | 509804 | E 11TH ST 4 | 138 | 31.3627 | 31.4304 | 0.0677
ERAS-2025-023 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.8712 | 8.88 | 0.0088
ERAS-2025-023 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 51.7853 | 52.0633 | 0.278
ERAS-2025-023 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 31.8843 | 32.1899 | 0.3056
ERAS-2025-023 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 27.082 | 27.1336 | 0.0516
ERAS-2025-023 | 04 SOUTHEAST | 509814 | S HILLWT4 | 138 | 22.2521 | 22.279 | 0.0269
ERAS-2025-023 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.9707 | 30.0324 | 0.0617
ERAS-2025-023 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 46.4917 | 46.8096 | 0.3179
ERAS-2025-023 | 04 SOUTHEAST | 509822 | W.ED.-E4 | 138 | 8.6766 | 8.6878 | 0.0112
ERAS-2025-023 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 20.0247 | 20.0544 | 0.0297
ERAS-2025-023 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 31.1767 | 31.3811 | 0.2044
ERAS-2025-023 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 31.7802 | 32.0828 | 0.3026
ERAS-2025-023 | 04 SOUTHEAST | 509837 | 46ST--E4 | 138 | 3.6233 | 3.6249 | 0.0016
ERAS-2025-023 | 04 SOUTHEAST | 509839 | CDC-ET 4 | 138 | 26.5651 | 26.6538 | 0.0887
ERAS-2025-023 | 04 SOUTHEAST | 509840 | WHIRLPO4 | 138 | 27.3299 | 27.4251 | 0.0952
ERAS-2025-023 | 04 SOUTHEAST | 509842 | CDC-WT 4 | 138 | 28.1387 | 28.2399 | 0.1012
ERAS-2025-023 | 04 SOUTHEAST | 509843 | OWASO2_4 | 138 | 14.9678 | 14.9787 | 0.0109
ERAS-2025-023 | 04 SOUTHEAST | 509844 | OWASOTP4 | 138 | 16.1302 | 16.1543 | 0.0241
ERAS-2025-023 | 04 SOUTHEAST | 509845 | KIMCLRK4 | 138 | 23.4625 | 23.4958 | 0.0333
ERAS-2025-023 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 23.3527 | 23.3848 | 0.0321
ERAS-2025-023 | 04 SOUTHEAST | 509849 | ORU ETP4 | 138 | 35.8537 | 35.9243 | 0.0706
ERAS-2025-023 | 04 SOUTHEAST | 509850 | OAKSETP4 | 138 | 28.3352 | 28.3789 | 0.0437
ERAS-2025-023 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 16.2906 | 16.3201 | 0.0295
ERAS-2025-023 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 26.2946 | 26.7032 | 0.4086
ERAS-2025-023 | 04 SOUTHEAST | 509853 | ORU-WTP4 | 138 | 31.3782 | 31.4334 | 0.0552
ERAS-2025-023 | 04 SOUTHEAST | 509854 | VERDIGS4 | 138 | 14.9271 | 14.9375 | 0.0104
ERAS-2025-023 | 04 SOUTHEAST | 509855 | 81GARN-4 | 138 | 18.4808 | 18.5057 | 0.0249
ERAS-2025-023 | 04 SOUTHEAST | 509860 | OWAS1094 | 138 | 15.5253 | 15.5445 | 0.0192
ERAS-2025-023 | 04 SOUTHEAST | 509861 | E41ST_E4 | 138 | 17.6899 | 17.7142 | 0.0243
ERAS-2025-023 | 04 SOUTHEAST | 509863 | PPTAP 4 | 138 | 20.1048 | 20.1557 | 0.0509
ERAS-2025-023 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.4772 | 12.4888 | 0.0116
ERAS-2025-023 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 18.457 | 18.4873 | 0.0303
ERAS-2025-023 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.7974 | 23.9275 | 0.1301
ERAS-2025-023 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.3601 | 34.4375 | 0.0774
ERAS-2025-023 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 54.3281 | 54.4971 | 0.169
ERAS-2025-023 | 04 SOUTHEAST | 509884 | SKIATOK4 | 138 | 12.4253 | 12.444 | 0.0187
ERAS-2025-023 | 04 SOUTHEAST | 509887 | OWAS88_4 | 138 | 18.8622 | 18.9001 | 0.0379
ERAS-2025-023 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.4911 | 24.5266 | 0.0355
ERAS-2025-023 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 16.5675 | 16.59 | 0.0225
ERAS-2025-023 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 24.2538 | 24.3087 | 0.0549
ERAS-2025-023 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 45.9016 | 46.2139 | 0.3123
ERAS-2025-023 | 04 SOUTHEAST | 509900 | 46ST-TP-4 | 138 | 20.6494 | 20.704 | 0.0546
ERAS-2025-023 | 04 SOUTHEAST | 509908 | SKIATKTP4 | 138 | 12.4647 | 12.4835 | 0.0188
ERAS-2025-023 | 04 SOUTHEAST | 509915 | ANTHEM7 | 345 | 13.8916 | 13.9441 | 0.0525
ERAS-2025-023 | 04 SOUTHEAST | 510378 | SCOFCTY4 | 138 | 9.2018 | 9.2122 | 0.0104
ERAS-2025-023 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 11.6154 | 11.6765 | 0.0611
ERAS-2025-023 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.7719 | 11.9977 | 0.2258
ERAS-2025-023 | 04 SOUTHEAST | 510384 | WATOVA 4 | 138 | 9.6008 | 9.6047 | 0.0039
ERAS-2025-023 | 04 SOUTHEAST | 510385 | RICE CK4 | 138 | 12.3357 | 12.3441 | 0.0084
ERAS-2025-023 | 04 SOUTHEAST | 510388 | BARNSAL4 | 138 | 8.8449 | 8.8512 | 0.0063
ERAS-2025-023 | 04 SOUTHEAST | 510396 | N.E.S.-4 | 138 | 38.1396 | 38.1864 | 0.0468
ERAS-2025-023 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 17.392 | 18.4977 | 1.1057
ERAS-2025-023 | 04 SOUTHEAST | 510413 | HAWTHRN4 | 138 | 21.4779 | 21.4925 | 0.0146
ERAS-2025-023 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 12.367 | 12.3729 | 0.0059
ERAS-2025-023 | 04 SOUTHEAST | 510904 | EXP_OKM4 | 138 | 10.5787 | 10.5832 | 0.0045
ERAS-2025-023 | 04 SOUTHEAST | 511877 | G16133G16146 | 345 | 33.7409 | 33.9837 | 0.2428
ERAS-2025-023 | 04 SOUTHEAST | 511878 | G16133_765TN | 765 | 9.7473 | 9.7858 | 0.0385
ERAS-2025-023 | 04 SOUTHEAST | 511879 | G16133_765R1 | 765 | 9.7473 | 9.7858 | 0.0385
ERAS-2025-023 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 27.8454 | 27.8815 | 0.0361
ERAS-2025-023 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 20.2128 | 20.3007 | 0.0879
ERAS-2025-023 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 18.0014 | 18.0188 | 0.0174
ERAS-2025-023 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 25.5564 | 25.5807 | 0.0243
ERAS-2025-023 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.8845 | 8.8978 | 0.0133
ERAS-2025-023 | 04 SOUTHEAST | 512735 | COFCTY2 | 69 | 10.0777 | 10.0826 | 0.0049
ERAS-2025-023 | 04 SOUTHEAST | 512749 | PAWNSW4 | 138 | 11.3384 | 11.3432 | 0.0048
ERAS-2025-023 | 04 SOUTHEAST | 512865 | GREC TAP7 | 345 | 26.5041 | 26.5392 | 0.0351
ERAS-2025-023 | 04 SOUTHEAST | 513124 | OOLOGAH 4 | 138 | 21.8655 | 21.8806 | 0.0151
ERAS-2025-023 | 04 SOUTHEAST | 513591 | HERRON 5 | 161 | 17.3759 | 17.3858 | 0.0099
ERAS-2025-023 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.5702 | 17.5803 | 0.0101
ERAS-2025-023 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.5702 | 17.5803 | 0.0101
ERAS-2025-023 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 20.7535 | 20.7844 | 0.0309
ERAS-2025-023 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 21.7236 | 21.7343 | 0.0107
ERAS-2025-023 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.988 | 11.9927 | 0.0047
ERAS-2025-023 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 21.3715 | 21.4688 | 0.0973
ERAS-2025-023 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 21.784 | 21.7948 | 0.0108
ERAS-2025-023 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.799 | 33.8258 | 0.0268
ERAS-2025-023 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.8609 | 30.9996 | 0.1387
ERAS-2025-023 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.3368 | 36.8966 | 1.5598
ERAS-2025-023 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.7865 | 25.3715 | 0.585
ERAS-2025-023 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 39.3701 | 40.5458 | 1.1757
ERAS-2025-023 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 40.576 | 42.4858 | 1.9098
ERAS-2025-023 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 26.9886 | 31.7606 | 4.772
ERAS-2025-023 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 26.3069 | 31.9114 | 5.6045
ERAS-2025-023 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.6408 | 30.9883 | 0.3475
ERAS-2025-023 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 33.3645 | 33.4316 | 0.0671
ERAS-2025-023 | 04 SOUTHEAST | 515228 | 5TRIBES5 | 161 | 16.3353 | 16.3431 | 0.0078
ERAS-2025-023 | 04 SOUTHEAST | 515230 | AGENCY 5 | 161 | 14.8048 | 14.8109 | 0.0061
ERAS-2025-023 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 14.3988 | 14.4059 | 0.0071
ERAS-2025-023 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.6334 | 21.6481 | 0.0147
ERAS-2025-023 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 24.7224 | 24.7708 | 0.0484
ERAS-2025-023 | 04 SOUTHEAST | 515249 | BEGGS 4 | 138 | 6.0311 | 6.0328 | 0.0017
ERAS-2025-023 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 25.9081 | 25.9116 | 0.0035
ERAS-2025-023 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 14.5506 | 14.5541 | 0.0035
ERAS-2025-023 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 10.4153 | 10.4173 | 0.002
ERAS-2025-023 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 18.4395 | 18.5635 | 0.124
ERAS-2025-023 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8527 | 11.8652 | 0.0125
ERAS-2025-023 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.9788 | 14.9879 | 0.0091
ERAS-2025-023 | 04 SOUTHEAST | 515473 | EXPGLNT4 | 138 | 25.5056 | 25.5403 | 0.0347
ERAS-2025-023 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 38.873 | 40.4054 | 1.5324
ERAS-2025-023 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.3677 | 15.3841 | 0.0164
ERAS-2025-023 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.3096 | 13.3201 | 0.0105
ERAS-2025-023 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 13.0658 | 13.0774 | 0.0116
ERAS-2025-023 | 04 SOUTHEAST | 515778 | GRIFFIN7 | 345 | 23.8997 | 23.9403 | 0.0406
ERAS-2025-023 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 19.4825 | 19.6592 | 0.1767
ERAS-2025-023 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.5661 | 13.5902 | 0.0241
ERAS-2025-023 | 04 SOUTHEAST | 515974 | GEN-2015-066 | 345 | 17.4329 | 17.4802 | 0.0473
ERAS-2025-023 | 04 SOUTHEAST | 515975 | G15-066T | 345 | 20.23 | 20.294 | 0.064
ERAS-2025-023 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 18.1531 | 18.2067 | 0.0536
ERAS-2025-023 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 18.0876 | 18.1408 | 0.0532
ERAS-2025-023 | 04 SOUTHEAST | 516036 | TRAV3WD7 | 345 | 8.88 | 8.9142 | 0.0342
ERAS-2025-023 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 18.1716 | 18.1952 | 0.0236
ERAS-2025-023 | 04 SOUTHEAST | 516092 | OKTAHA 5 | 161 | 11.2395 | 11.2435 | 0.004
ERAS-2025-023 | 04 SOUTHEAST | 516192 | WAGNWTIE7 | 345 | 15.7353 | 15.8377 | 0.1024
ERAS-2025-023 | 04 SOUTHEAST | 516207 | GADWALL7 | 345 | 15.7353 | 15.8377 | 0.1024
ERAS-2025-023 | 04 SOUTHEAST | 516210 | RAVEN 7 | 345 | 20.2204 | 20.2519 | 0.0315
ERAS-2025-023 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 15.3375 | 15.3539 | 0.0164
ERAS-2025-023 | 04 SOUTHEAST | 532774 | SWISVAL7 | 345 | 17.0997 | 17.1001 | 0.0004
ERAS-2025-023 | 04 SOUTHEAST | 532777 | NRSS7 | 345 | 11.9956 | 12.0197 | 0.0241
ERAS-2025-023 | 04 SOUTHEAST | 532778 | NEOSHORDGWF7 | 345 | 11.1098 | 11.1303 | 0.0205
ERAS-2025-023 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.5645 | 9.5705 | 0.006
ERAS-2025-023 | 04 SOUTHEAST | 532781 | CANEYWF7 | 345 | 9.21 | 9.2155 | 0.0055
ERAS-2025-023 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 19.2197 | 19.2285 | 0.0088
ERAS-2025-023 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.7609 | 17.8299 | 0.069
ERAS-2025-023 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 18.6073 | 18.6185 | 0.0112
ERAS-2025-023 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 18.0585 | 18.0635 | 0.005
ERAS-2025-023 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 16.01 | 16.0138 | 0.0038
ERAS-2025-023 | 04 SOUTHEAST | 532800 | LATHAMS7 | 345 | 10.1679 | 10.1737 | 0.0058
ERAS-2025-023 | 04 SOUTHEAST | 532911 | MUSTNG5 | 161 | 6.6959 | 6.6975 | 0.0016
ERAS-2025-023 | 04 SOUTHEAST | 532937 | NEOSHO 5 | 161 | 22.6501 | 22.6846 | 0.0345
ERAS-2025-023 | 04 SOUTHEAST | 532939 | N345 4 5 | 161 | 22.433 | 22.4674 | 0.0344
ERAS-2025-023 | 04 SOUTHEAST | 533020 | NEOSHOS4 | 138 | 26.3276 | 26.3673 | 0.0397
ERAS-2025-023 | 04 SOUTHEAST | 533021 | NEOSHO 4 | 138 | 26.3853 | 26.4251 | 0.0398
ERAS-2025-023 | 04 SOUTHEAST | 533022 | NEOSHON4 | 138 | 26.2551 | 26.2946 | 0.0395
ERAS-2025-023 | 04 SOUTHEAST | 533023 | N345 3 4 | 138 | 26.1036 | 26.1429 | 0.0393
ERAS-2025-023 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 24.746 | 24.748 | 0.002
ERAS-2025-023 | 04 SOUTHEAST | 533778 | NEOSHOS2 | 69 | 24.4865 | 24.5019 | 0.0154
ERAS-2025-023 | 04 SOUTHEAST | 541198 | PECULR 7 | 345 | 21.38 | 21.3808 | 0.0008
ERAS-2025-023 | 04 SOUTHEAST | 542940 | ATLNTIC7 | 345 | 20.7507 | 20.7513 | 0.0006
ERAS-2025-023 | 04 SOUTHEAST | 542965 | W.GRDNR7 | 345 | 26.6458 | 26.6473 | 0.0015
ERAS-2025-023 | 04 SOUTHEAST | 542966 | WGARDNR5 | 161 | 29.0718 | 29.0722 | 0.0004
ERAS-2025-023 | 04 SOUTHEAST | 542968 | STILWEL7 | 345 | 26.0765 | 26.0781 | 0.0016
ERAS-2025-023 | 04 SOUTHEAST | 542969 | STILWEL5 | 161 | 42.905 | 42.9064 | 0.0014
ERAS-2025-023 | 04 SOUTHEAST | 542981 | LACYGNE7 | 345 | 26.9552 | 26.9614 | 0.0062
ERAS-2025-023 | 04 SOUTHEAST | 543023 | LACYGNE_LK2 | 69 | 2.7047 | 2.7047 | 0
ERAS-2025-023 | 04 SOUTHEAST | 543629 | LACYGNE11_7 | 345 | 26.2638 | 26.2696 | 0.0058
ERAS-2025-023 | 04 SOUTHEAST | 543632 | LACYGNE22_7 | 345 | 26.2635 | 26.2693 | 0.0058
ERAS-2025-023 | 04 SOUTHEAST | 543659 | LACYGNE2 | 69 | 2.8421 | 2.8421 | 0
ERAS-2025-023 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 34.3644 | 34.467 | 0.1026
ERAS-2025-023 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.2204 | 20.2519 | 0.0315
ERAS-2025-023 | 04 SOUTHEAST | 709500 | GI-95_POI | 345 | 11.6479 | 11.6522 | 0.0043
ERAS-2025-023 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9345 | 5.0274 | 0.0929
ERAS-2025-023 | 04 SOUTHEAST | 760152 | TNOXF2 | 138 | 45.8472 | 46.1592 | 0.312
ERAS-2025-023 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.9029 | 1.9031 | 0.0002
ERAS-2025-023 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.89 | 1.8902 | 0.0002
ERAS-2025-023 | 04 SOUTHEAST | 762279 | GEN-2017-195 | 345 | 26.5728 | 26.5743 | 0.0015
ERAS-2025-023 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 36.4429 | 36.6373 | 0.1944
ERAS-2025-023 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 17.4048 | 17.4283 | 0.0235
ERAS-2025-023 | 04 SOUTHEAST | 763069 | G18-071-TAP | 345 | 14.9639 | 14.9794 | 0.0155
ERAS-2025-023 | 04 SOUTHEAST | 763109 | GEN-2018-079 | 138 | 7.1004 | 7.1177 | 0.0173
ERAS-2025-023 | 04 SOUTHEAST | 763113 | G18-079-TAP | 138 | 9.8434 | 9.8781 | 0.0347
ERAS-2025-023 | 04 SOUTHEAST | 764310 | G20-079-TAP | 161 | 18.1571 | 18.1625 | 0.0054
ERAS-2025-023 | 04 SOUTHEAST | 766260 | GEN-2020-007 | 345 | 23.4784 | 23.4831 | 0.0047
ERAS-2025-023 | 04 SOUTHEAST | 766261 | G20-007-TAP | 345 | 26.0953 | 26.1011 | 0.0058
ERAS-2025-023 | 04 SOUTHEAST | 788833 | ERA-23 | 345 | 17.2808 | 18.3869 | 1.1061
ERAS-2025-024 | 04 SOUTHEAST | 500001 | COMANC7_TAP | 345 | 13.2782 | 13.7211 | 0.4429
ERAS-2025-024 | 04 SOUTHEAST | 511405 | BINGER 4 | 138 | 6.052 | 6.0617 | 0.0097
ERAS-2025-024 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.0639 | 16.3657 | 0.3018
ERAS-2025-024 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.8288 | 10.8578 | 0.029
ERAS-2025-024 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.3764 | 8.4819 | 0.1055
ERAS-2025-024 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.1782 | 9.3049 | 0.1267
ERAS-2025-024 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 13.3274 | 14.1485 | 0.8211
ERAS-2025-024 | 04 SOUTHEAST | 511429 | L AIRGS4 | 138 | 12.3847 | 13.0854 | 0.7007
ERAS-2025-024 | 04 SOUTHEAST | 511430 | LWS N4 | 138 | 11.1261 | 11.68 | 0.5539
ERAS-2025-024 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.7536 | 12.3698 | 0.6162
ERAS-2025-024 | 04 SOUTHEAST | 511435 | SNYDER-4 | 138 | 6.9231 | 6.9915 | 0.0684
ERAS-2025-024 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 10.0887 | 10.1776 | 0.0889
ERAS-2025-024 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 19.7392 | 23.996 | 4.2568
ERAS-2025-024 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.2613 | 12.9336 | 0.6723
ERAS-2025-024 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 9.1665 | 9.1892 | 0.0227
ERAS-2025-024 | 04 SOUTHEAST | 511450 | CORNVIL2 | 69 | 7.1325 | 7.1433 | 0.0108
ERAS-2025-024 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 5.2374 | 5.2537 | 0.0163
ERAS-2025-024 | 04 SOUTHEAST | 511452 | DUNCAN-2 | 69 | 7.1546 | 7.1826 | 0.028
ERAS-2025-024 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 7.0476 | 7.1337 | 0.0861
ERAS-2025-024 | 04 SOUTHEAST | 511455 | D.E.S.-4 | 138 | 6.5339 | 6.5924 | 0.0585
ERAS-2025-024 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 7.0281 | 7.0766 | 0.0485
ERAS-2025-024 | 04 SOUTHEAST | 511457 | DUNTOS TP2 | 69 | 7.1791 | 7.2014 | 0.0223
ERAS-2025-024 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 6.4486 | 6.4985 | 0.0499
ERAS-2025-024 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 17.1359 | 17.5792 | 0.4433
ERAS-2025-024 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 27.4818 | 30.7996 | 3.3178
ERAS-2025-024 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 15.5713 | 16.2237 | 0.6524
ERAS-2025-024 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 8.4516 | 8.5473 | 0.0957
ERAS-2025-024 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.3299 | 7.4091 | 0.0792
ERAS-2025-024 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 12.5124 | 13.2165 | 0.7041
ERAS-2025-024 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 6.224 | 6.2621 | 0.0381
ERAS-2025-024 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 13.2577 | 14.0274 | 0.7697
ERAS-2025-024 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.3182 | 34.6305 | 0.3123
ERAS-2025-024 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 12.829 | 12.8684 | 0.0394
ERAS-2025-024 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.6483 | 10.8534 | 0.2051
ERAS-2025-024 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 9.2246 | 9.2956 | 0.071
ERAS-2025-024 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 13.6603 | 14.5292 | 0.8689
ERAS-2025-024 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 23.7789 | 26.6762 | 2.8973
ERAS-2025-024 | 04 SOUTHEAST | 511500 | CACHETP4 | 138 | 8.7832 | 9.0554 | 0.2722
ERAS-2025-024 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.8175 | 4.8513 | 0.0338
ERAS-2025-024 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 12.5504 | 13.2538 | 0.7034
ERAS-2025-024 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 13.2088 | 14.0091 | 0.8003
ERAS-2025-024 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.6414 | 13.3675 | 0.7261
ERAS-2025-024 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 9.3105 | 9.3847 | 0.0742
ERAS-2025-024 | 04 SOUTHEAST | 511525 | LDISPOS2 | 69 | 5.266 | 5.2899 | 0.0239
ERAS-2025-024 | 04 SOUTHEAST | 511526 | L-RLITP2 | 69 | 7.8132 | 7.8625 | 0.0493
ERAS-2025-024 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 12.5704 | 13.275 | 0.7046
ERAS-2025-024 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 9.0046 | 9.361 | 0.3564
ERAS-2025-024 | 04 SOUTHEAST | 511552 | DUNCHERTP4 | 138 | 6.8372 | 6.913 | 0.0758
ERAS-2025-024 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.5987 | 10.7983 | 0.1996
ERAS-2025-024 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 11.0311 | 11.195 | 0.1639
ERAS-2025-024 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 7.0877 | 7.1479 | 0.0602
ERAS-2025-024 | 04 SOUTHEAST | 511586 | TONKAWA4 | 138 | 10.9402 | 11.0381 | 0.0979
ERAS-2025-024 | 04 SOUTHEAST | 511587 | MATO 7 | 345 | 10.1267 | 10.1569 | 0.0302
ERAS-2025-024 | 04 SOUTHEAST | 511600 | HVBUS | 138 | 7.9538 | 8.0043 | 0.0505
ERAS-2025-024 | 04 SOUTHEAST | 511607 | O.K.U.3-7 | 345 | 7.0281 | 7.0766 | 0.0485
ERAS-2025-024 | 04 SOUTHEAST | 511920 | CDW-SUB | 345 | 11.5457 | 11.6902 | 0.1445
ERAS-2025-024 | 04 SOUTHEAST | 511979 | RSHSPR1_MPT1 | 345 | 6.0534 | 6.1025 | 0.0491
ERAS-2025-024 | 04 SOUTHEAST | 511990 | GREATPL4 | 138 | 7.0132 | 7.1334 | 0.1202
ERAS-2025-024 | 04 SOUTHEAST | 511992 | HVBUS | 345 | 12.7044 | 12.8909 | 0.1865
ERAS-2025-024 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 25.2674 | 25.5801 | 0.3127
ERAS-2025-024 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.133 | 12.1909 | 0.0579
ERAS-2025-024 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.1602 | 20.4235 | 0.2633
ERAS-2025-024 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 35.6275 | 35.8665 | 0.239
ERAS-2025-024 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 38.7651 | 39.0014 | 0.2363
ERAS-2025-024 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 32.0601 | 32.2784 | 0.2183
ERAS-2025-024 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 7.2252 | 7.338 | 0.1128
ERAS-2025-024 | 04 SOUTHEAST | 588780 | GEN-2017-036 | 138 | 6.7789 | 6.8912 | 0.1123
ERAS-2025-024 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 12.3305 | 12.6196 | 0.2891
ERAS-2025-024 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 12.2576 | 12.5431 | 0.2855
ERAS-2025-024 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 15.2545 | 15.8793 | 0.6248
ERAS-2025-024 | 04 SOUTHEAST | 788837 | ERA-24 | 138 | 19.7099 | 23.9681 | 4.2582
ERAS-2025-024 | 04 SOUTHEAST | 789744 | ERA-2025-26 | 345 | 13.1182 | 13.5503 | 0.4321
ERAS-2025-025 | 04 SOUTHEAST | 500001 | COMANC7_TAP | 345 | 13.6982 | 13.7211 | 0.0229
ERAS-2025-025 | 04 SOUTHEAST | 511405 | BINGER 4 | 138 | 6.0417 | 6.0617 | 0.02
ERAS-2025-025 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.315 | 16.3657 | 0.0507
ERAS-2025-025 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.8165 | 10.8578 | 0.0413
ERAS-2025-025 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.4649 | 8.4819 | 0.017
ERAS-2025-025 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.2844 | 9.3049 | 0.0205
ERAS-2025-025 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 23.9679 | 23.996 | 0.0281
ERAS-2025-025 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.923 | 12.9336 | 0.0106
ERAS-2025-025 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 9.1571 | 9.1892 | 0.0321
ERAS-2025-025 | 04 SOUTHEAST | 511446 | CL-AFTP4 | 138 | 7.1691 | 7.1736 | 0.0045
ERAS-2025-025 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 18.4164 | 18.4831 | 0.0667
ERAS-2025-025 | 04 SOUTHEAST | 511450 | CORNVIL2 | 69 | 7.1386 | 7.1433 | 0.0047
ERAS-2025-025 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 5.2514 | 5.2537 | 0.0023
ERAS-2025-025 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 12.2538 | 12.2622 | 0.0084
ERAS-2025-025 | 04 SOUTHEAST | 511463 | HOB-JCT4 | 138 | 7.6138 | 7.6225 | 0.0087
ERAS-2025-025 | 04 SOUTHEAST | 511464 | HOB-JCT2 | 69 | 6.5297 | 6.5326 | 0.0029
ERAS-2025-025 | 04 SOUTHEAST | 511465 | HOBART-2 | 69 | 5.7667 | 5.769 | 0.0023
ERAS-2025-025 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 17.5691 | 17.5792 | 0.0101
ERAS-2025-025 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 30.7381 | 30.7996 | 0.0615
ERAS-2025-025 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 16.1899 | 16.2237 | 0.0338
ERAS-2025-025 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 6.2594 | 6.2621 | 0.0027
ERAS-2025-025 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 14.0148 | 14.0274 | 0.0126
ERAS-2025-025 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 33.9901 | 34.6305 | 0.6404
ERAS-2025-025 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 12.8286 | 12.8684 | 0.0398
ERAS-2025-025 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.8302 | 10.8534 | 0.0232
ERAS-2025-025 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 9.2884 | 9.2956 | 0.0072
ERAS-2025-025 | 04 SOUTHEAST | 511491 | RUSHSPT4 | 138 | 8.9986 | 9.0089 | 0.0103
ERAS-2025-025 | 04 SOUTHEAST | 511492 | SANTAFE4 | 138 | 9.5103 | 9.5221 | 0.0118
ERAS-2025-025 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 26.6317 | 26.6762 | 0.0445
ERAS-2025-025 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.5719 | 10.5887 | 0.0168
ERAS-2025-025 | 04 SOUTHEAST | 511502 | N29CHIK4 | 138 | 11.5799 | 11.6146 | 0.0347
ERAS-2025-025 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 7.3082 | 7.3163 | 0.0081
ERAS-2025-025 | 04 SOUTHEAST | 511515 | TEXAS 4 | 138 | 6.3256 | 6.3317 | 0.0061
ERAS-2025-025 | 04 SOUTHEAST | 511516 | ALEX BR4 | 138 | 6.869 | 6.8768 | 0.0078
ERAS-2025-025 | 04 SOUTHEAST | 511535 | CLIN-AF4 | 138 | 5.5288 | 5.5315 | 0.0027
ERAS-2025-025 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 11.3552 | 11.3674 | 0.0122
ERAS-2025-025 | 04 SOUTHEAST | 511554 | RKY_RDG4 | 138 | 6.0435 | 6.0485 | 0.005
ERAS-2025-025 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.3708 | 12.3788 | 0.008
ERAS-2025-025 | 04 SOUTHEAST | 511562 | ROUNDCK4 | 138 | 7.3872 | 7.3946 | 0.0074
ERAS-2025-025 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.775 | 10.7983 | 0.0233
ERAS-2025-025 | 04 SOUTHEAST | 511564 | MARTHA 4 | 138 | 4.599 | 4.6013 | 0.0023
ERAS-2025-025 | 04 SOUTHEAST | 511569 | DRFTSND4 | 138 | 7.8488 | 7.8559 | 0.0071
ERAS-2025-025 | 04 SOUTHEAST | 511573 | REDBDPLN4 | 138 | 4.2832 | 4.2856 | 0.0024
ERAS-2025-025 | 04 SOUTHEAST | 511575 | LEONARD4 | 138 | 10.4067 | 10.4227 | 0.016
ERAS-2025-025 | 04 SOUTHEAST | 511586 | TONKAWA4 | 138 | 10.9965 | 11.0381 | 0.0416
ERAS-2025-025 | 04 SOUTHEAST | 511587 | MATO 7 | 345 | 10.1424 | 10.1569 | 0.0145
ERAS-2025-025 | 04 SOUTHEAST | 511592 | SEVEN7A_HV | 345 | 9.7184 | 9.7315 | 0.0131
ERAS-2025-025 | 04 SOUTHEAST | 511599 | SEVEN7AB2 | 345 | 9.7184 | 9.7315 | 0.0131
ERAS-2025-025 | 04 SOUTHEAST | 511600 | HVBUS | 138 | 7.9829 | 8.0043 | 0.0214
ERAS-2025-025 | 04 SOUTHEAST | 511608 | SEVEN7AB3 | 345 | 9.7184 | 9.7315 | 0.0131
ERAS-2025-025 | 04 SOUTHEAST | 511920 | CDW-SUB | 345 | 11.666 | 11.6902 | 0.0242
ERAS-2025-025 | 04 SOUTHEAST | 511992 | HVBUS | 345 | 12.8596 | 12.8909 | 0.0313
ERAS-2025-025 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 25.3289 | 25.5801 | 0.2512
ERAS-2025-025 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.3347 | 36.8966 | 1.5619
ERAS-2025-025 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.3391 | 47.7986 | 0.4595
ERAS-2025-025 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 39.3584 | 40.5458 | 1.1874
ERAS-2025-025 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.8508 | 28.1741 | 0.3233
ERAS-2025-025 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 22.1012 | 22.1463 | 0.0451
ERAS-2025-025 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 25.2236 | 25.4727 | 0.2491
ERAS-2025-025 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 38.8684 | 40.4054 | 1.537
ERAS-2025-025 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.6223 | 15.7094 | 0.0871
ERAS-2025-025 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 19.6214 | 19.8521 | 0.2307
ERAS-2025-025 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.3128 | 20.4235 | 0.1107
ERAS-2025-025 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 35.3392 | 35.8665 | 0.5273
ERAS-2025-025 | 04 SOUTHEAST | 515933 | MLCLMRD4 | 138 | 9.4151 | 9.4282 | 0.0131
ERAS-2025-025 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.9808 | 11.0209 | 0.0401
ERAS-2025-025 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 11.3337 | 11.3457 | 0.012
ERAS-2025-025 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.9215 | 29.295 | 0.3735
ERAS-2025-025 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.611 | 44.8911 | 0.2801
ERAS-2025-025 | 04 SOUTHEAST | 520404 | MDCPRK4 | 138 | 5.7974 | 5.8018 | 0.0044
ERAS-2025-025 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 27.3413 | 27.5496 | 0.2083
ERAS-2025-025 | 04 SOUTHEAST | 520440 | HARPER2 | 69 | 16.4259 | 16.4602 | 0.0343
ERAS-2025-025 | 04 SOUTHEAST | 520468 | HINTON 4 | 138 | 4.0307 | 4.0417 | 0.011
ERAS-2025-025 | 04 SOUTHEAST | 520472 | CHCKSHA4 | 138 | 8.9934 | 9.0113 | 0.0179
ERAS-2025-025 | 04 SOUTHEAST | 520473 | CKSHATP4 | 138 | 11.7768 | 11.8076 | 0.0308
ERAS-2025-025 | 04 SOUTHEAST | 520490 | MTNVIEW2 | 69 | 2.5271 | 2.5278 | 0.0007
ERAS-2025-025 | 04 SOUTHEAST | 520496 | TUTTLE 4 | 138 | 6.6163 | 6.6229 | 0.0066
ERAS-2025-025 | 04 SOUTHEAST | 520501 | BRIDGCR4 | 138 | 8.8602 | 8.8706 | 0.0104
ERAS-2025-025 | 04 SOUTHEAST | 520503 | DEERCR 4 | 138 | 4.744 | 4.7519 | 0.0079
ERAS-2025-025 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 13.2983 | 13.3294 | 0.0311
ERAS-2025-025 | 04 SOUTHEAST | 520510 | NAPLSTP4 | 138 | 9.5102 | 9.5233 | 0.0131
ERAS-2025-025 | 04 SOUTHEAST | 520512 | BC SW 4 | 138 | 7.9444 | 7.9623 | 0.0179
ERAS-2025-025 | 04 SOUTHEAST | 520513 | BCV SW 4 | 138 | 6.0583 | 6.0633 | 0.005
ERAS-2025-025 | 04 SOUTHEAST | 520514 | BCVI SW4 | 138 | 8.869 | 8.8968 | 0.0278
ERAS-2025-025 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.5435 | 8.5536 | 0.0101
ERAS-2025-025 | 04 SOUTHEAST | 520531 | AMBER 4 | 138 | 7.4045 | 7.4122 | 0.0077
ERAS-2025-025 | 04 SOUTHEAST | 520543 | PINERDG2 | 69 | 2.9192 | 2.9208 | 0.0016
ERAS-2025-025 | 04 SOUTHEAST | 520547 | SEQOYAH4 | 138 | 21.4035 | 21.5312 | 0.1277
ERAS-2025-025 | 04 SOUTHEAST | 520552 | REDCNTP4 | 138 | 9.623 | 9.6353 | 0.0123
ERAS-2025-025 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 17.5156 | 17.5548 | 0.0392
ERAS-2025-025 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 38.577 | 39.0014 | 0.4244
ERAS-2025-025 | 04 SOUTHEAST | 520827 | BINGERJ4 | 138 | 8.2692 | 8.3213 | 0.0521
ERAS-2025-025 | 04 SOUTHEAST | 520828 | BLANCHD4 | 138 | 12.9447 | 12.9644 | 0.0197
ERAS-2025-025 | 04 SOUTHEAST | 520838 | CADDO 2 | 69 | 12.9719 | 12.9965 | 0.0246
ERAS-2025-025 | 04 SOUTHEAST | 520859 | COGAR 4 | 138 | 9.5928 | 9.6053 | 0.0125
ERAS-2025-025 | 04 SOUTHEAST | 520866 | CORDELL2 | 69 | 2.6338 | 2.634 | 0.0002
ERAS-2025-025 | 04 SOUTHEAST | 520867 | CORN TP4 | 138 | 15.4505 | 15.4963 | 0.0458
ERAS-2025-025 | 04 SOUTHEAST | 520870 | CYRIL 2 | 69 | 6.8514 | 6.8565 | 0.0051
ERAS-2025-025 | 04 SOUTHEAST | 520900 | EMPIRE 4 | 138 | 5.0875 | 5.091 | 0.0035
ERAS-2025-025 | 04 SOUTHEAST | 520911 | FLETCHR2 | 69 | 9.0638 | 9.0719 | 0.0081
ERAS-2025-025 | 04 SOUTHEAST | 520912 | FLETCH-4 | 138 | 7.6233 | 7.6355 | 0.0122
ERAS-2025-025 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 19.5831 | 19.687 | 0.1039
ERAS-2025-025 | 04 SOUTHEAST | 520925 | GOTEBO 2 | 69 | 4.2937 | 4.2944 | 0.0007
ERAS-2025-025 | 04 SOUTHEAST | 520950 | HYDRO 4 | 138 | 5.2903 | 5.3049 | 0.0146
ERAS-2025-025 | 04 SOUTHEAST | 520982 | LONEWLF2 | 69 | 3.3516 | 3.352 | 0.0004
ERAS-2025-025 | 04 SOUTHEAST | 521003 | MTNVWTP2 | 69 | 3.5241 | 3.5254 | 0.0013
ERAS-2025-025 | 04 SOUTHEAST | 521010 | NIJECT 4 | 138 | 5.5588 | 5.5824 | 0.0236
ERAS-2025-025 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.601 | 11.7167 | 0.1157
ERAS-2025-025 | 04 SOUTHEAST | 521024 | PARADSE4 | 138 | 6.195 | 6.2003 | 0.0053
ERAS-2025-025 | 04 SOUTHEAST | 521027 | PINERTP2 | 69 | 5.0544 | 5.0592 | 0.0048
ERAS-2025-025 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.5778 | 8.5918 | 0.014
ERAS-2025-025 | 04 SOUTHEAST | 521050 | SICKLES4 | 138 | 6.7167 | 6.7471 | 0.0304
ERAS-2025-025 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 7.7787 | 7.7878 | 0.0091
ERAS-2025-025 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.6937 | 9.7161 | 0.0224
ERAS-2025-025 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 31.2851 | 32.2784 | 0.9933
ERAS-2025-025 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 8.8976 | 8.9256 | 0.028
ERAS-2025-025 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 6.5764 | 6.5824 | 0.006
ERAS-2025-025 | 04 SOUTHEAST | 521137 | LTELKSW2 | 69 | 3.6932 | 3.6936 | 0.0004
ERAS-2025-025 | 04 SOUTHEAST | 529302 | OMALTUS4 | 138 | 4.7429 | 4.7452 | 0.0023
ERAS-2025-025 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 12.6028 | 12.6196 | 0.0168
ERAS-2025-025 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 24.4096 | 24.6422 | 0.2326
ERAS-2025-025 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 24.4593 | 24.6929 | 0.2336
ERAS-2025-025 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 15.8469 | 15.8793 | 0.0324
ERAS-2025-025 | 04 SOUTHEAST | 788995 | ERA-2025-25 | 138 | 28.9253 | 29.9182 | 0.9929
ERAS-2025-002 | 05 SOUTHWEST | 500001 | COMANC7_TAP | 345 | 13.6642 | 13.6679 | 0.0037
ERAS-2025-002 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 7.6212 | 7.6304 | 0.0092
ERAS-2025-002 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 11.605 | 11.6004 | -0.0046
ERAS-2025-002 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 7.5903 | 7.5994 | 0.0091
ERAS-2025-002 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.6212 | 7.6304 | 0.0092
ERAS-2025-002 | 05 SOUTHWEST | 511607 | O.K.U.3-7 | 345 | 7.6212 | 7.6304 | 0.0092
ERAS-2025-002 | 05 SOUTHWEST | 511999 | DVRSION-WIND | 345 | 4.9576 | 4.9613 | 0.0037
ERAS-2025-002 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 23.1929 | 23.142 | -0.0509
ERAS-2025-002 | 05 SOUTHWEST | 515378 | WWRDEHV9 | 765 | 5.4173 | 5.3665 | -0.0508
ERAS-2025-002 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.9934 | 8.9961 | 0.0027
ERAS-2025-002 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 11.6219 | 11.6175 | -0.0044
ERAS-2025-002 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3275 | 17.334 | 0.0065
ERAS-2025-002 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 30.0605 | 30.063 | 0.0025
ERAS-2025-002 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.2085 | 16.2097 | 0.0012
ERAS-2025-002 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.8421 | 17.8428 | 0.0007
ERAS-2025-002 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 15.172 | 15.1733 | 0.0013
ERAS-2025-002 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 7.1403 | 7.1406 | 0.0003
ERAS-2025-002 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.9435 | 8.9439 | 0.0004
ERAS-2025-002 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.3417 | 11.3421 | 0.0004
ERAS-2025-002 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6917 | 10.6924 | 0.0007
ERAS-2025-002 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.4139 | 12.416 | 0.0021
ERAS-2025-002 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.7775 | 11.7795 | 0.002
ERAS-2025-002 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2191 | 11.2233 | 0.0042
ERAS-2025-002 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.9007 | 6.9015 | 0.0008
ERAS-2025-002 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.9741 | 7.9748 | 0.0007
ERAS-2025-002 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9492 | 6.9496 | 0.0004
ERAS-2025-002 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.8449 | 10.8468 | 0.0019
ERAS-2025-002 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.1958 | 15.198 | 0.0022
ERAS-2025-002 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.9622 | 11.965 | 0.0028
ERAS-2025-002 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.9741 | 15.9758 | 0.0017
ERAS-2025-002 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4824 | 25.4894 | 0.007
ERAS-2025-002 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7675 | 33.7794 | 0.0119
ERAS-2025-002 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.6117 | 14.6161 | 0.0044
ERAS-2025-002 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5968 | 11.5984 | 0.0016
ERAS-2025-002 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5968 | 11.5984 | 0.0016
ERAS-2025-002 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.7743 | 8.7749 | 0.0006
ERAS-2025-002 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0041 | 6.0045 | 0.0004
ERAS-2025-002 | 05 SOUTHWEST | 525731 | SP-ABERNTH+2 | 69 | 3.0534 | 3.0536 | 0.0002
ERAS-2025-002 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.6292 | 2.6294 | 0.0002
ERAS-2025-002 | 05 SOUTHWEST | 525750 | G18-015-TAP | 345 | 5.9045 | 5.9147 | 0.0102
ERAS-2025-002 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.1947 | 6.1954 | 0.0007
ERAS-2025-002 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4948 | 5.4951 | 0.0003
ERAS-2025-002 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0918 | 7.0928 | 0.001
ERAS-2025-002 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 6.1441 | 6.1447 | 0.0006
ERAS-2025-002 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.5229 | 4.5234 | 0.0005
ERAS-2025-002 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9489 | 7.9502 | 0.0013
ERAS-2025-002 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.7336 | 21.7514 | 0.0178
ERAS-2025-002 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 28.8802 | 28.977 | 0.0968
ERAS-2025-002 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 28.8802 | 28.977 | 0.0968
ERAS-2025-002 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.0386 | 22.4092 | 0.3706
ERAS-2025-002 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.1935 | 10.2557 | 0.0622
ERAS-2025-002 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.58 | 28.6746 | 0.0946
ERAS-2025-002 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 21.7111 | 22.0844 | 0.3733
ERAS-2025-002 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 21.7047 | 22.0634 | 0.3587
ERAS-2025-002 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7173 | 2.7174 | 0.0001
ERAS-2025-002 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.8629 | 3.8632 | 0.0003
ERAS-2025-002 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.344 | 13.3594 | 0.0154
ERAS-2025-002 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.4003 | 19.5398 | 0.1395
ERAS-2025-002 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.3452 | 8.3822 | 0.037
ERAS-2025-002 | 05 SOUTHWEST | 526108 | SP-ERSKINE+3 | 115 | 12.4421 | 12.446 | 0.0039
ERAS-2025-002 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 12.4215 | 12.4254 | 0.0039
ERAS-2025-002 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.7317 | 2.7318 | 0.0001
ERAS-2025-002 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.8259 | 14.8312 | 0.0053
ERAS-2025-002 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.5518 | 11.5594 | 0.0076
ERAS-2025-002 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.8832 | 12.8871 | 0.0039
ERAS-2025-002 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.615 | 11.618 | 0.003
ERAS-2025-002 | 05 SOUTHWEST | 526241 | SP-LEPRINO 3 | 115 | 13.2151 | 13.2185 | 0.0034
ERAS-2025-002 | 05 SOUTHWEST | 526242 | SP-LPRNO_TP3 | 115 | 14.2644 | 14.2684 | 0.004
ERAS-2025-002 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.4044 | 19.4105 | 0.0061
ERAS-2025-002 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.7995 | 16.808 | 0.0085
ERAS-2025-002 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.7913 | 15.7959 | 0.0046
ERAS-2025-002 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.3184 | 12.3228 | 0.0044
ERAS-2025-002 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.9411 | 18.9511 | 0.01
ERAS-2025-002 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0336 | 12.037 | 0.0034
ERAS-2025-002 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5956 | 10.5982 | 0.0026
ERAS-2025-002 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.8589 | 12.8621 | 0.0032
ERAS-2025-002 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8422 | 13.8496 | 0.0074
ERAS-2025-002 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.4098 | 7.4106 | 0.0008
ERAS-2025-002 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6079 | 6.6091 | 0.0012
ERAS-2025-002 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1722 | 5.1729 | 0.0007
ERAS-2025-002 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6561 | 19.6594 | 0.0033
ERAS-2025-002 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.0487 | 21.058 | 0.0093
ERAS-2025-002 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.1721 | 11.1838 | 0.0117
ERAS-2025-002 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6932 | 16.6979 | 0.0047
ERAS-2025-002 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.353 | 12.3553 | 0.0023
ERAS-2025-002 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.6604 | 17.6642 | 0.0038
ERAS-2025-002 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8945 | 17.9042 | 0.0097
ERAS-2025-002 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9481 | 7.9551 | 0.007
ERAS-2025-002 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.9586 | 20.972 | 0.0134
ERAS-2025-002 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9366 | 7.9519 | 0.0153
ERAS-2025-002 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.2287 | 17.26 | 0.0313
ERAS-2025-002 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
ERAS-2025-002 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.6917 | 10.6924 | 0.0007
ERAS-2025-002 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.138 | 8.1385 | 0.0005
ERAS-2025-002 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.6339 | 14.6359 | 0.002
ERAS-2025-002 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.0826 | 7.1112 | 0.0286
ERAS-2025-002 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.8926 | 5.9027 | 0.0101
ERAS-2025-002 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.61 | 11.6126 | 0.0026
ERAS-2025-002 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.5443 | 9.5449 | 0.0006
ERAS-2025-002 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.3958 | 10.4059 | 0.0101
ERAS-2025-002 | 05 SOUTHWEST | 788703 | ERA-02 | 345 | 21.3454 | 21.7204 | 0.375
ERAS-2025-002 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0733 | 33.0847 | 0.0114
ERAS-2025-002 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 16.8197 | 16.8295 | 0.0098
ERAS-2025-002 | 05 SOUTHWEST | 788810 | ERA-21 | 345 | 11.6616 | 11.7471 | 0.0855
ERAS-2025-002 | 05 SOUTHWEST | 788817 | ERA-21-MPT1 | 345 | 10.1906 | 10.2549 | 0.0643
ERAS-2025-002 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.8926 | 16.9025 | 0.0099
ERAS-2025-002 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.452 | 13.5691 | 0.1171
ERAS-2025-002 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9446 | 8.9668 | 0.0222
ERAS-2025-002 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.9389 | 8.9611 | 0.0222
ERAS-2025-002 | 05 SOUTHWEST | 789905 | ERAS-36-TAP | 230 | 10.5255 | 10.5266 | 0.0011
ERAS-2025-014 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 15.3476 | 15.3487 | 0.0011
ERAS-2025-014 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 28.5026 | 28.515 | 0.0124
ERAS-2025-014 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3148 | 17.334 | 0.0192
ERAS-2025-014 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 7.6492 | 7.6581 | 0.0089
ERAS-2025-014 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.8814 | 5.8835 | 0.0021
ERAS-2025-014 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6911 | 10.6924 | 0.0013
ERAS-2025-014 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4823 | 25.4894 | 0.0071
ERAS-2025-014 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7638 | 33.7794 | 0.0156
ERAS-2025-014 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.6033 | 14.6161 | 0.0128
ERAS-2025-014 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5959 | 11.5984 | 0.0025
ERAS-2025-014 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.004 | 6.0045 | 0.0005
ERAS-2025-014 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.0269 | 28.977 | -0.0499
ERAS-2025-014 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.4037 | 22.4092 | 0.0055
ERAS-2025-014 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.3703 | 8.3822 | 0.0119
ERAS-2025-014 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5961 | 10.5982 | 0.0021
ERAS-2025-014 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6501 | 19.6594 | 0.0093
ERAS-2025-014 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.031 | 21.058 | 0.027
ERAS-2025-014 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.1563 | 11.1838 | 0.0275
ERAS-2025-014 | 05 SOUTHWEST | 527000 | ERAS-014 | 345 | 11.6352 | 12.1878 | 0.5526
ERAS-2025-014 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6839 | 16.6979 | 0.014
ERAS-2025-014 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 12.9704 | 13.4726 | 0.5022
ERAS-2025-014 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2854 | 13.292 | 0.0066
ERAS-2025-014 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.3404 | 12.3553 | 0.0149
ERAS-2025-014 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.723 | 12.7282 | 0.0052
ERAS-2025-014 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.6518 | 17.6642 | 0.0124
ERAS-2025-014 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 11.0984 | 11.1033 | 0.0049
ERAS-2025-014 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 14.5938 | 14.6393 | 0.0455
ERAS-2025-014 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 14.5938 | 14.6393 | 0.0455
ERAS-2025-014 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.5938 | 14.6393 | 0.0455
ERAS-2025-014 | 05 SOUTHWEST | 527640 | MILO_WIND 7 | 345 | 14.2773 | 14.3216 | 0.0443
ERAS-2025-014 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 11.7791 | 11.8082 | 0.0291
ERAS-2025-014 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.2773 | 14.3216 | 0.0443
ERAS-2025-014 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8325 | 17.9042 | 0.0717
ERAS-2025-014 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 11.7791 | 11.8082 | 0.0291
ERAS-2025-014 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 11.7791 | 11.8082 | 0.0291
ERAS-2025-014 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9328 | 7.9551 | 0.0223
ERAS-2025-014 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 13.9694 | 13.9753 | 0.0059
ERAS-2025-014 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 13.9694 | 13.9753 | 0.0059
ERAS-2025-014 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 11.989 | 11.9931 | 0.0041
ERAS-2025-014 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.6329 | 9.6583 | 0.0254
ERAS-2025-014 | 05 SOUTHWEST | 527845 | C1_MPT_PRI 3 | 115 | 11.0182 | 11.0268 | 0.0086
ERAS-2025-014 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 33.3795 | 33.4572 | 0.0777
ERAS-2025-014 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 22.3937 | 22.4838 | 0.0901
ERAS-2025-014 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 22.3937 | 22.4838 | 0.0901
ERAS-2025-014 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 37.2744 | 37.3663 | 0.0919
ERAS-2025-014 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 25.8475 | 25.9982 | 0.1507
ERAS-2025-014 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.6122 | 20.972 | 0.3598
ERAS-2025-014 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 22.3448 | 22.4009 | 0.0561
ERAS-2025-014 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 9.2999 | 9.3131 | 0.0132
ERAS-2025-014 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 14.0352 | 14.1206 | 0.0854
ERAS-2025-014 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 22.4487 | 22.5054 | 0.0567
ERAS-2025-014 | 05 SOUTHWEST | 527972 | MIDSPRON_TP3 | 115 | 21.1961 | 21.2674 | 0.0713
ERAS-2025-014 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 33.7685 | 33.8529 | 0.0844
ERAS-2025-014 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9234 | 7.9519 | 0.0285
ERAS-2025-014 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.1959 | 17.26 | 0.0641
ERAS-2025-014 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 15.7509 | 15.7803 | 0.0294
ERAS-2025-014 | 05 SOUTHWEST | 528020 | BOPCO_PKRLK3 | 115 | 32.3845 | 32.4637 | 0.0792
ERAS-2025-014 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 37.5718 | 37.8262 | 0.2544
ERAS-2025-014 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 37.5718 | 37.8262 | 0.2544
ERAS-2025-014 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 14.8564 | 14.9797 | 0.1233
ERAS-2025-014 | 05 SOUTHWEST | 528033 | CPERHEAD_HV3 | 115 | 15.4948 | 15.53 | 0.0352
ERAS-2025-014 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 17.0306 | 17.0595 | 0.0289
ERAS-2025-014 | 05 SOUTHWEST | 528052 | TIPTOP-SOLAR | 115 | 30.7582 | 30.9301 | 0.1719
ERAS-2025-014 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 7.6673 | 7.6728 | 0.0055
ERAS-2025-014 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 19.7037 | 19.7366 | 0.0329
ERAS-2025-014 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 11.2962 | 11.3389 | 0.0427
ERAS-2025-014 | 05 SOUTHWEST | 528194 | MALAGABEND 3 | 115 | 10.298 | 10.3063 | 0.0083
ERAS-2025-014 | 05 SOUTHWEST | 528222 | CHINA_DRAW 3 | 115 | 18.0997 | 18.1257 | 0.026
ERAS-2025-014 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 11.9446 | 11.9835 | 0.0389
ERAS-2025-014 | 05 SOUTHWEST | 528228 | WOOD_DRAW 3 | 115 | 12.5898 | 12.6019 | 0.0121
ERAS-2025-014 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 28.8332 | 28.983 | 0.1498
ERAS-2025-014 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 25.4299 | 25.5455 | 0.1156
ERAS-2025-014 | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 25.5245 | 25.6419 | 0.1174
ERAS-2025-014 | 05 SOUTHWEST | 528235 | WOLFCAMP_TP3 | 115 | 28.3652 | 28.4311 | 0.0659
ERAS-2025-014 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 11.5938 | 11.6172 | 0.0234
ERAS-2025-014 | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 9.2351 | 9.2489 | 0.0138
ERAS-2025-014 | 05 SOUTHWEST | 528317 | ENRON_TP 3 | 115 | 31.1025 | 31.2555 | 0.153
ERAS-2025-014 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.3879 | 9.3913 | 0.0034
ERAS-2025-014 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.7862 | 9.7903 | 0.0041
ERAS-2025-014 | 05 SOUTHWEST | 528334 | LE-NRTH_INT3 | 115 | 9.7215 | 9.7255 | 0.004
ERAS-2025-014 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 9.1531 | 9.1585 | 0.0054
ERAS-2025-014 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 31.8849 | 31.9549 | 0.07
ERAS-2025-014 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 31.8849 | 31.9549 | 0.07
ERAS-2025-014 | 05 SOUTHWEST | 528390 | LYNCH_TP 3 | 115 | 11.3608 | 11.377 | 0.0162
ERAS-2025-014 | 05 SOUTHWEST | 528392 | PEARLE 3 | 115 | 10.2393 | 10.2505 | 0.0112
ERAS-2025-014 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 16.5403 | 16.5769 | 0.0366
ERAS-2025-014 | 05 SOUTHWEST | 528396 | XTO_BULLDOG3 | 115 | 12.3563 | 12.3744 | 0.0181
ERAS-2025-014 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 32.8026 | 32.9729 | 0.1703
ERAS-2025-014 | 05 SOUTHWEST | 528400 | LEANTL_345 | 345 | 12.9168 | 12.9985 | 0.0817
ERAS-2025-014 | 05 SOUTHWEST | 528422 | DCP_ZIA TP 3 | 115 | 12.7552 | 12.7769 | 0.0217
ERAS-2025-014 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.6276 | 8.6315 | 0.0039
ERAS-2025-014 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.9011 | 12.9128 | 0.0117
ERAS-2025-014 | 05 SOUTHWEST | 528435 | MILLEN 3 | 115 | 12.9011 | 12.9128 | 0.0117
ERAS-2025-014 | 05 SOUTHWEST | 528436 | MILLEN_TPE 3 | 115 | 12.9011 | 12.9128 | 0.0117
ERAS-2025-014 | 05 SOUTHWEST | 528491 | MONUMENT 3 | 115 | 17.5052 | 17.5319 | 0.0267
ERAS-2025-014 | 05 SOUTHWEST | 528533 | DRINKARD_TP3 | 115 | 8.8841 | 8.9117 | 0.0276
ERAS-2025-014 | 05 SOUTHWEST | 528540 | WHITTEN 3 | 115 | 10.3347 | 10.3535 | 0.0188
ERAS-2025-014 | 05 SOUTHWEST | 528542 | ZIAHILS13 3 | 115 | 8.1999 | 8.2066 | 0.0067
ERAS-2025-014 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 11.3213 | 11.332 | 0.0107
ERAS-2025-014 | 05 SOUTHWEST | 528589 | DRINKARD 3 | 115 | 9.2948 | 9.3294 | 0.0346
ERAS-2025-014 | 05 SOUTHWEST | 528596 | CARDINAL 3 | 115 | 10.0809 | 10.1225 | 0.0416
ERAS-2025-014 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 15.1806 | 15.3321 | 0.1515
ERAS-2025-014 | 05 SOUTHWEST | 528603 | NA_ENRICH 3 | 115 | 14.1868 | 14.3039 | 0.1171
ERAS-2025-014 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 9.2932 | 9.5272 | 0.234
ERAS-2025-014 | 05 SOUTHWEST | 528605 | TARGA_CLARK3 | 115 | 10.7933 | 10.8478 | 0.0545
ERAS-2025-014 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 11.989 | 11.9931 | 0.0041
ERAS-2025-014 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.6333 | 14.6359 | 0.0026
ERAS-2025-014 | 05 SOUTHWEST | 762442 | G18-004-TAP | 115 | 27.034 | 27.0842 | 0.0502
ERAS-2025-014 | 05 SOUTHWEST | 762866 | GEN-2018-052 | 115 | 35.9921 | 36.2257 | 0.2336
ERAS-2025-014 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.3822 | 10.4059 | 0.0237
ERAS-2025-014 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0698 | 33.0847 | 0.0149
ERAS-2025-014 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 16.633 | 16.8295 | 0.1965
ERAS-2025-014 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.7041 | 16.9025 | 0.1984
ERAS-2025-014 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9586 | 8.9668 | 0.0082
ERAS-2025-014 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.953 | 8.9611 | 0.0081
ERAS-2025-014 | 05 SOUTHWEST | 789915 | ERA-030-TAP | 230 | 6.508 | 6.5088 | 0.0008
ERAS-2025-016 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 7.631 | 7.6304 | -0.0006
ERAS-2025-016 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 7.6 | 7.5994 | -0.0006
ERAS-2025-016 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.631 | 7.6304 | -0.0006
ERAS-2025-016 | 05 SOUTHWEST | 511607 | O.K.U.3-7 | 345 | 7.631 | 7.6304 | -0.0006
ERAS-2025-016 | 05 SOUTHWEST | 511999 | DVRSION-WIND | 345 | 4.9615 | 4.9613 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 515378 | WWRDEHV9 | 765 | 5.3667 | 5.3665 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 9.0002 | 8.9961 | -0.0041
ERAS-2025-016 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 14.8846 | 14.8848 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.4518 | 12.452 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 515634 | PALDR1W7 | 345 | 11.1043 | 11.1044 | 0.0001
ERAS-2025-016 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 14.2205 | 14.2206 | 0.0001
ERAS-2025-016 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 11.6261 | 11.6175 | -0.0086
ERAS-2025-016 | 05 SOUTHWEST | 523019 | OSLO-SYLVIE7 | 345 | 10.6227 | 10.6229 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 523020 | SYLVIE 7 | 345 | 10.6227 | 10.6229 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 523030 | OLSO 7 | 345 | 10.6227 | 10.6229 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 523040 | OLYMPIA7 | 345 | 15.0402 | 15.0407 | 0.0005
ERAS-2025-016 | 05 SOUTHWEST | 523041 | FRWLN7 | 345 | 12.1385 | 12.1388 | 0.0003
ERAS-2025-016 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 16.7611 | 16.7582 | -0.0029
ERAS-2025-016 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 15.5761 | 15.5755 | -0.0006
ERAS-2025-016 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 15.3482 | 15.3487 | 0.0005
ERAS-2025-016 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 12.2416 | 12.2417 | 0.0001
ERAS-2025-016 | 05 SOUTHWEST | 523131 | GRPLNS-HV2-3 | 115 | 11.4535 | 11.4536 | 0.0001
ERAS-2025-016 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.6608 | 4.6603 | -0.0005
ERAS-2025-016 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 6.1585 | 6.1589 | 0.0004
ERAS-2025-016 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.5818 | 4.582 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 9.2612 | 9.2621 | 0.0009
ERAS-2025-016 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 10.4273 | 10.4281 | 0.0008
ERAS-2025-016 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 10.5357 | 10.5379 | 0.0022
ERAS-2025-016 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.9086 | 7.9092 | 0.0006
ERAS-2025-016 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 6.3299 | 6.3272 | -0.0027
ERAS-2025-016 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.8209 | 6.8209 | 0
ERAS-2025-016 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 10.6681 | 10.6681 | 0
ERAS-2025-016 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 5.7875 | 5.7881 | 0.0006
ERAS-2025-016 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 28.4913 | 28.515 | 0.0237
ERAS-2025-016 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3126 | 17.334 | 0.0214
ERAS-2025-016 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 7.6489 | 7.6581 | 0.0092
ERAS-2025-016 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 31.3023 | 31.3157 | 0.0134
ERAS-2025-016 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 31.3023 | 31.3157 | 0.0134
ERAS-2025-016 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 31.3023 | 31.3157 | 0.0134
ERAS-2025-016 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 20.7731 | 20.7765 | 0.0034
ERAS-2025-016 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 23.7112 | 23.7222 | 0.011
ERAS-2025-016 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 33.1695 | 33.1751 | 0.0056
ERAS-2025-016 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 30.0511 | 30.063 | 0.0119
ERAS-2025-016 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 11.1147 | 11.117 | 0.0023
ERAS-2025-016 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.8985 | 10.9048 | 0.0063
ERAS-2025-016 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 7.2978 | 7.3005 | 0.0027
ERAS-2025-016 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.8812 | 5.8835 | 0.0023
ERAS-2025-016 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.8812 | 5.8835 | 0.0023
ERAS-2025-016 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 22.8039 | 22.8095 | 0.0056
ERAS-2025-016 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.2051 | 16.2097 | 0.0046
ERAS-2025-016 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 16.5063 | 16.5092 | 0.0029
ERAS-2025-016 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 14.5001 | 14.5021 | 0.002
ERAS-2025-016 | 05 SOUTHWEST | 524405 | OWENSCORN_E3 | 115 | 15.9735 | 15.9761 | 0.0026
ERAS-2025-016 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.8396 | 17.8428 | 0.0032
ERAS-2025-016 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 15.1691 | 15.1733 | 0.0042
ERAS-2025-016 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.7917 | 2.7919 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 3.1401 | 3.1405 | 0.0004
ERAS-2025-016 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.5585 | 2.5587 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.776 | 6.7764 | 0.0004
ERAS-2025-016 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 12.2291 | 12.2397 | 0.0106
ERAS-2025-016 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 12.2338 | 12.2444 | 0.0106
ERAS-2025-016 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.4422 | 8.453 | 0.0108
ERAS-2025-016 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.5614 | 12.5726 | 0.0112
ERAS-2025-016 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 4.6361 | 4.6388 | 0.0027
ERAS-2025-016 | 05 SOUTHWEST | 524668 | DS-#20 +3 | 115 | 5.5501 | 5.5544 | 0.0043
ERAS-2025-016 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 5.5417 | 5.546 | 0.0043
ERAS-2025-016 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 11.8093 | 11.8164 | 0.0071
ERAS-2025-016 | 05 SOUTHWEST | 524748 | DS-#26 3 | 115 | 10.5423 | 10.5485 | 0.0062
ERAS-2025-016 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4487 | 11.4701 | 0.0214
ERAS-2025-016 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5746 | 10.5925 | 0.0179
ERAS-2025-016 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 7.1232 | 7.1406 | 0.0174
ERAS-2025-016 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 9.1005 | 9.1139 | 0.0134
ERAS-2025-016 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.5603 | 7.5694 | 0.0091
ERAS-2025-016 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.8435 | 6.851 | 0.0075
ERAS-2025-016 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.627 | 2.6276 | 0.0006
ERAS-2025-016 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.1628 | 6.169 | 0.0062
ERAS-2025-016 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.7412 | 6.7487 | 0.0075
ERAS-2025-016 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4775 | 10.4954 | 0.0179
ERAS-2025-016 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 7.008 | 7.0159 | 0.0079
ERAS-2025-016 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.6273 | 4.6292 | 0.0019
ERAS-2025-016 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4793 | 11.5008 | 0.0215
ERAS-2025-016 | 05 SOUTHWEST | 524830 | FE-HOLLAND+3 | 115 | 9.3554 | 9.3695 | 0.0141
ERAS-2025-016 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.3302 | 9.3443 | 0.0141
ERAS-2025-016 | 05 SOUTHWEST | 524837 | FE-CLOVIS2+3 | 115 | 10.3945 | 10.4121 | 0.0176
ERAS-2025-016 | 05 SOUTHWEST | 524838 | FE-CLOVIS2 3 | 115 | 10.8601 | 10.8793 | 0.0192
ERAS-2025-016 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.2312 | 2.2317 | 0.0005
ERAS-2025-016 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.2257 | 8.2369 | 0.0112
ERAS-2025-016 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.2961 | 10.314 | 0.0179
ERAS-2025-016 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.9184 | 8.9439 | 0.0255
ERAS-2025-016 | 05 SOUTHWEST | 524885 | SN_JUAN_SS 6 | 230 | 4.5659 | 4.5686 | 0.0027
ERAS-2025-016 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.2754 | 4.2777 | 0.0023
ERAS-2025-016 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.319 | 11.3421 | 0.0231
ERAS-2025-016 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6477 | 10.6924 | 0.0447
ERAS-2025-016 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.3264 | 7.332 | 0.0056
ERAS-2025-016 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.8707 | 7.8813 | 0.0106
ERAS-2025-016 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.3264 | 7.332 | 0.0056
ERAS-2025-016 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.4595 | 5.4627 | 0.0032
ERAS-2025-016 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.4329 | 6.44 | 0.0071
ERAS-2025-016 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7008 | 5.7042 | 0.0034
ERAS-2025-016 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 6.041 | 6.0472 | 0.0062
ERAS-2025-016 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.9503 | 5.9564 | 0.0061
ERAS-2025-016 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.1453 | 5.149 | 0.0037
ERAS-2025-016 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4769 | 5.4812 | 0.0043
ERAS-2025-016 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 4.9126 | 4.9147 | 0.0021
ERAS-2025-016 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.3694 | 5.3735 | 0.0041
ERAS-2025-016 | 05 SOUTHWEST | 525049 | BC-EARTH +3 | 115 | 8.5416 | 8.5485 | 0.0069
ERAS-2025-016 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 8.3038 | 8.3094 | 0.0056
ERAS-2025-016 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.5333 | 8.5402 | 0.0069
ERAS-2025-016 | 05 SOUTHWEST | 525082 | BC-ERTH_INT2 | 69 | 4.0186 | 4.0195 | 0.0009
ERAS-2025-016 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.795 | 7.7987 | 0.0037
ERAS-2025-016 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.8201 | 6.8212 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.5006 | 4.5009 | 0.0003
ERAS-2025-016 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.4114 | 12.416 | 0.0046
ERAS-2025-016 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.7756 | 11.7795 | 0.0039
ERAS-2025-016 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2182 | 11.2233 | 0.0051
ERAS-2025-016 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.8281 | 6.8293 | 0.0012
ERAS-2025-016 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.7113 | 5.712 | 0.0007
ERAS-2025-016 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 4.2919 | 4.2922 | 0.0003
ERAS-2025-016 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 3.0006 | 3.0008 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.15 | 3.1501 | 0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.9007 | 6.9015 | 0.0008
ERAS-2025-016 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 4.8742 | 4.8753 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.9703 | 7.9748 | 0.0045
ERAS-2025-016 | 05 SOUTHWEST | 525432 | SP-HLFWAYTP2 | 69 | 5.9401 | 5.9408 | 0.0007
ERAS-2025-016 | 05 SOUTHWEST | 525439 | LC-S_OLTON 3 | 115 | 6.1921 | 6.1955 | 0.0034
ERAS-2025-016 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.3894 | 7.3943 | 0.0049
ERAS-2025-016 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9487 | 6.9496 | 0.0009
ERAS-2025-016 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.8428 | 10.8468 | 0.004
ERAS-2025-016 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.185 | 15.198 | 0.013
ERAS-2025-016 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.9488 | 11.965 | 0.0162
ERAS-2025-016 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.9409 | 15.9758 | 0.0349
ERAS-2025-016 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.1941 | 25.4894 | 0.2953
ERAS-2025-016 | 05 SOUTHWEST | 525516 | XS1_MPT1PRI3 | 115 | 14.9302 | 14.9609 | 0.0307
ERAS-2025-016 | 05 SOUTHWEST | 525521 | EASTER_WND 6 | 230 | 8.1156 | 8.129 | 0.0134
ERAS-2025-016 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 32.9577 | 33.7794 | 0.8217
ERAS-2025-016 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.4889 | 14.6161 | 0.1272
ERAS-2025-016 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.4521 | 11.5246 | 0.0725
ERAS-2025-016 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.525 | 11.5984 | 0.0734
ERAS-2025-016 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.525 | 11.5984 | 0.0734
ERAS-2025-016 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.5121 | 2.5128 | 0.0007
ERAS-2025-016 | 05 SOUTHWEST | 525612 | W_LITTLFLD+2 | 69 | 3.1426 | 3.1437 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 3.0442 | 3.0452 | 0.001
ERAS-2025-016 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.3039 | 4.3062 | 0.0023
ERAS-2025-016 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 6.0462 | 6.0504 | 0.0042
ERAS-2025-016 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.7594 | 8.7749 | 0.0155
ERAS-2025-016 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.986 | 6.0045 | 0.0185
ERAS-2025-016 | 05 SOUTHWEST | 525649 | LC-LTTLFLD 2 | 69 | 4.7803 | 4.783 | 0.0027
ERAS-2025-016 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.0978 | 5.1009 | 0.0031
ERAS-2025-016 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.2716 | 4.2737 | 0.0021
ERAS-2025-016 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.7722 | 4.7749 | 0.0027
ERAS-2025-016 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.601 | 3.6026 | 0.0016
ERAS-2025-016 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2462 | 2.2461 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525731 | SP-ABERNTH+2 | 69 | 3.0538 | 3.0536 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525732 | SP-ABERNTHY2 | 69 | 3.052 | 3.0518 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.6295 | 2.6294 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525745 | LH-HALECTR+2 | 69 | 1.5681 | 1.5681 | 0
ERAS-2025-016 | 05 SOUTHWEST | 525750 | G18-015-TAP | 345 | 5.9154 | 5.9147 | -0.0007
ERAS-2025-016 | 05 SOUTHWEST | 525762 | IRICK 2 | 69 | 2.7826 | 2.7825 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.1954 | 6.1954 | 0
ERAS-2025-016 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4952 | 5.4951 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0931 | 7.0928 | -0.0003
ERAS-2025-016 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.711 | 2.711 | 0
ERAS-2025-016 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 6.1439 | 6.1437 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 6.1449 | 6.1447 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.4185 | 4.4184 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.5238 | 4.5234 | -0.0004
ERAS-2025-016 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9514 | 7.9502 | -0.0012
ERAS-2025-016 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.7671 | 21.7514 | -0.0157
ERAS-2025-016 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.0876 | 28.977 | -0.1106
ERAS-2025-016 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 29.0876 | 28.977 | -0.1106
ERAS-2025-016 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.4331 | 22.4092 | -0.0239
ERAS-2025-016 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.2596 | 10.2557 | -0.0039
ERAS-2025-016 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.7826 | 28.6746 | -0.108
ERAS-2025-016 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 22.1075 | 22.0844 | -0.0231
ERAS-2025-016 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 22.0865 | 22.0634 | -0.0231
ERAS-2025-016 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7176 | 2.7174 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525854 | LH-WILSON 2 | 69 | 2.1143 | 2.1142 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525860 | SP-BECTONTP2 | 69 | 2.4189 | 2.4188 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.8635 | 3.8632 | -0.0003
ERAS-2025-016 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 3.1784 | 3.1782 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.4733 | 5.4731 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.3772 | 13.3594 | -0.0178
ERAS-2025-016 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.5466 | 19.5398 | -0.0068
ERAS-2025-016 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.3833 | 8.3822 | -0.0011
ERAS-2025-016 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.418 | 4.4191 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.2658 | 5.2674 | 0.0016
ERAS-2025-016 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.9032 | 5.9065 | 0.0033
ERAS-2025-016 | 05 SOUTHWEST | 526035 | LC-OPDYKE +3 | 115 | 6.2541 | 6.2572 | 0.0031
ERAS-2025-016 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 6.2448 | 6.248 | 0.0032
ERAS-2025-016 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.3895 | 2.3899 | 0.0004
ERAS-2025-016 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.43 | 4.4311 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 526108 | SP-ERSKINE+3 | 115 | 12.4481 | 12.446 | -0.0021
ERAS-2025-016 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 12.4275 | 12.4254 | -0.0021
ERAS-2025-016 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.2381 | 2.238 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.7319 | 2.7318 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.8339 | 14.8312 | -0.0027
ERAS-2025-016 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.564 | 11.5594 | -0.0046
ERAS-2025-016 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.8887 | 12.8871 | -0.0016
ERAS-2025-016 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 9.8728 | 9.8718 | -0.001
ERAS-2025-016 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.2931 | 2.293 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.6195 | 11.618 | -0.0015
ERAS-2025-016 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 10.8825 | 10.8811 | -0.0014
ERAS-2025-016 | 05 SOUTHWEST | 526241 | SP-LEPRINO 3 | 115 | 13.2208 | 13.2185 | -0.0023
ERAS-2025-016 | 05 SOUTHWEST | 526242 | SP-LPRNO_TP3 | 115 | 14.2711 | 14.2684 | -0.0027
ERAS-2025-016 | 05 SOUTHWEST | 526243 | SP-QUAKER 3 | 115 | 10.6561 | 10.6549 | -0.0012
ERAS-2025-016 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.4732 | 4.4731 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.4143 | 19.4105 | -0.0038
ERAS-2025-016 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.813 | 16.808 | -0.005
ERAS-2025-016 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8759 | 7.8754 | -0.0005
ERAS-2025-016 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.799 | 15.7959 | -0.0031
ERAS-2025-016 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.3258 | 12.3228 | -0.003
ERAS-2025-016 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.9578 | 18.9511 | -0.0067
ERAS-2025-016 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 7.4214 | 7.423 | 0.0016
ERAS-2025-016 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 10.4717 | 10.4757 | 0.004
ERAS-2025-016 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 12.4737 | 12.4798 | 0.0061
ERAS-2025-016 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0255 | 12.037 | 0.0115
ERAS-2025-016 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 11.5698 | 11.5749 | 0.0051
ERAS-2025-016 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 7.026 | 7.0279 | 0.0019
ERAS-2025-016 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5902 | 10.5982 | 0.008
ERAS-2025-016 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 12.0862 | 12.0851 | -0.0011
ERAS-2025-016 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 12.3016 | 12.3003 | -0.0013
ERAS-2025-016 | 05 SOUTHWEST | 526485 | LG-LEVELND+3 | 115 | 10.2379 | 10.2416 | 0.0037
ERAS-2025-016 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.8625 | 12.8621 | -0.0004
ERAS-2025-016 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8504 | 13.8496 | -0.0008
ERAS-2025-016 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.9052 | 9.9042 | -0.001
ERAS-2025-016 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 6.4018 | 6.4015 | -0.0003
ERAS-2025-016 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.4111 | 7.4106 | -0.0005
ERAS-2025-016 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6099 | 6.6091 | -0.0008
ERAS-2025-016 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1734 | 5.1729 | -0.0005
ERAS-2025-016 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 3.0491 | 3.049 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1619 | 11.1636 | 0.0017
ERAS-2025-016 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 16.0355 | 16.0403 | 0.0048
ERAS-2025-016 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3785 | 6.3791 | 0.0006
ERAS-2025-016 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.6973 | 10.6988 | 0.0015
ERAS-2025-016 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6545 | 19.6594 | 0.0049
ERAS-2025-016 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.0451 | 21.058 | 0.0129
ERAS-2025-016 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.181 | 11.1838 | 0.0028
ERAS-2025-016 | 05 SOUTHWEST | 526943 | LG-PLAINS +3 | 115 | 8.5098 | 8.5108 | 0.001
ERAS-2025-016 | 05 SOUTHWEST | 527000 | ERAS-014 | 345 | 12.186 | 12.1878 | 0.0018
ERAS-2025-016 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6914 | 16.6979 | 0.0065
ERAS-2025-016 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 16.5331 | 16.5394 | 0.0063
ERAS-2025-016 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 16.3989 | 16.4047 | 0.0058
ERAS-2025-016 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.5927 | 14.5944 | 0.0017
ERAS-2025-016 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 13.4702 | 13.4726 | 0.0024
ERAS-2025-016 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2908 | 13.292 | 0.0012
ERAS-2025-016 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.3526 | 12.3553 | 0.0027
ERAS-2025-016 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.7272 | 12.7282 | 0.001
ERAS-2025-016 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.4874 | 14.4892 | 0.0018
ERAS-2025-016 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.5459 | 11.547 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 17.6689 | 17.6712 | 0.0023
ERAS-2025-016 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 23.6158 | 23.6193 | 0.0035
ERAS-2025-016 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 23.6158 | 23.6193 | 0.0035
ERAS-2025-016 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.2104 | 25.2143 | 0.0039
ERAS-2025-016 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.6589 | 17.6642 | 0.0053
ERAS-2025-016 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.6589 | 17.6642 | 0.0053
ERAS-2025-016 | 05 SOUTHWEST | 527193 | LG-PLSHILL+3 | 115 | 8.3699 | 8.3706 | 0.0007
ERAS-2025-016 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3538 | 8.3545 | 0.0007
ERAS-2025-016 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.6538 | 9.6546 | 0.0008
ERAS-2025-016 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.8549 | 14.8564 | 0.0015
ERAS-2025-016 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.8052 | 8.8063 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.7073 | 7.7061 | -0.0012
ERAS-2025-016 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 5.5414 | 5.5405 | -0.0009
ERAS-2025-016 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 14.618 | 14.6393 | 0.0213
ERAS-2025-016 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 14.618 | 14.6393 | 0.0213
ERAS-2025-016 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.618 | 14.6393 | 0.0213
ERAS-2025-016 | 05 SOUTHWEST | 527640 | MILO_WIND 7 | 345 | 14.2985 | 14.3216 | 0.0231
ERAS-2025-016 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 11.7909 | 11.8082 | 0.0173
ERAS-2025-016 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.2985 | 14.3216 | 0.0231
ERAS-2025-016 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8705 | 17.9042 | 0.0337
ERAS-2025-016 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 11.7909 | 11.8082 | 0.0173
ERAS-2025-016 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 11.7909 | 11.8082 | 0.0173
ERAS-2025-016 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9458 | 7.9551 | 0.0093
ERAS-2025-016 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 13.9924 | 13.9753 | -0.0171
ERAS-2025-016 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 13.9924 | 13.9753 | -0.0171
ERAS-2025-016 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 12.0276 | 11.9931 | -0.0345
ERAS-2025-016 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.6653 | 9.6583 | -0.007
ERAS-2025-016 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 22.4859 | 22.4838 | -0.0021
ERAS-2025-016 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 22.4859 | 22.4838 | -0.0021
ERAS-2025-016 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 37.3649 | 37.3663 | 0.0014
ERAS-2025-016 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 25.9969 | 25.9982 | 0.0013
ERAS-2025-016 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.964 | 20.972 | 0.008
ERAS-2025-016 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 14.1218 | 14.1206 | -0.0012
ERAS-2025-016 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 22.5093 | 22.5054 | -0.0039
ERAS-2025-016 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9485 | 7.9519 | 0.0034
ERAS-2025-016 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.2531 | 17.26 | 0.0069
ERAS-2025-016 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 37.8197 | 37.8262 | 0.0065
ERAS-2025-016 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 14.9766 | 14.9797 | 0.0031
ERAS-2025-016 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 7.6805 | 7.6728 | -0.0077
ERAS-2025-016 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 11.3381 | 11.3389 | 0.0008
ERAS-2025-016 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.3908 | 9.3913 | 0.0005
ERAS-2025-016 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 32.9733 | 32.9729 | -0.0004
ERAS-2025-016 | 05 SOUTHWEST | 528400 | LEANTL_345 | 345 | 12.9986 | 12.9985 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 9.5261 | 9.5272 | 0.0011
ERAS-2025-016 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 6.0309 | 6.0311 | 0.0002
ERAS-2025-016 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.8146 | 6.8146 | 0
ERAS-2025-016 | 05 SOUTHWEST | 599950 | LAMAR7 | 345 | 2.4563 | 2.4563 | 0
ERAS-2025-016 | 05 SOUTHWEST | 599951 | LAMAR 6 | 345 | 60.6375 | 60.6375 | 0
ERAS-2025-016 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.6477 | 10.6924 | 0.0447
ERAS-2025-016 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 12.0276 | 11.9931 | -0.0345
ERAS-2025-016 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.1251 | 8.1385 | 0.0134
ERAS-2025-016 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 14.7066 | 14.7112 | 0.0046
ERAS-2025-016 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.4986 | 14.6359 | 0.1373
ERAS-2025-016 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.113 | 7.1112 | -0.0018
ERAS-2025-016 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.9033 | 5.9027 | -0.0006
ERAS-2025-016 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.5974 | 11.6126 | 0.0152
ERAS-2025-016 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.5096 | 9.5449 | 0.0353
ERAS-2025-016 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.4035 | 10.4059 | 0.0024
ERAS-2025-016 | 05 SOUTHWEST | 764980 | GEN-2020-008 | 345 | 6.8209 | 6.8209 | 0
ERAS-2025-016 | 05 SOUTHWEST | 788703 | ERA-02 | 345 | 21.7428 | 21.7204 | -0.0224
ERAS-2025-016 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 32.2622 | 33.0847 | 0.8225
ERAS-2025-016 | 05 SOUTHWEST | 788772 | ERA-18 | 230 | 8.0051 | 8.0249 | 0.0198
ERAS-2025-016 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 16.8244 | 16.8295 | 0.0051
ERAS-2025-016 | 05 SOUTHWEST | 788810 | ERA-21 | 345 | 11.7526 | 11.7471 | -0.0055
ERAS-2025-016 | 05 SOUTHWEST | 788817 | ERA-21-MPT1 | 345 | 10.2591 | 10.2549 | -0.0042
ERAS-2025-016 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.8973 | 16.9025 | 0.0052
ERAS-2025-016 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.5768 | 13.5691 | -0.0077
ERAS-2025-016 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9669 | 8.9668 | -0.0001
ERAS-2025-016 | 05 SOUTHWEST | 788945 | ERA-2025-27 | 230 | 15.2082 | 15.2131 | 0.0049
ERAS-2025-016 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.9613 | 8.9611 | -0.0002
ERAS-2025-016 | 05 SOUTHWEST | 789905 | ERAS-36-TAP | 230 | 10.5219 | 10.5266 | 0.0047
ERAS-2025-016 | 05 SOUTHWEST | 789913 | ERAS-36-GSU1 | 230 | 9.6252 | 9.6291 | 0.0039
ERAS-2025-016 | 05 SOUTHWEST | 789915 | ERA-030-TAP | 230 | 6.5113 | 6.5088 | -0.0025
ERAS-2025-018 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.6324 | 7.6304 | -0.002
ERAS-2025-018 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 15.3526 | 15.3487 | -0.0039
ERAS-2025-018 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 28.4963 | 28.515 | 0.0187
ERAS-2025-018 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3206 | 17.334 | 0.0134
ERAS-2025-018 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 7.6524 | 7.6581 | 0.0057
ERAS-2025-018 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.882 | 5.8835 | 0.0015
ERAS-2025-018 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 15.1696 | 15.1733 | 0.0037
ERAS-2025-018 | 05 SOUTHWEST | 524472 | LOPEZ 3 | 115 | 2.426 | 2.4301 | 0.0041
ERAS-2025-018 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.7864 | 2.7919 | 0.0055
ERAS-2025-018 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 3.1312 | 3.1405 | 0.0093
ERAS-2025-018 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.5537 | 2.5587 | 0.005
ERAS-2025-018 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.4373 | 8.453 | 0.0157
ERAS-2025-018 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 4.5957 | 4.6388 | 0.0431
ERAS-2025-018 | 05 SOUTHWEST | 524668 | DS-#20 +3 | 115 | 5.4723 | 5.5544 | 0.0821
ERAS-2025-018 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 5.4641 | 5.546 | 0.0819
ERAS-2025-018 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 10.9814 | 11.4701 | 0.4887
ERAS-2025-018 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.1443 | 10.5925 | 0.4482
ERAS-2025-018 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.6787 | 7.1406 | 0.4619
ERAS-2025-018 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.7912 | 9.1139 | 0.3227
ERAS-2025-018 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.3283 | 7.5694 | 0.2411
ERAS-2025-018 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.6517 | 6.851 | 0.1993
ERAS-2025-018 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.6126 | 2.6276 | 0.015
ERAS-2025-018 | 05 SOUTHWEST | 524784 | W_CLOVIS 3 | 115 | 6.2666 | 6.4513 | 0.1847
ERAS-2025-018 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 5.9923 | 6.169 | 0.1767
ERAS-2025-018 | 05 SOUTHWEST | 524794 | CANNONAFB 3 | 115 | 5.6411 | 5.7973 | 0.1562
ERAS-2025-018 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5213 | 6.7487 | 0.2274
ERAS-2025-018 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.0835 | 10.4954 | 0.4119
ERAS-2025-018 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.8046 | 7.0159 | 0.2113
ERAS-2025-018 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.5833 | 4.6292 | 0.0459
ERAS-2025-018 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.0099 | 11.5008 | 0.4909
ERAS-2025-018 | 05 SOUTHWEST | 524830 | FE-HOLLAND+3 | 115 | 9.0266 | 9.3695 | 0.3429
ERAS-2025-018 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.0031 | 9.3443 | 0.3412
ERAS-2025-018 | 05 SOUTHWEST | 524837 | FE-CLOVIS2+3 | 115 | 10.0061 | 10.4121 | 0.406
ERAS-2025-018 | 05 SOUTHWEST | 524838 | FE-CLOVIS2 3 | 115 | 10.4368 | 10.8793 | 0.4425
ERAS-2025-018 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.2202 | 2.2317 | 0.0115
ERAS-2025-018 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 7.9317 | 8.2369 | 0.3052
ERAS-2025-018 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 9.7535 | 10.314 | 0.5605
ERAS-2025-018 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.9121 | 8.9439 | 1.0318
ERAS-2025-018 | 05 SOUTHWEST | 524885 | SN_JUAN_SS 6 | 230 | 4.4449 | 4.5686 | 0.1237
ERAS-2025-018 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.1701 | 4.2777 | 0.1076
ERAS-2025-018 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 10.8208 | 11.3421 | 0.5213
ERAS-2025-018 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.8472 | 10.6924 | 0.8452
ERAS-2025-018 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.1735 | 7.332 | 0.1585
ERAS-2025-018 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5843 | 7.8813 | 0.297
ERAS-2025-018 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.1735 | 7.332 | 0.1585
ERAS-2025-018 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.3721 | 5.4627 | 0.0906
ERAS-2025-018 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.2409 | 6.44 | 0.1991
ERAS-2025-018 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.6067 | 5.7042 | 0.0975
ERAS-2025-018 | 05 SOUTHWEST | 524948 | PORTALES#2 2 | 69 | 4.8007 | 4.8731 | 0.0724
ERAS-2025-018 | 05 SOUTHWEST | 524962 | S_PORTALES 2 | 69 | 4.2436 | 4.3006 | 0.057
ERAS-2025-018 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.8715 | 6.0472 | 0.1757
ERAS-2025-018 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.7857 | 5.9564 | 0.1707
ERAS-2025-018 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4548 | 5.4812 | 0.0264
ERAS-2025-018 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 4.9011 | 4.9147 | 0.0136
ERAS-2025-018 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.3464 | 5.3735 | 0.0271
ERAS-2025-018 | 05 SOUTHWEST | 525049 | BC-EARTH +3 | 115 | 8.5383 | 8.5485 | 0.0102
ERAS-2025-018 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.7758 | 11.7795 | 0.0037
ERAS-2025-018 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2193 | 11.2233 | 0.004
ERAS-2025-018 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.3878 | 7.3943 | 0.0065
ERAS-2025-018 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.8419 | 10.8468 | 0.0049
ERAS-2025-018 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.1852 | 15.198 | 0.0128
ERAS-2025-018 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.9517 | 11.965 | 0.0133
ERAS-2025-018 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.9252 | 15.9758 | 0.0506
ERAS-2025-018 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.2896 | 25.4894 | 0.1998
ERAS-2025-018 | 05 SOUTHWEST | 525516 | XS1_MPT1PRI3 | 115 | 14.9165 | 14.9609 | 0.0444
ERAS-2025-018 | 05 SOUTHWEST | 525521 | EASTER_WND 6 | 230 | 8.1137 | 8.129 | 0.0153
ERAS-2025-018 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.2873 | 33.7794 | 0.4921
ERAS-2025-018 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.5375 | 14.6161 | 0.0786
ERAS-2025-018 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.481 | 11.5246 | 0.0436
ERAS-2025-018 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5543 | 11.5984 | 0.0441
ERAS-2025-018 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5543 | 11.5984 | 0.0441
ERAS-2025-018 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 6.047 | 6.0504 | 0.0034
ERAS-2025-018 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.7622 | 8.7749 | 0.0127
ERAS-2025-018 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.9918 | 6.0045 | 0.0127
ERAS-2025-018 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0931 | 7.0928 | -0.0003
ERAS-2025-018 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.5238 | 4.5234 | -0.0004
ERAS-2025-018 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9514 | 7.9502 | -0.0012
ERAS-2025-018 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.7667 | 21.7514 | -0.0153
ERAS-2025-018 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.0838 | 28.977 | -0.1068
ERAS-2025-018 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 29.0838 | 28.977 | -0.1068
ERAS-2025-018 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.4526 | 22.4092 | -0.0434
ERAS-2025-018 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.2632 | 10.2557 | -0.0075
ERAS-2025-018 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.779 | 28.6746 | -0.1044
ERAS-2025-018 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 22.1263 | 22.0844 | -0.0419
ERAS-2025-018 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 22.1053 | 22.0634 | -0.0419
ERAS-2025-018 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.3767 | 13.3594 | -0.0173
ERAS-2025-018 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.5821 | 19.5398 | -0.0423
ERAS-2025-018 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.904 | 5.9065 | 0.0025
ERAS-2025-018 | 05 SOUTHWEST | 526108 | SP-ERSKINE+3 | 115 | 12.4484 | 12.446 | -0.0024
ERAS-2025-018 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.8344 | 14.8312 | -0.0032
ERAS-2025-018 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.5646 | 11.5594 | -0.0052
ERAS-2025-018 | 05 SOUTHWEST | 526242 | SP-LPRNO_TP3 | 115 | 14.2712 | 14.2684 | -0.0028
ERAS-2025-018 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.8137 | 16.808 | -0.0057
ERAS-2025-018 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.326 | 12.3228 | -0.0032
ERAS-2025-018 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.9584 | 18.9511 | -0.0073
ERAS-2025-018 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 12.4755 | 12.4798 | 0.0043
ERAS-2025-018 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0294 | 12.037 | 0.0076
ERAS-2025-018 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5929 | 10.5982 | 0.0053
ERAS-2025-018 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8519 | 13.8496 | -0.0023
ERAS-2025-018 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.61 | 6.6091 | -0.0009
ERAS-2025-018 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6562 | 19.6594 | 0.0032
ERAS-2025-018 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.0496 | 21.058 | 0.0084
ERAS-2025-018 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.1829 | 11.1838 | 0.0009
ERAS-2025-018 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6937 | 16.6979 | 0.0042
ERAS-2025-018 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.3535 | 12.3553 | 0.0018
ERAS-2025-018 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.6608 | 17.6642 | 0.0034
ERAS-2025-018 | 05 SOUTHWEST | 527455 | RSWL_SLRCOL3 | 115 | 7.5806 | 7.611 | 0.0304
ERAS-2025-018 | 05 SOUTHWEST | 527470 | CHVS_SLRCOL3 | 115 | 7.4098 | 7.4387 | 0.0289
ERAS-2025-018 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.675 | 7.7061 | 0.0311
ERAS-2025-018 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 5.5035 | 5.5405 | 0.037
ERAS-2025-018 | 05 SOUTHWEST | 527501 | URTON 3 | 115 | 6.4237 | 6.4442 | 0.0205
ERAS-2025-018 | 05 SOUTHWEST | 527508 | PRICE 3 | 115 | 5.2708 | 5.2848 | 0.014
ERAS-2025-018 | 05 SOUTHWEST | 527509 | PRICE_TAP 3 | 115 | 5.9403 | 5.9582 | 0.0179
ERAS-2025-018 | 05 SOUTHWEST | 527522 | ROSWELL_CTY3 | 115 | 6.1412 | 6.1589 | 0.0177
ERAS-2025-018 | 05 SOUTHWEST | 527541 | CAPITAN 3 | 115 | 5.1241 | 5.1365 | 0.0124
ERAS-2025-018 | 05 SOUTHWEST | 527546 | SAMSON 3 | 115 | 6.0427 | 6.0598 | 0.0171
ERAS-2025-018 | 05 SOUTHWEST | 527564 | ROSWLL_INT 3 | 115 | 6.3929 | 6.4112 | 0.0183
ERAS-2025-018 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.6247 | 14.6393 | 0.0146
ERAS-2025-018 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.305 | 14.3216 | 0.0166
ERAS-2025-018 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8811 | 17.9042 | 0.0231
ERAS-2025-018 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.951 | 7.9551 | 0.0041
ERAS-2025-018 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 13.9912 | 13.9753 | -0.0159
ERAS-2025-018 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 13.9912 | 13.9753 | -0.0159
ERAS-2025-018 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 12.0331 | 11.9931 | -0.04
ERAS-2025-018 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.6668 | 9.6583 | -0.0085
ERAS-2025-018 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 22.4872 | 22.4838 | -0.0034
ERAS-2025-018 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.9695 | 20.972 | 0.0025
ERAS-2025-018 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 7.6814 | 7.6728 | -0.0086
ERAS-2025-018 | 05 SOUTHWEST | 599950 | LAMAR7 | 345 | 2.4563 | 2.4563 | 0
ERAS-2025-018 | 05 SOUTHWEST | 599951 | LAMAR 6 | 345 | 60.6375 | 60.6375 | 0
ERAS-2025-018 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.8472 | 10.6924 | 0.8452
ERAS-2025-018 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 12.0331 | 11.9931 | -0.04
ERAS-2025-018 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.1232 | 8.1385 | 0.0153
ERAS-2025-018 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.5541 | 14.6359 | 0.0818
ERAS-2025-018 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.6001 | 11.6126 | 0.0125
ERAS-2025-018 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.8725 | 9.5449 | 0.6724
ERAS-2025-018 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 32.613 | 33.0847 | 0.4717
ERAS-2025-018 | 05 SOUTHWEST | 788772 | ERA-18 | 230 | 6.9746 | 8.0249 | 1.0503
ERAS-2025-018 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.5836 | 13.5691 | -0.0145
ERAS-2025-018 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9687 | 8.9668 | -0.0019
ERAS-2025-018 | 05 SOUTHWEST | 788971 | ERA-30 | 230 | 6.4739 | 6.4996 | 0.0257
ERAS-2025-018 | 05 SOUTHWEST | 789905 | ERAS-36-TAP | 230 | 10.5228 | 10.5266 | 0.0038
ERAS-2025-018 | 05 SOUTHWEST | 789915 | ERA-030-TAP | 230 | 6.4829 | 6.5088 | 0.0259
ERAS-2025-018 | 05 SOUTHWEST | 999997 | DUMMY | 230 | 6.4829 | 6.5088 | 0.0259
ERAS-2025-020 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 7.6285 | 7.6304 | 0.0019
ERAS-2025-020 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.6285 | 7.6304 | 0.0019
ERAS-2025-020 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.9979 | 8.9961 | -0.0018
ERAS-2025-020 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 15.3478 | 15.3487 | 0.0009
ERAS-2025-020 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 28.4664 | 28.515 | 0.0486
ERAS-2025-020 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.2614 | 17.334 | 0.0726
ERAS-2025-020 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 7.6245 | 7.6581 | 0.0336
ERAS-2025-020 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.8757 | 5.8835 | 0.0078
ERAS-2025-020 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6866 | 10.6924 | 0.0058
ERAS-2025-020 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2233 | 11.2233 | 0
ERAS-2025-020 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4563 | 25.4894 | 0.0331
ERAS-2025-020 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7093 | 33.7794 | 0.0701
ERAS-2025-020 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.5635 | 14.6161 | 0.0526
ERAS-2025-020 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.5128 | 11.5246 | 0.0118
ERAS-2025-020 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5865 | 11.5984 | 0.0119
ERAS-2025-020 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5865 | 11.5984 | 0.0119
ERAS-2025-020 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0025 | 6.0045 | 0.002
ERAS-2025-020 | 05 SOUTHWEST | 525750 | G18-015-TAP | 345 | 5.9133 | 5.9147 | 0.0014
ERAS-2025-020 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.771 | 21.7514 | -0.0196
ERAS-2025-020 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.1019 | 28.977 | -0.1249
ERAS-2025-020 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 29.1019 | 28.977 | -0.1249
ERAS-2025-020 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.3739 | 22.4092 | 0.0353
ERAS-2025-020 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.2494 | 10.2557 | 0.0063
ERAS-2025-020 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.7967 | 28.6746 | -0.1221
ERAS-2025-020 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 22.0502 | 22.0844 | 0.0342
ERAS-2025-020 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 22.0292 | 22.0634 | 0.0342
ERAS-2025-020 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.3798 | 13.3594 | -0.0204
ERAS-2025-020 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.4826 | 19.5398 | 0.0572
ERAS-2025-020 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.3514 | 8.3822 | 0.0308
ERAS-2025-020 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.5637 | 11.5594 | -0.0043
ERAS-2025-020 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.9579 | 18.9511 | -0.0068
ERAS-2025-020 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 12.4725 | 12.4798 | 0.0073
ERAS-2025-020 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0239 | 12.037 | 0.0131
ERAS-2025-020 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5854 | 10.5982 | 0.0128
ERAS-2025-020 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8491 | 13.8496 | 0.0005
ERAS-2025-020 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1563 | 11.1636 | 0.0073
ERAS-2025-020 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.9796 | 16.0403 | 0.0607
ERAS-2025-020 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3755 | 6.3791 | 0.0036
ERAS-2025-020 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.6856 | 10.6988 | 0.0132
ERAS-2025-020 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6091 | 19.6594 | 0.0503
ERAS-2025-020 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 20.9041 | 21.058 | 0.1539
ERAS-2025-020 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 10.9865 | 11.1838 | 0.1973
ERAS-2025-020 | 05 SOUTHWEST | 526943 | LG-PLAINS +3 | 115 | 8.5031 | 8.5108 | 0.0077
ERAS-2025-020 | 05 SOUTHWEST | 527000 | ERAS-014 | 345 | 11.8911 | 12.1878 | 0.2967
ERAS-2025-020 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6191 | 16.6979 | 0.0788
ERAS-2025-020 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 16.4621 | 16.5394 | 0.0773
ERAS-2025-020 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 16.3339 | 16.4047 | 0.0708
ERAS-2025-020 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.5719 | 14.5944 | 0.0225
ERAS-2025-020 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 13.073 | 13.4726 | 0.3996
ERAS-2025-020 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2634 | 13.292 | 0.0286
ERAS-2025-020 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.2872 | 12.3553 | 0.0681
ERAS-2025-020 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.7053 | 12.7282 | 0.0229
ERAS-2025-020 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.4669 | 14.4892 | 0.0223
ERAS-2025-020 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.5329 | 11.547 | 0.0141
ERAS-2025-020 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 17.6401 | 17.6712 | 0.0311
ERAS-2025-020 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 23.5644 | 23.6193 | 0.0549
ERAS-2025-020 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 23.5644 | 23.6193 | 0.0549
ERAS-2025-020 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.1583 | 25.2143 | 0.056
ERAS-2025-020 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.597 | 17.6642 | 0.0672
ERAS-2025-020 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.597 | 17.6642 | 0.0672
ERAS-2025-020 | 05 SOUTHWEST | 527193 | LG-PLSHILL+3 | 115 | 8.3639 | 8.3706 | 0.0067
ERAS-2025-020 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3478 | 8.3545 | 0.0067
ERAS-2025-020 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.6464 | 9.6546 | 0.0082
ERAS-2025-020 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.8314 | 14.8564 | 0.025
ERAS-2025-020 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.7903 | 8.8063 | 0.016
ERAS-2025-020 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 11.0856 | 11.1033 | 0.0177
ERAS-2025-020 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 14.4589 | 14.6393 | 0.1804
ERAS-2025-020 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 14.4589 | 14.6393 | 0.1804
ERAS-2025-020 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.4589 | 14.6393 | 0.1804
ERAS-2025-020 | 05 SOUTHWEST | 527640 | MILO_WIND 7 | 345 | 14.1391 | 14.3216 | 0.1825
ERAS-2025-020 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 11.6819 | 11.8082 | 0.1263
ERAS-2025-020 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.1391 | 14.3216 | 0.1825
ERAS-2025-020 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.6207 | 17.9042 | 0.2835
ERAS-2025-020 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 11.6819 | 11.8082 | 0.1263
ERAS-2025-020 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 11.6819 | 11.8082 | 0.1263
ERAS-2025-020 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.8719 | 7.9551 | 0.0832
ERAS-2025-020 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 13.9488 | 13.9753 | 0.0265
ERAS-2025-020 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 13.9488 | 13.9753 | 0.0265
ERAS-2025-020 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 11.9677 | 11.9931 | 0.0254
ERAS-2025-020 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.5623 | 9.6583 | 0.096
ERAS-2025-020 | 05 SOUTHWEST | 527845 | C1_MPT_PRI 3 | 115 | 10.9992 | 11.0268 | 0.0276
ERAS-2025-020 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 33.2093 | 33.4572 | 0.2479
ERAS-2025-020 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 22.1526 | 22.4838 | 0.3312
ERAS-2025-020 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 22.1526 | 22.4838 | 0.3312
ERAS-2025-020 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 37.0718 | 37.3663 | 0.2945
ERAS-2025-020 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 25.441 | 25.9982 | 0.5572
ERAS-2025-020 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 19.6544 | 20.972 | 1.3176
ERAS-2025-020 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 22.2026 | 22.4009 | 0.1983
ERAS-2025-020 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 9.2646 | 9.3131 | 0.0485
ERAS-2025-020 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 13.8126 | 14.1206 | 0.308
ERAS-2025-020 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 22.3045 | 22.5054 | 0.2009
ERAS-2025-020 | 05 SOUTHWEST | 527972 | MIDSPRON_TP3 | 115 | 21.0091 | 21.2674 | 0.2583
ERAS-2025-020 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 33.5696 | 33.8529 | 0.2833
ERAS-2025-020 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.8533 | 7.9519 | 0.0986
ERAS-2025-020 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.0386 | 17.26 | 0.2214
ERAS-2025-020 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 15.6808 | 15.7803 | 0.0995
ERAS-2025-020 | 05 SOUTHWEST | 528020 | BOPCO_PKRLK3 | 115 | 32.1979 | 32.4637 | 0.2658
ERAS-2025-020 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 36.9193 | 37.8262 | 0.9069
ERAS-2025-020 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 36.9193 | 37.8262 | 0.9069
ERAS-2025-020 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 14.5354 | 14.9797 | 0.4443
ERAS-2025-020 | 05 SOUTHWEST | 528033 | CPERHEAD_HV3 | 115 | 15.4066 | 15.53 | 0.1234
ERAS-2025-020 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 16.9646 | 17.0595 | 0.0949
ERAS-2025-020 | 05 SOUTHWEST | 528052 | TIPTOP-SOLAR | 115 | 30.3155 | 30.9301 | 0.6146
ERAS-2025-020 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 7.6507 | 7.6728 | 0.0221
ERAS-2025-020 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 19.626 | 19.7366 | 0.1106
ERAS-2025-020 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 11.1894 | 11.3389 | 0.1495
ERAS-2025-020 | 05 SOUTHWEST | 528194 | MALAGABEND 3 | 115 | 10.2782 | 10.3063 | 0.0281
ERAS-2025-020 | 05 SOUTHWEST | 528222 | CHINA_DRAW 3 | 115 | 18.0819 | 18.1257 | 0.0438
ERAS-2025-020 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 11.853 | 11.9835 | 0.1305
ERAS-2025-020 | 05 SOUTHWEST | 528228 | WOOD_DRAW 3 | 115 | 12.5662 | 12.6019 | 0.0357
ERAS-2025-020 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 28.4467 | 28.983 | 0.5363
ERAS-2025-020 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 25.1311 | 25.5455 | 0.4144
ERAS-2025-020 | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 25.2212 | 25.6419 | 0.4207
ERAS-2025-020 | 05 SOUTHWEST | 528235 | WOLFCAMP_TP3 | 115 | 28.2105 | 28.4311 | 0.2206
ERAS-2025-020 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 11.5532 | 11.6172 | 0.064
ERAS-2025-020 | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 9.2132 | 9.2489 | 0.0357
ERAS-2025-020 | 05 SOUTHWEST | 528317 | ENRON_TP 3 | 115 | 30.7037 | 31.2555 | 0.5518
ERAS-2025-020 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.3773 | 9.3913 | 0.014
ERAS-2025-020 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.7758 | 9.7903 | 0.0145
ERAS-2025-020 | 05 SOUTHWEST | 528334 | LE-NRTH_INT3 | 115 | 9.7112 | 9.7255 | 0.0143
ERAS-2025-020 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 9.1411 | 9.1585 | 0.0174
ERAS-2025-020 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 31.7455 | 31.9549 | 0.2094
ERAS-2025-020 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 31.7455 | 31.9549 | 0.2094
ERAS-2025-020 | 05 SOUTHWEST | 528390 | LYNCH_TP 3 | 115 | 11.3255 | 11.377 | 0.0515
ERAS-2025-020 | 05 SOUTHWEST | 528392 | PEARLE 3 | 115 | 10.2155 | 10.2505 | 0.035
ERAS-2025-020 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 16.446 | 16.5769 | 0.1309
ERAS-2025-020 | 05 SOUTHWEST | 528396 | XTO_BULLDOG3 | 115 | 12.3094 | 12.3744 | 0.065
ERAS-2025-020 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 32.3582 | 32.9729 | 0.6147
ERAS-2025-020 | 05 SOUTHWEST | 528400 | LEANTL_345 | 345 | 12.7023 | 12.9985 | 0.2962
ERAS-2025-020 | 05 SOUTHWEST | 528422 | DCP_ZIA TP 3 | 115 | 12.6991 | 12.7769 | 0.0778
ERAS-2025-020 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.6182 | 8.6315 | 0.0133
ERAS-2025-020 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.8783 | 12.9128 | 0.0345
ERAS-2025-020 | 05 SOUTHWEST | 528435 | MILLEN 3 | 115 | 12.8783 | 12.9128 | 0.0345
ERAS-2025-020 | 05 SOUTHWEST | 528436 | MILLEN_TPE 3 | 115 | 12.8783 | 12.9128 | 0.0345
ERAS-2025-020 | 05 SOUTHWEST | 528491 | MONUMENT 3 | 115 | 17.4633 | 17.5319 | 0.0686
ERAS-2025-020 | 05 SOUTHWEST | 528540 | WHITTEN 3 | 115 | 10.3059 | 10.3535 | 0.0476
ERAS-2025-020 | 05 SOUTHWEST | 528542 | ZIAHILS13 3 | 115 | 8.1847 | 8.2066 | 0.0219
ERAS-2025-020 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 11.2993 | 11.332 | 0.0327
ERAS-2025-020 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 15.1862 | 15.3321 | 0.1459
ERAS-2025-020 | 05 SOUTHWEST | 528603 | NA_ENRICH 3 | 115 | 14.184 | 14.3039 | 0.1199
ERAS-2025-020 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 9.3348 | 9.5272 | 0.1924
ERAS-2025-020 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 6.0288 | 6.0311 | 0.0023
ERAS-2025-020 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 11.9677 | 11.9931 | 0.0254
ERAS-2025-020 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 14.655 | 14.7112 | 0.0562
ERAS-2025-020 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.6243 | 14.6359 | 0.0116
ERAS-2025-020 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.1083 | 7.1112 | 0.0029
ERAS-2025-020 | 05 SOUTHWEST | 762442 | G18-004-TAP | 115 | 26.9345 | 27.0842 | 0.1497
ERAS-2025-020 | 05 SOUTHWEST | 762866 | GEN-2018-052 | 115 | 35.3925 | 36.2257 | 0.8332
ERAS-2025-020 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.2349 | 10.4059 | 0.171
ERAS-2025-020 | 05 SOUTHWEST | 788703 | ERA-02 | 345 | 21.6874 | 21.7204 | 0.033
ERAS-2025-020 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0175 | 33.0847 | 0.0672
ERAS-2025-020 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 15.3 | 16.8295 | 1.5295
ERAS-2025-020 | 05 SOUTHWEST | 788810 | ERA-21 | 345 | 11.7389 | 11.7471 | 0.0082
ERAS-2025-020 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 15.3738 | 16.9025 | 1.5287
ERAS-2025-020 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.5581 | 13.5691 | 0.011
ERAS-2025-020 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9115 | 8.9668 | 0.0553
ERAS-2025-020 | 05 SOUTHWEST | 788945 | ERA-2025-27 | 230 | 15.1527 | 15.2131 | 0.0604
ERAS-2025-020 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.906 | 8.9611 | 0.0551
ERAS-2025-020 | 05 SOUTHWEST | 789915 | ERA-030-TAP | 230 | 6.5048 | 6.5088 | 0.004
ERAS-2025-021 | 05 SOUTHWEST | 500001 | COMANC7_TAP | 345 | 13.6557 | 13.6679 | 0.0122
ERAS-2025-021 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 7.6058 | 7.6304 | 0.0246
ERAS-2025-021 | 05 SOUTHWEST | 511490 | ELKCITY6 | 230 | 7.7029 | 7.7064 | 0.0035
ERAS-2025-021 | 05 SOUTHWEST | 511541 | DEMPSEYR POI | 230 | 9.3361 | 9.3423 | 0.0062
ERAS-2025-021 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 11.5708 | 11.6004 | 0.0296
ERAS-2025-021 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.3501 | 12.3645 | 0.0144
ERAS-2025-021 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 7.5751 | 7.5994 | 0.0243
ERAS-2025-021 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.6058 | 7.6304 | 0.0246
ERAS-2025-021 | 05 SOUTHWEST | 511587 | MATO 7 | 345 | 9.1273 | 9.1347 | 0.0074
ERAS-2025-021 | 05 SOUTHWEST | 511592 | SEVEN7A_HV | 345 | 8.6932 | 8.6996 | 0.0064
ERAS-2025-021 | 05 SOUTHWEST | 511607 | O.K.U.3-7 | 345 | 7.6058 | 7.6304 | 0.0246
ERAS-2025-021 | 05 SOUTHWEST | 511999 | DVRSION-WIND | 345 | 4.9515 | 4.9613 | 0.0098
ERAS-2025-021 | 05 SOUTHWEST | 514785 | WOODWRD4 | 138 | 20.2608 | 20.2378 | -0.023
ERAS-2025-021 | 05 SOUTHWEST | 514796 | IODINE-4 | 138 | 7.7915 | 7.7889 | -0.0026
ERAS-2025-021 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 23.2921 | 23.142 | -0.1501
ERAS-2025-021 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 27.1653 | 27.1123 | -0.053
ERAS-2025-021 | 05 SOUTHWEST | 515378 | WWRDEHV9 | 765 | 5.4112 | 5.3665 | -0.0447
ERAS-2025-021 | 05 SOUTHWEST | 515394 | KEENAN 4 | 138 | 9.4404 | 9.4346 | -0.0058
ERAS-2025-021 | 05 SOUTHWEST | 515398 | OUSPRT 4 | 138 | 10.2104 | 10.2035 | -0.0069
ERAS-2025-021 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 18.7759 | 18.7419 | -0.034
ERAS-2025-021 | 05 SOUTHWEST | 515425 | WWDPST 4 | 138 | 20.2711 | 20.248 | -0.0231
ERAS-2025-021 | 05 SOUTHWEST | 515448 | CRSRDSW7 | 345 | 12.9049 | 12.8892 | -0.0157
ERAS-2025-021 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.9536 | 8.9961 | 0.0425
ERAS-2025-021 | 05 SOUTHWEST | 515497 | MATHWSN7 | 345 | 38.4169 | 38.4061 | -0.0108
ERAS-2025-021 | 05 SOUTHWEST | 515582 | SLNGWND7 | 345 | 8.9288 | 8.9215 | -0.0073
ERAS-2025-021 | 05 SOUTHWEST | 515585 | MAMTHPW7 | 345 | 14.5927 | 14.5726 | -0.0201
ERAS-2025-021 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 14.2367 | 14.2206 | -0.0161
ERAS-2025-021 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 18.4778 | 18.4866 | 0.0088
ERAS-2025-021 | 05 SOUTHWEST | 515825 | GRTWSRN7 | 345 | 9.4209 | 9.396 | -0.0249
ERAS-2025-021 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 15.0392 | 15.0099 | -0.0293
ERAS-2025-021 | 05 SOUTHWEST | 515853 | DGRASSE4 | 138 | 14.9741 | 14.966 | -0.0081
ERAS-2025-021 | 05 SOUTHWEST | 515951 | PERSIMN7 | 345 | 11.652 | 11.6141 | -0.0379
ERAS-2025-021 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 13.369 | 13.3191 | -0.0499
ERAS-2025-021 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 11.5872 | 11.6175 | 0.0303
ERAS-2025-021 | 05 SOUTHWEST | 516106 | BOBCAT 7 | 345 | 16.4638 | 16.409 | -0.0548
ERAS-2025-021 | 05 SOUTHWEST | 516146 | 25MILE 7 | 345 | 16.4309 | 16.3763 | -0.0546
ERAS-2025-021 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3124 | 17.334 | 0.0216
ERAS-2025-021 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 30.0503 | 30.063 | 0.0127
ERAS-2025-021 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.2052 | 16.2097 | 0.0045
ERAS-2025-021 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.8402 | 17.8428 | 0.0026
ERAS-2025-021 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 15.1688 | 15.1733 | 0.0045
ERAS-2025-021 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 7.1399 | 7.1406 | 0.0007
ERAS-2025-021 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.9428 | 8.9439 | 0.0011
ERAS-2025-021 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.3411 | 11.3421 | 0.001
ERAS-2025-021 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6906 | 10.6924 | 0.0018
ERAS-2025-021 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.4114 | 12.416 | 0.0046
ERAS-2025-021 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.7752 | 11.7795 | 0.0043
ERAS-2025-021 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2142 | 11.2233 | 0.0091
ERAS-2025-021 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.8999 | 6.9015 | 0.0016
ERAS-2025-021 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.9733 | 7.9748 | 0.0015
ERAS-2025-021 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9487 | 6.9496 | 0.0009
ERAS-2025-021 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.8427 | 10.8468 | 0.0041
ERAS-2025-021 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.1929 | 15.198 | 0.0051
ERAS-2025-021 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.9586 | 11.965 | 0.0064
ERAS-2025-021 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.9719 | 15.9758 | 0.0039
ERAS-2025-021 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4723 | 25.4894 | 0.0171
ERAS-2025-021 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7497 | 33.7794 | 0.0297
ERAS-2025-021 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.6037 | 14.6161 | 0.0124
ERAS-2025-021 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5945 | 11.5984 | 0.0039
ERAS-2025-021 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5945 | 11.5984 | 0.0039
ERAS-2025-021 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.7736 | 8.7749 | 0.0013
ERAS-2025-021 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0035 | 6.0045 | 0.001
ERAS-2025-021 | 05 SOUTHWEST | 525731 | SP-ABERNTH+2 | 69 | 3.0532 | 3.0536 | 0.0004
ERAS-2025-021 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.6291 | 2.6294 | 0.0003
ERAS-2025-021 | 05 SOUTHWEST | 525750 | G18-015-TAP | 345 | 5.8891 | 5.9147 | 0.0256
ERAS-2025-021 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.194 | 6.1954 | 0.0014
ERAS-2025-021 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4944 | 5.4951 | 0.0007
ERAS-2025-021 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0908 | 7.0928 | 0.002
ERAS-2025-021 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 6.1435 | 6.1447 | 0.0012
ERAS-2025-021 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.5225 | 4.5234 | 0.0009
ERAS-2025-021 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9476 | 7.9502 | 0.0026
ERAS-2025-021 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.7169 | 21.7514 | 0.0345
ERAS-2025-021 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 28.7922 | 28.977 | 0.1848
ERAS-2025-021 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 28.7922 | 28.977 | 0.1848
ERAS-2025-021 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 21.532 | 22.4092 | 0.8772
ERAS-2025-021 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.1053 | 10.2557 | 0.1504
ERAS-2025-021 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.494 | 28.6746 | 0.1806
ERAS-2025-021 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 21.2343 | 22.0844 | 0.8501
ERAS-2025-021 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 21.2141 | 22.0634 | 0.8493
ERAS-2025-021 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7171 | 2.7174 | 0.0003
ERAS-2025-021 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.8626 | 3.8632 | 0.0006
ERAS-2025-021 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.33 | 13.3594 | 0.0294
ERAS-2025-021 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.1603 | 19.5398 | 0.3795
ERAS-2025-021 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.2673 | 8.3822 | 0.1149
ERAS-2025-021 | 05 SOUTHWEST | 526108 | SP-ERSKINE+3 | 115 | 12.4381 | 12.446 | 0.0079
ERAS-2025-021 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 12.4176 | 12.4254 | 0.0078
ERAS-2025-021 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.7316 | 2.7318 | 0.0002
ERAS-2025-021 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.8206 | 14.8312 | 0.0106
ERAS-2025-021 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.5442 | 11.5594 | 0.0152
ERAS-2025-021 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.8794 | 12.8871 | 0.0077
ERAS-2025-021 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.612 | 11.618 | 0.006
ERAS-2025-021 | 05 SOUTHWEST | 526241 | SP-LEPRINO 3 | 115 | 13.2118 | 13.2185 | 0.0067
ERAS-2025-021 | 05 SOUTHWEST | 526242 | SP-LPRNO_TP3 | 115 | 14.2605 | 14.2684 | 0.0079
ERAS-2025-021 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.3983 | 19.4105 | 0.0122
ERAS-2025-021 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.7911 | 16.808 | 0.0169
ERAS-2025-021 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.7868 | 15.7959 | 0.0091
ERAS-2025-021 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.3141 | 12.3228 | 0.0087
ERAS-2025-021 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.9313 | 18.9511 | 0.0198
ERAS-2025-021 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0293 | 12.037 | 0.0077
ERAS-2025-021 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5923 | 10.5982 | 0.0059
ERAS-2025-021 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.8556 | 12.8621 | 0.0065
ERAS-2025-021 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8344 | 13.8496 | 0.0152
ERAS-2025-021 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.4091 | 7.4106 | 0.0015
ERAS-2025-021 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6067 | 6.6091 | 0.0024
ERAS-2025-021 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1715 | 5.1729 | 0.0014
ERAS-2025-021 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6512 | 19.6594 | 0.0082
ERAS-2025-021 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.035 | 21.058 | 0.023
ERAS-2025-021 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.1548 | 11.1838 | 0.029
ERAS-2025-021 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6863 | 16.6979 | 0.0116
ERAS-2025-021 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.3494 | 12.3553 | 0.0059
ERAS-2025-021 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.6546 | 17.6642 | 0.0096
ERAS-2025-021 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8709 | 17.9042 | 0.0333
ERAS-2025-021 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9332 | 7.9551 | 0.0219
ERAS-2025-021 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.9341 | 20.972 | 0.0379
ERAS-2025-021 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9052 | 7.9519 | 0.0467
ERAS-2025-021 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.1652 | 17.26 | 0.0948
ERAS-2025-021 | 05 SOUTHWEST | 539801 | THISTLE7 | 345 | 16.2254 | 16.2145 | -0.0109
ERAS-2025-021 | 05 SOUTHWEST | 588560 | GEN-2017-011 | 345 | 13.1708 | 13.1356 | -0.0352
ERAS-2025-021 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
ERAS-2025-021 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.6906 | 10.6924 | 0.0018
ERAS-2025-021 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.1371 | 8.1385 | 0.0014
ERAS-2025-021 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.631 | 14.6359 | 0.0049
ERAS-2025-021 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.0419 | 7.1112 | 0.0693
ERAS-2025-021 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.8772 | 5.9027 | 0.0255
ERAS-2025-021 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.6066 | 11.6126 | 0.006
ERAS-2025-021 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.5434 | 9.5449 | 0.0015
ERAS-2025-021 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.3808 | 10.4059 | 0.0251
ERAS-2025-021 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 20.0982 | 19.9863 | -0.1119
ERAS-2025-021 | 05 SOUTHWEST | 788703 | ERA-02 | 345 | 20.8982 | 21.7204 | 0.8222
ERAS-2025-021 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0562 | 33.0847 | 0.0285
ERAS-2025-021 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 16.8026 | 16.8295 | 0.0269
ERAS-2025-021 | 05 SOUTHWEST | 788810 | ERA-21 | 345 | 10.6628 | 11.7471 | 1.0843
ERAS-2025-021 | 05 SOUTHWEST | 788817 | ERA-21-MPT1 | 345 | 9.2949 | 10.2549 | 0.96
ERAS-2025-021 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.8753 | 16.9025 | 0.0272
ERAS-2025-021 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 12.5083 | 13.5691 | 1.0608
ERAS-2025-021 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9127 | 8.9668 | 0.0541
ERAS-2025-021 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.9071 | 8.9611 | 0.054
ERAS-2025-021 | 05 SOUTHWEST | 789905 | ERAS-36-TAP | 230 | 10.5235 | 10.5266 | 0.0031
ERAS-2025-026 | 05 SOUTHWEST | 500001 | COMANC7_TAP | 345 | 11.9686 | 13.6679 | 1.6993
ERAS-2025-026 | 05 SOUTHWEST | 511409 | TREASILD7 | 345 | 13.7646 | 14.4227 | 0.6581
ERAS-2025-026 | 05 SOUTHWEST | 511422 | FLETCHR4 | 138 | 8.1448 | 8.1932 | 0.0484
ERAS-2025-026 | 05 SOUTHWEST | 511423 | FLE TAP4 | 138 | 8.901 | 8.9586 | 0.0576
ERAS-2025-026 | 05 SOUTHWEST | 511428 | LG-YEAR4 | 138 | 12.9731 | 13.1962 | 0.2231
ERAS-2025-026 | 05 SOUTHWEST | 511431 | LWS S4 | 138 | 11.4693 | 11.651 | 0.1817
ERAS-2025-026 | 05 SOUTHWEST | 511436 | COMANC-2 | 69 | 10.0252 | 10.0613 | 0.0361
ERAS-2025-026 | 05 SOUTHWEST | 511437 | COMANC-4 | 138 | 18.9745 | 19.4704 | 0.4959
ERAS-2025-026 | 05 SOUTHWEST | 511439 | LWSTAP 4 | 138 | 11.9521 | 12.1496 | 0.1975
ERAS-2025-026 | 05 SOUTHWEST | 511451 | CYRIL--2 | 69 | 5.2102 | 5.218 | 0.0078
ERAS-2025-026 | 05 SOUTHWEST | 511453 | DUNCAN-4 | 138 | 6.781 | 6.8146 | 0.0336
ERAS-2025-026 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 7.4207 | 7.6304 | 0.2097
ERAS-2025-026 | 05 SOUTHWEST | 511461 | FT.SILL2 | 69 | 6.411 | 6.4316 | 0.0206
ERAS-2025-026 | 05 SOUTHWEST | 511466 | L.E.S.-2 | 69 | 16.8607 | 17.0317 | 0.171
ERAS-2025-026 | 05 SOUTHWEST | 511467 | L.E.S.-4 | 138 | 25.8031 | 26.9046 | 1.1015
ERAS-2025-026 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 13.6165 | 15.1672 | 1.5507
ERAS-2025-026 | 05 SOUTHWEST | 511469 | LGORE-N2 | 69 | 8.3859 | 8.4244 | 0.0385
ERAS-2025-026 | 05 SOUTHWEST | 511470 | LGORE-S2 | 69 | 7.2792 | 7.3108 | 0.0316
ERAS-2025-026 | 05 SOUTHWEST | 511471 | LWS-NTP4 | 138 | 12.188 | 12.3954 | 0.2074
ERAS-2025-026 | 05 SOUTHWEST | 511473 | PO.HILL2 | 69 | 6.1889 | 6.2054 | 0.0165
ERAS-2025-026 | 05 SOUTHWEST | 511474 | SHERID4 | 138 | 12.8831 | 13.1255 | 0.2424
ERAS-2025-026 | 05 SOUTHWEST | 511477 | S.W.S.-4 | 138 | 32.6591 | 32.8738 | 0.2147
ERAS-2025-026 | 05 SOUTHWEST | 511486 | ELGINJT4 | 138 | 10.4493 | 10.5387 | 0.0894
ERAS-2025-026 | 05 SOUTHWEST | 511487 | ELGINJT2 | 69 | 9.1485 | 9.1799 | 0.0314
ERAS-2025-026 | 05 SOUTHWEST | 511488 | 112GORE4 | 138 | 13.2898 | 13.5225 | 0.2327
ERAS-2025-026 | 05 SOUTHWEST | 511494 | COMMTAP4 | 138 | 22.5326 | 23.3289 | 0.7963
ERAS-2025-026 | 05 SOUTHWEST | 511503 | LAW WC2 | 69 | 4.7958 | 4.8094 | 0.0136
ERAS-2025-026 | 05 SOUTHWEST | 511509 | 53CACHE4 | 138 | 12.2212 | 12.4324 | 0.2112
ERAS-2025-026 | 05 SOUTHWEST | 511510 | LAIRGST4 | 138 | 12.8642 | 13.0798 | 0.2156
ERAS-2025-026 | 05 SOUTHWEST | 511512 | RPPAPER4 | 138 | 12.3184 | 12.5232 | 0.2048
ERAS-2025-026 | 05 SOUTHWEST | 511524 | L-DISTP2 | 69 | 9.2563 | 9.2866 | 0.0303
ERAS-2025-026 | 05 SOUTHWEST | 511537 | ARTVLTP4 | 138 | 12.2395 | 12.4519 | 0.2124
ERAS-2025-026 | 05 SOUTHWEST | 511538 | ARTVILL4 | 138 | 8.8339 | 8.9438 | 0.1099
ERAS-2025-026 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 11.5652 | 11.6004 | 0.0352
ERAS-2025-026 | 05 SOUTHWEST | 511563 | ELSWORTH 4 | 138 | 10.4023 | 10.4897 | 0.0874
ERAS-2025-026 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 7.3915 | 7.5994 | 0.2079
ERAS-2025-026 | 05 SOUTHWEST | 511568 | TERRYRD7 | 345 | 9.6017 | 10.0164 | 0.4147
ERAS-2025-026 | 05 SOUTHWEST | 511571 | RUSHSPR7 | 345 | 6.2321 | 6.3947 | 0.1626
ERAS-2025-026 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.4207 | 7.6304 | 0.2097
ERAS-2025-026 | 05 SOUTHWEST | 511586 | TONKAWA4 | 138 | 10.4194 | 10.4697 | 0.0503
ERAS-2025-026 | 05 SOUTHWEST | 511587 | MATO 7 | 345 | 9.0792 | 9.1347 | 0.0555
ERAS-2025-026 | 05 SOUTHWEST | 511592 | SEVEN7A_HV | 345 | 8.6492 | 8.6996 | 0.0504
ERAS-2025-026 | 05 SOUTHWEST | 511600 | HVBUS | 138 | 7.5033 | 7.5296 | 0.0263
ERAS-2025-026 | 05 SOUTHWEST | 511607 | O.K.U.3-7 | 345 | 7.4207 | 7.6304 | 0.2097
ERAS-2025-026 | 05 SOUTHWEST | 511920 | CDW-SUB | 345 | 9.8084 | 10.1367 | 0.3283
ERAS-2025-026 | 05 SOUTHWEST | 511979 | RSHSPR1_MPT1 | 345 | 5.5958 | 5.7342 | 0.1384
ERAS-2025-026 | 05 SOUTHWEST | 511992 | HVBUS | 345 | 11.1341 | 11.5612 | 0.4271
ERAS-2025-026 | 05 SOUTHWEST | 511999 | DVRSION-WIND | 345 | 4.8765 | 4.9613 | 0.0848
ERAS-2025-026 | 05 SOUTHWEST | 514801 | MINCO 7 | 345 | 22.9101 | 23.1231 | 0.213
ERAS-2025-026 | 05 SOUTHWEST | 514809 | JOHNCO 7 | 345 | 9.0751 | 9.1375 | 0.0624
ERAS-2025-026 | 05 SOUTHWEST | 514901 | CIMARON7 | 345 | 38.1632 | 38.3011 | 0.1379
ERAS-2025-026 | 05 SOUTHWEST | 515135 | SUNNYSD4 | 138 | 20.9328 | 21.1266 | 0.1938
ERAS-2025-026 | 05 SOUTHWEST | 515136 | SUNNYSD7 | 345 | 10.3287 | 10.4719 | 0.1432
ERAS-2025-026 | 05 SOUTHWEST | 515444 | MCNOWND7 | 345 | 22.8243 | 23.0357 | 0.2114
ERAS-2025-026 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.9765 | 8.9961 | 0.0196
ERAS-2025-026 | 05 SOUTHWEST | 515549 | MNCWND37 | 345 | 14.2544 | 14.3328 | 0.0784
ERAS-2025-026 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 18.0156 | 18.4866 | 0.471
ERAS-2025-026 | 05 SOUTHWEST | 515802 | GRACMNT4 | 138 | 34.0917 | 34.3361 | 0.2444
ERAS-2025-026 | 05 SOUTHWEST | 516096 | NORMHLL7 | 345 | 27.9058 | 28.002 | 0.0962
ERAS-2025-026 | 05 SOUTHWEST | 520814 | ANADARK4 | 138 | 37.3913 | 37.5982 | 0.2069
ERAS-2025-026 | 05 SOUTHWEST | 521089 | WASHITA4 | 138 | 30.3416 | 30.5162 | 0.1746
ERAS-2025-026 | 05 SOUTHWEST | 525750 | G18-015-TAP | 345 | 5.8567 | 5.9147 | 0.058
ERAS-2025-026 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 28.9461 | 28.977 | 0.0309
ERAS-2025-026 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.3422 | 22.4092 | 0.067
ERAS-2025-026 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.2213 | 10.2557 | 0.0344
ERAS-2025-026 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 22.0195 | 22.0844 | 0.0649
ERAS-2025-026 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 21.9985 | 22.0634 | 0.0649
ERAS-2025-026 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.4723 | 19.5398 | 0.0675
ERAS-2025-026 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.3594 | 8.3822 | 0.0228
ERAS-2025-026 | 05 SOUTHWEST | 529304 | OMDUNCN4 | 138 | 6.9922 | 7.0342 | 0.042
ERAS-2025-026 | 05 SOUTHWEST | 560088 | G17-075-TAP | 345 | 6.7555 | 6.7882 | 0.0327
ERAS-2025-026 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
ERAS-2025-026 | 05 SOUTHWEST | 599892 | OKLAUN2 | 345 | 4.2384 | 4.2384 | 0
ERAS-2025-026 | 05 SOUTHWEST | 760938 | G17-171-TAP | 345 | 10.7019 | 11.4086 | 0.7067
ERAS-2025-026 | 05 SOUTHWEST | 760939 | GEN-2017-171 | 345 | 10.6421 | 11.3407 | 0.6986
ERAS-2025-026 | 05 SOUTHWEST | 761250 | GEN-2017-233 | 345 | 22.1469 | 22.3459 | 0.199
ERAS-2025-026 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.0954 | 7.1112 | 0.0158
ERAS-2025-026 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.8449 | 5.9027 | 0.0578
ERAS-2025-026 | 05 SOUTHWEST | 762900 | GEN-2018-055 | 345 | 5.9153 | 6.0616 | 0.1463
ERAS-2025-026 | 05 SOUTHWEST | 763318 | GEN-2018-115 | 345 | 13.3581 | 14.8472 | 1.4891
ERAS-2025-026 | 05 SOUTHWEST | 788837 | ERA-24 | 138 | 18.9474 | 19.4419 | 0.4945
ERAS-2025-026 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.5449 | 13.5691 | 0.0242
ERAS-2025-026 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9625 | 8.9668 | 0.0043
ERAS-2025-026 | 05 SOUTHWEST | 789744 | ERA-2025-26 | 345 | 11.8386 | 13.5407 | 1.7021
ERAS-2025-027 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.691 | 10.6924 | 0.0014
ERAS-2025-027 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4742 | 25.4894 | 0.0152
ERAS-2025-027 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7549 | 33.7794 | 0.0245
ERAS-2025-027 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.6098 | 14.6161 | 0.0063
ERAS-2025-027 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.511 | 11.5246 | 0.0136
ERAS-2025-027 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5846 | 11.5984 | 0.0138
ERAS-2025-027 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5846 | 11.5984 | 0.0138
ERAS-2025-027 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0033 | 6.0045 | 0.0012
ERAS-2025-027 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.0861 | 28.977 | -0.1091
ERAS-2025-027 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.443 | 22.4092 | -0.0338
ERAS-2025-027 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 12.4591 | 12.4798 | 0.0207
ERAS-2025-027 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0007 | 12.037 | 0.0363
ERAS-2025-027 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5591 | 10.5982 | 0.0391
ERAS-2025-027 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8416 | 13.8496 | 0.008
ERAS-2025-027 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1397 | 11.1636 | 0.0239
ERAS-2025-027 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.4244 | 16.0403 | 0.6159
ERAS-2025-027 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3658 | 6.3791 | 0.0133
ERAS-2025-027 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.6452 | 10.6988 | 0.0536
ERAS-2025-027 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.45 | 19.6594 | 0.2094
ERAS-2025-027 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 20.3994 | 21.058 | 0.6586
ERAS-2025-027 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.0973 | 11.1838 | 0.0865
ERAS-2025-027 | 05 SOUTHWEST | 526943 | LG-PLAINS +3 | 115 | 8.48 | 8.5108 | 0.0308
ERAS-2025-027 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.9103 | 16.6979 | 0.7876
ERAS-2025-027 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.7664 | 16.5394 | 0.773
ERAS-2025-027 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.507 | 16.4047 | 0.8977
ERAS-2025-027 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.5073 | 14.5944 | 0.0871
ERAS-2025-027 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2406 | 13.292 | 0.0514
ERAS-2025-027 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.2439 | 12.3553 | 0.1114
ERAS-2025-027 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.6796 | 12.7282 | 0.0486
ERAS-2025-027 | 05 SOUTHWEST | 527036 | SHELL_C2 3 | 115 | 15.5422 | 15.6211 | 0.0789
ERAS-2025-027 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.4028 | 14.4892 | 0.0864
ERAS-2025-027 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.4922 | 11.547 | 0.0548
ERAS-2025-027 | 05 SOUTHWEST | 527051 | ODC_TP 3 | 115 | 14.5244 | 14.6117 | 0.0873
ERAS-2025-027 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 17.5543 | 17.6712 | 0.1169
ERAS-2025-027 | 05 SOUTHWEST | 527080 | EL_PASO 3 | 115 | 17.2669 | 17.3786 | 0.1117
ERAS-2025-027 | 05 SOUTHWEST | 527105 | SAN_ANDS_TP3 | 115 | 18.1715 | 18.2893 | 0.1178
ERAS-2025-027 | 05 SOUTHWEST | 527107 | SANSEMTP | 115 | 11.4959 | 11.5515 | 0.0556
ERAS-2025-027 | 05 SOUTHWEST | 527125 | DENVER_CTY 2 | 69 | 8.7907 | 8.8065 | 0.0158
ERAS-2025-027 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 23.4293 | 23.6193 | 0.19
ERAS-2025-027 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 23.4293 | 23.6193 | 0.19
ERAS-2025-027 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.9911 | 25.2143 | 0.2232
ERAS-2025-027 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.1219 | 17.6642 | 0.5423
ERAS-2025-027 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.1219 | 17.6642 | 0.5423
ERAS-2025-027 | 05 SOUTHWEST | 527193 | LG-PLSHILL+3 | 115 | 8.344 | 8.3706 | 0.0266
ERAS-2025-027 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.328 | 8.3545 | 0.0265
ERAS-2025-027 | 05 SOUTHWEST | 527201 | SEAGRAVES 2 | 69 | 5.6819 | 5.619 | -0.0629
ERAS-2025-027 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.6221 | 9.6546 | 0.0325
ERAS-2025-027 | 05 SOUTHWEST | 527238 | ROZ 3 | 115 | 11.4927 | 11.5585 | 0.0658
ERAS-2025-027 | 05 SOUTHWEST | 527242 | AMERADA 3 | 115 | 11.6375 | 11.705 | 0.0675
ERAS-2025-027 | 05 SOUTHWEST | 527257 | FLATLAND 3 | 115 | 7.0156 | 7.028 | 0.0124
ERAS-2025-027 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.7477 | 14.8564 | 0.1087
ERAS-2025-027 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.7086 | 8.8063 | 0.0977
ERAS-2025-027 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.8576 | 10.8825 | 0.0249
ERAS-2025-027 | 05 SOUTHWEST | 527322 | GAINES 3 | 115 | 10.5314 | 10.5712 | 0.0398
ERAS-2025-027 | 05 SOUTHWEST | 527340 | DOSS 3 | 115 | 8.4984 | 8.5298 | 0.0314
ERAS-2025-027 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 22.4544 | 22.4838 | 0.0294
ERAS-2025-027 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 37.3131 | 37.3663 | 0.0532
ERAS-2025-027 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 25.9432 | 25.9982 | 0.055
ERAS-2025-027 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.9321 | 20.972 | 0.0399
ERAS-2025-027 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.3721 | 9.3913 | 0.0192
ERAS-2025-027 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 6.0211 | 6.0311 | 0.01
ERAS-2025-027 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.9941 | 14.7112 | 0.7171
ERAS-2025-027 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.6319 | 14.6359 | 0.004
ERAS-2025-027 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.331 | 10.4059 | 0.0749
ERAS-2025-027 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0612 | 33.0847 | 0.0235
ERAS-2025-027 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 16.7935 | 16.8295 | 0.036
ERAS-2025-027 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.8661 | 16.9025 | 0.0364
ERAS-2025-027 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9477 | 8.9668 | 0.0191
ERAS-2025-027 | 05 SOUTHWEST | 788945 | ERA-2025-27 | 230 | 14.3109 | 15.2131 | 0.9022
ERAS-2025-027 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.942 | 8.9611 | 0.0191
ERAS-2025-028 | 05 SOUTHWEST | 500001 | COMANC7_TAP | 345 | 13.6653 | 13.6679 | 0.0026
ERAS-2025-028 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 7.6238 | 7.6304 | 0.0066
ERAS-2025-028 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 11.6031 | 11.6004 | -0.0027
ERAS-2025-028 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 7.5929 | 7.5994 | 0.0065
ERAS-2025-028 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.6238 | 7.6304 | 0.0066
ERAS-2025-028 | 05 SOUTHWEST | 511607 | O.K.U.3-7 | 345 | 7.6238 | 7.6304 | 0.0066
ERAS-2025-028 | 05 SOUTHWEST | 511999 | DVRSION-WIND | 345 | 4.9587 | 4.9613 | 0.0026
ERAS-2025-028 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 23.1939 | 23.142 | -0.0519
ERAS-2025-028 | 05 SOUTHWEST | 515378 | WWRDEHV9 | 765 | 5.4183 | 5.3665 | -0.0518
ERAS-2025-028 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.994 | 8.9961 | 0.0021
ERAS-2025-028 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 11.6202 | 11.6175 | -0.0027
ERAS-2025-028 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3198 | 17.334 | 0.0142
ERAS-2025-028 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 30.058 | 30.063 | 0.005
ERAS-2025-028 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.208 | 16.2097 | 0.0017
ERAS-2025-028 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.8418 | 17.8428 | 0.001
ERAS-2025-028 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 15.1718 | 15.1733 | 0.0015
ERAS-2025-028 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 7.14 | 7.1406 | 0.0006
ERAS-2025-028 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.943 | 8.9439 | 0.0009
ERAS-2025-028 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.3412 | 11.3421 | 0.0009
ERAS-2025-028 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6908 | 10.6924 | 0.0016
ERAS-2025-028 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.4156 | 12.416 | 0.0004
ERAS-2025-028 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.7792 | 11.7795 | 0.0003
ERAS-2025-028 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2232 | 11.2233 | 0.0001
ERAS-2025-028 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.9015 | 6.9015 | 0
ERAS-2025-028 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.9744 | 7.9748 | 0.0004
ERAS-2025-028 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9496 | 6.9496 | 0
ERAS-2025-028 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.8465 | 10.8468 | 0.0003
ERAS-2025-028 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.1967 | 15.198 | 0.0013
ERAS-2025-028 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.9633 | 11.965 | 0.0017
ERAS-2025-028 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.9734 | 15.9758 | 0.0024
ERAS-2025-028 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4749 | 25.4894 | 0.0145
ERAS-2025-028 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7534 | 33.7794 | 0.026
ERAS-2025-028 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.6046 | 14.6161 | 0.0115
ERAS-2025-028 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.5178 | 11.5246 | 0.0068
ERAS-2025-028 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5916 | 11.5984 | 0.0068
ERAS-2025-028 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5916 | 11.5984 | 0.0068
ERAS-2025-028 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.7736 | 8.7749 | 0.0013
ERAS-2025-028 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0035 | 6.0045 | 0.001
ERAS-2025-028 | 05 SOUTHWEST | 525731 | SP-ABERNTH+2 | 69 | 3.0537 | 3.0536 | -0.0001
ERAS-2025-028 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.6294 | 2.6294 | 0
ERAS-2025-028 | 05 SOUTHWEST | 525750 | G18-015-TAP | 345 | 5.9076 | 5.9147 | 0.0071
ERAS-2025-028 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.1956 | 6.1954 | -0.0002
ERAS-2025-028 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.4952 | 5.4951 | -0.0001
ERAS-2025-028 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0931 | 7.0928 | -0.0003
ERAS-2025-028 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 6.1449 | 6.1447 | -0.0002
ERAS-2025-028 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.5236 | 4.5234 | -0.0002
ERAS-2025-028 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.951 | 7.9502 | -0.0008
ERAS-2025-028 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.7604 | 21.7514 | -0.009
ERAS-2025-028 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.0444 | 28.977 | -0.0674
ERAS-2025-028 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 29.0444 | 28.977 | -0.0674
ERAS-2025-028 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.1565 | 22.4092 | 0.2527
ERAS-2025-028 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.2132 | 10.2557 | 0.0425
ERAS-2025-028 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.7405 | 28.6746 | -0.0659
ERAS-2025-028 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 21.8396 | 22.0844 | 0.2448
ERAS-2025-028 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 21.8188 | 22.0634 | 0.2446
ERAS-2025-028 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7175 | 2.7174 | -0.0001
ERAS-2025-028 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.8634 | 3.8632 | -0.0002
ERAS-2025-028 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.3705 | 13.3594 | -0.0111
ERAS-2025-028 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.4343 | 19.5398 | 0.1055
ERAS-2025-028 | 05 SOUTHWEST | 526001 | CRWFSHDRW9 | 765 | 8.352 | 8.3822 | 0.0302
ERAS-2025-028 | 05 SOUTHWEST | 526108 | SP-ERSKINE+3 | 115 | 12.4451 | 12.446 | 0.0009
ERAS-2025-028 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 12.4245 | 12.4254 | 0.0009
ERAS-2025-028 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.7318 | 2.7318 | 0
ERAS-2025-028 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.8297 | 14.8312 | 0.0015
ERAS-2025-028 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.5586 | 11.5594 | 0.0008
ERAS-2025-028 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.8853 | 12.8871 | 0.0018
ERAS-2025-028 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.6172 | 11.618 | 0.0008
ERAS-2025-028 | 05 SOUTHWEST | 526241 | SP-LEPRINO 3 | 115 | 13.219 | 13.2185 | -0.0005
ERAS-2025-028 | 05 SOUTHWEST | 526242 | SP-LPRNO_TP3 | 115 | 14.2689 | 14.2684 | -0.0005
ERAS-2025-028 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.4103 | 19.4105 | 0.0002
ERAS-2025-028 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.8071 | 16.808 | 0.0009
ERAS-2025-028 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.7965 | 15.7959 | -0.0006
ERAS-2025-028 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.323 | 12.3228 | -0.0002
ERAS-2025-028 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.9513 | 18.9511 | -0.0002
ERAS-2025-028 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 12.4725 | 12.4798 | 0.0073
ERAS-2025-028 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0228 | 12.037 | 0.0142
ERAS-2025-028 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5844 | 10.5982 | 0.0138
ERAS-2025-028 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.8586 | 12.8621 | 0.0035
ERAS-2025-028 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.844 | 13.8496 | 0.0056
ERAS-2025-028 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.4106 | 7.4106 | 0
ERAS-2025-028 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6091 | 6.6091 | 0
ERAS-2025-028 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1729 | 5.1729 | 0
ERAS-2025-028 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1565 | 11.1636 | 0.0071
ERAS-2025-028 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.9803 | 16.0403 | 0.06
ERAS-2025-028 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3756 | 6.3791 | 0.0035
ERAS-2025-028 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.686 | 10.6988 | 0.0128
ERAS-2025-028 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.6104 | 19.6594 | 0.049
ERAS-2025-028 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 20.8956 | 21.058 | 0.1624
ERAS-2025-028 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 10.8662 | 11.1838 | 0.3176
ERAS-2025-028 | 05 SOUTHWEST | 526943 | LG-PLAINS +3 | 115 | 8.5033 | 8.5108 | 0.0075
ERAS-2025-028 | 05 SOUTHWEST | 527000 | ERAS-014 | 345 | 12.1643 | 12.1878 | 0.0235
ERAS-2025-028 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.6169 | 16.6979 | 0.081
ERAS-2025-028 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 16.46 | 16.5394 | 0.0794
ERAS-2025-028 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 16.3326 | 16.4047 | 0.0721
ERAS-2025-028 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.5764 | 14.5944 | 0.018
ERAS-2025-028 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 13.4408 | 13.4726 | 0.0318
ERAS-2025-028 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.2783 | 13.292 | 0.0137
ERAS-2025-028 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.3217 | 12.3553 | 0.0336
ERAS-2025-028 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.7164 | 12.7282 | 0.0118
ERAS-2025-028 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.4712 | 14.4892 | 0.018
ERAS-2025-028 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.5356 | 11.547 | 0.0114
ERAS-2025-028 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 17.6481 | 17.6712 | 0.0231
ERAS-2025-028 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 23.5826 | 23.6193 | 0.0367
ERAS-2025-028 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 23.5826 | 23.6193 | 0.0367
ERAS-2025-028 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.174 | 25.2143 | 0.0403
ERAS-2025-028 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.5994 | 17.6642 | 0.0648
ERAS-2025-028 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.5994 | 17.6642 | 0.0648
ERAS-2025-028 | 05 SOUTHWEST | 527193 | LG-PLSHILL+3 | 115 | 8.3648 | 8.3706 | 0.0058
ERAS-2025-028 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3487 | 8.3545 | 0.0058
ERAS-2025-028 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.6477 | 9.6546 | 0.0069
ERAS-2025-028 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.8395 | 14.8564 | 0.0169
ERAS-2025-028 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.7933 | 8.8063 | 0.013
ERAS-2025-028 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.6154 | 14.6393 | 0.0239
ERAS-2025-028 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.296 | 14.3216 | 0.0256
ERAS-2025-028 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8665 | 17.9042 | 0.0377
ERAS-2025-028 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9399 | 7.9551 | 0.0152
ERAS-2025-028 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.6587 | 9.6583 | -0.0004
ERAS-2025-028 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 22.4521 | 22.4838 | 0.0317
ERAS-2025-028 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 37.3276 | 37.3663 | 0.0387
ERAS-2025-028 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 25.9393 | 25.9982 | 0.0589
ERAS-2025-028 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.8658 | 20.972 | 0.1062
ERAS-2025-028 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 14.0929 | 14.1206 | 0.0277
ERAS-2025-028 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9281 | 7.9519 | 0.0238
ERAS-2025-028 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.2095 | 17.26 | 0.0505
ERAS-2025-028 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 37.7353 | 37.8262 | 0.0909
ERAS-2025-028 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 14.9358 | 14.9797 | 0.0439
ERAS-2025-028 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.3857 | 9.3913 | 0.0056
ERAS-2025-028 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 32.9183 | 32.9729 | 0.0546
ERAS-2025-028 | 05 SOUTHWEST | 528400 | LEANTL_345 | 345 | 12.9722 | 12.9985 | 0.0263
ERAS-2025-028 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 9.5117 | 9.5272 | 0.0155
ERAS-2025-028 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 6.0288 | 6.0311 | 0.0023
ERAS-2025-028 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
ERAS-2025-028 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.6908 | 10.6924 | 0.0016
ERAS-2025-028 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.1375 | 8.1385 | 0.001
ERAS-2025-028 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 14.654 | 14.7112 | 0.0572
ERAS-2025-028 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.6316 | 14.6359 | 0.0043
ERAS-2025-028 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.0917 | 7.1112 | 0.0195
ERAS-2025-028 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.8957 | 5.9027 | 0.007
ERAS-2025-028 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.611 | 11.6126 | 0.0016
ERAS-2025-028 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.5436 | 9.5449 | 0.0013
ERAS-2025-028 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.1304 | 10.4059 | 0.2755
ERAS-2025-028 | 05 SOUTHWEST | 788703 | ERA-02 | 345 | 21.4837 | 21.7204 | 0.2367
ERAS-2025-028 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0598 | 33.0847 | 0.0249
ERAS-2025-028 | 05 SOUTHWEST | 788790 | ERA-20 | 345 | 16.7247 | 16.8295 | 0.1048
ERAS-2025-028 | 05 SOUTHWEST | 788810 | ERA-21 | 345 | 11.6888 | 11.7471 | 0.0583
ERAS-2025-028 | 05 SOUTHWEST | 788817 | ERA-21-MPT1 | 345 | 10.2111 | 10.2549 | 0.0438
ERAS-2025-028 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.7967 | 16.9025 | 0.1058
ERAS-2025-028 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.4894 | 13.5691 | 0.0797
ERAS-2025-028 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.144 | 8.9668 | 0.8228
ERAS-2025-028 | 05 SOUTHWEST | 788945 | ERA-2025-27 | 230 | 15.1517 | 15.2131 | 0.0614
ERAS-2025-028 | 05 SOUTHWEST | 788955 | ERA-28 | 345 | 8.1383 | 8.9611 | 0.8228
ERAS-2025-028 | 05 SOUTHWEST | 789905 | ERAS-36-TAP | 230 | 10.5251 | 10.5266 | 0.0015
ERAS-2025-030 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.3035 | 17.334 | 0.0305
ERAS-2025-030 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 7.6442 | 7.6581 | 0.0139
ERAS-2025-030 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5358 | 10.5925 | 0.0567
ERAS-2025-030 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 7.0809 | 7.1406 | 0.0597
ERAS-2025-030 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.7205 | 6.7487 | 0.0282
ERAS-2025-030 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.1986 | 8.2369 | 0.0383
ERAS-2025-030 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.2439 | 10.314 | 0.0701
ERAS-2025-030 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.8079 | 8.9439 | 0.136
ERAS-2025-030 | 05 SOUTHWEST | 524885 | SN_JUAN_SS 6 | 230 | 4.2855 | 4.5686 | 0.2831
ERAS-2025-030 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.0307 | 4.2777 | 0.247
ERAS-2025-030 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.2755 | 11.3421 | 0.0666
ERAS-2025-030 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.5785 | 10.6924 | 0.1139
ERAS-2025-030 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.8441 | 7.8813 | 0.0372
ERAS-2025-030 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.6585 | 33.7794 | 0.1209
ERAS-2025-030 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.575 | 14.6161 | 0.0411
ERAS-2025-030 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 13.4213 | 13.4726 | 0.0513
ERAS-2025-030 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.3391 | 12.3553 | 0.0162
ERAS-2025-030 | 05 SOUTHWEST | 527455 | RSWL_SLRCOL3 | 115 | 6.5496 | 7.611 | 1.0614
ERAS-2025-030 | 05 SOUTHWEST | 527470 | CHVS_SLRCOL3 | 115 | 6.4234 | 7.4387 | 1.0153
ERAS-2025-030 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 6.6196 | 7.7061 | 1.0865
ERAS-2025-030 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.3888 | 5.5405 | 1.1517
ERAS-2025-030 | 05 SOUTHWEST | 527501 | URTON 3 | 115 | 5.7005 | 6.4442 | 0.7437
ERAS-2025-030 | 05 SOUTHWEST | 527508 | PRICE 3 | 115 | 4.7686 | 5.2848 | 0.5162
ERAS-2025-030 | 05 SOUTHWEST | 527509 | PRICE_TAP 3 | 115 | 5.3079 | 5.9582 | 0.6503
ERAS-2025-030 | 05 SOUTHWEST | 527522 | ROSWELL_CTY3 | 115 | 5.5018 | 6.1589 | 0.6571
ERAS-2025-030 | 05 SOUTHWEST | 527533 | SW4J795_E 3 | 115 | 5.6532 | 6.3191 | 0.6659
ERAS-2025-030 | 05 SOUTHWEST | 527534 | SW4J795_W 3 | 115 | 5.7213 | 6.4052 | 0.6839
ERAS-2025-030 | 05 SOUTHWEST | 527541 | CAPITAN 3 | 115 | 4.6706 | 5.1365 | 0.4659
ERAS-2025-030 | 05 SOUTHWEST | 527546 | SAMSON 3 | 115 | 5.423 | 6.0598 | 0.6368
ERAS-2025-030 | 05 SOUTHWEST | 527563 | ROSWLL_INT 2 | 69 | 4.1982 | 4.3946 | 0.1964
ERAS-2025-030 | 05 SOUTHWEST | 527564 | ROSWLL_INT 3 | 115 | 5.7264 | 6.4112 | 0.6848
ERAS-2025-030 | 05 SOUTHWEST | 527597 | TWEEDY 3 | 115 | 5.341 | 5.8896 | 0.5486
ERAS-2025-030 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 14.5705 | 14.6393 | 0.0688
ERAS-2025-030 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.5705 | 14.6393 | 0.0688
ERAS-2025-030 | 05 SOUTHWEST | 527640 | MILO_WIND 7 | 345 | 14.2523 | 14.3216 | 0.0693
ERAS-2025-030 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 11.7607 | 11.8082 | 0.0475
ERAS-2025-030 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.2523 | 14.3216 | 0.0693
ERAS-2025-030 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.7956 | 17.9042 | 0.1086
ERAS-2025-030 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9237 | 7.9551 | 0.0314
ERAS-2025-030 | 05 SOUTHWEST | 527678 | SMITH 2 | 69 | 6.3202 | 6.3768 | 0.0566
ERAS-2025-030 | 05 SOUTHWEST | 527710 | EAGLE_CREEK2 | 69 | 6.332 | 6.3889 | 0.0569
ERAS-2025-030 | 05 SOUTHWEST | 527711 | EAGLE_CREEK3 | 115 | 8.1357 | 8.3037 | 0.168
ERAS-2025-030 | 05 SOUTHWEST | 527715 | NAVAJO_2TP 3 | 115 | 7.74 | 7.892 | 0.152
ERAS-2025-030 | 05 SOUTHWEST | 527717 | NAVAJO_2 3 | 115 | 7.6445 | 7.7927 | 0.1482
ERAS-2025-030 | 05 SOUTHWEST | 527720 | NAVAJO_3 3 | 115 | 7.6933 | 7.8434 | 0.1501
ERAS-2025-030 | 05 SOUTHWEST | 527733 | NAVAJO_1 2 | 69 | 5.3849 | 5.4267 | 0.0418
ERAS-2025-030 | 05 SOUTHWEST | 527736 | NAVAJO_5TP 3 | 115 | 7.6946 | 7.8447 | 0.1501
ERAS-2025-030 | 05 SOUTHWEST | 527739 | NAVAJO_4 3 | 115 | 7.6759 | 7.8253 | 0.1494
ERAS-2025-030 | 05 SOUTHWEST | 527743 | NAVAJO_5 3 | 115 | 7.6784 | 7.8279 | 0.1495
ERAS-2025-030 | 05 SOUTHWEST | 527757 | ARTESIA_TP 2 | 69 | 5.2714 | 5.3116 | 0.0402
ERAS-2025-030 | 05 SOUTHWEST | 527777 | ARTSA_CC_TP3 | 115 | 7.4593 | 7.5963 | 0.137
ERAS-2025-030 | 05 SOUTHWEST | 527778 | ARTESIA_CC 3 | 115 | 5.9717 | 6.0587 | 0.087
ERAS-2025-030 | 05 SOUTHWEST | 527782 | CV-HOPE_TP 3 | 115 | 7.6419 | 7.7853 | 0.1434
ERAS-2025-030 | 05 SOUTHWEST | 527785 | ATOKA 2 | 69 | 2.3514 | 2.3589 | 0.0075
ERAS-2025-030 | 05 SOUTHWEST | 527786 | ATOKA 3 | 115 | 7.9943 | 8.1509 | 0.1566
ERAS-2025-030 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 13.4386 | 13.9753 | 0.5367
ERAS-2025-030 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 13.4386 | 13.9753 | 0.5367
ERAS-2025-030 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 11.2596 | 11.9931 | 0.7335
ERAS-2025-030 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.4211 | 9.6583 | 0.2372
ERAS-2025-030 | 05 SOUTHWEST | 527809 | CV-8_MILE 3 | 115 | 5.961 | 6.0604 | 0.0994
ERAS-2025-030 | 05 SOUTHWEST | 527811 | CV-KEWAN_TP3 | 115 | 3.153 | 3.1811 | 0.0281
ERAS-2025-030 | 05 SOUTHWEST | 527821 | CV-DAYTON +3 | 115 | 7.8837 | 8.0384 | 0.1547
ERAS-2025-030 | 05 SOUTHWEST | 527822 | CV-TURKYTRK3 | 115 | 3.7297 | 3.7689 | 0.0392
ERAS-2025-030 | 05 SOUTHWEST | 527845 | C1_MPT_PRI 3 | 115 | 11.0161 | 11.0268 | 0.0107
ERAS-2025-030 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 33.3625 | 33.4572 | 0.0947
ERAS-2025-030 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 22.3013 | 22.4838 | 0.1825
ERAS-2025-030 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 22.3013 | 22.4838 | 0.1825
ERAS-2025-030 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 37.261 | 37.3663 | 0.1053
ERAS-2025-030 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 25.8178 | 25.9982 | 0.1804
ERAS-2025-030 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.8044 | 20.972 | 0.1676
ERAS-2025-030 | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 15.0674 | 15.1678 | 0.1004
ERAS-2025-030 | 05 SOUTHWEST | 527961 | POTASH_JCT 2 | 69 | 10.446 | 10.4731 | 0.0271
ERAS-2025-030 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 22.1919 | 22.4009 | 0.209
ERAS-2025-030 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 9.2135 | 9.3131 | 0.0996
ERAS-2025-030 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 13.927 | 14.1206 | 0.1936
ERAS-2025-030 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 22.299 | 22.5054 | 0.2064
ERAS-2025-030 | 05 SOUTHWEST | 527970 | MAGNUM 3 | 115 | 9.3827 | 9.4434 | 0.0607
ERAS-2025-030 | 05 SOUTHWEST | 527999 | INTREPDW_TP3 | 115 | 17.5493 | 17.6726 | 0.1233
ERAS-2025-030 | 05 SOUTHWEST | 528003 | CV-DAGGR&IH2 | 69 | 1.7202 | 1.7234 | 0.0032
ERAS-2025-030 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9175 | 7.9519 | 0.0344
ERAS-2025-030 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 17.1809 | 17.26 | 0.0791
ERAS-2025-030 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 37.6072 | 37.8262 | 0.219
ERAS-2025-030 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 14.8734 | 14.9797 | 0.1063
ERAS-2025-030 | 05 SOUTHWEST | 528070 | CV-AZMESA 3 | 115 | 8.2479 | 8.356 | 0.1081
ERAS-2025-030 | 05 SOUTHWEST | 528076 | CV-WALTCYN 3 | 115 | 4.9085 | 4.9469 | 0.0384
ERAS-2025-030 | 05 SOUTHWEST | 528093 | 7-RIVERS 2 | 69 | 2.5133 | 2.5197 | 0.0064
ERAS-2025-030 | 05 SOUTHWEST | 528094 | 7-RIVERS 3 | 115 | 9.1825 | 9.3379 | 0.1554
ERAS-2025-030 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 7.4819 | 7.6728 | 0.1909
ERAS-2025-030 | 05 SOUTHWEST | 528109 | CV-LAKEWOOD3 | 115 | 7.0958 | 7.2034 | 0.1076
ERAS-2025-030 | 05 SOUTHWEST | 528116 | CV-IRISHHL+3 | 115 | 7.1365 | 7.2518 | 0.1153
ERAS-2025-030 | 05 SOUTHWEST | 528132 | OCOTILLO 3 | 115 | 6.9574 | 7.0067 | 0.0493
ERAS-2025-030 | 05 SOUTHWEST | 528134 | SISKO_TP 3 | 115 | 8.0635 | 8.1299 | 0.0664
ERAS-2025-030 | 05 SOUTHWEST | 528135 | CAVEMAN 3 | 115 | 7.7696 | 7.8449 | 0.0753
ERAS-2025-030 | 05 SOUTHWEST | 528136 | CAVEMAN_TP 3 | 115 | 9.3014 | 9.41 | 0.1086
ERAS-2025-030 | 05 SOUTHWEST | 528137 | N_CANAL 3 | 115 | 10.0415 | 10.143 | 0.1015
ERAS-2025-030 | 05 SOUTHWEST | 528151 | FIESTA 3 | 115 | 11.4667 | 11.5882 | 0.1215
ERAS-2025-030 | 05 SOUTHWEST | 528159 | CARLSBAD 2 | 69 | 4.9225 | 4.9343 | 0.0118
ERAS-2025-030 | 05 SOUTHWEST | 528160 | CARLSBAD 3 | 115 | 13.4262 | 13.5933 | 0.1671
ERAS-2025-030 | 05 SOUTHWEST | 528178 | PECOS 3 | 115 | 14.2115 | 14.4164 | 0.2049
ERAS-2025-030 | 05 SOUTHWEST | 528179 | PECOS 6 | 230 | 8.0362 | 8.1611 | 0.1249
ERAS-2025-030 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 19.6575 | 19.7366 | 0.0791
ERAS-2025-030 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 11.2519 | 11.3389 | 0.087
ERAS-2025-030 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 11.9182 | 11.9835 | 0.0653
ERAS-2025-030 | 05 SOUTHWEST | 528226 | HOPI_SUB 3 | 115 | 8.6347 | 8.6726 | 0.0379
ERAS-2025-030 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 9.152 | 9.1585 | 0.0065
ERAS-2025-030 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 31.8799 | 31.9549 | 0.075
ERAS-2025-030 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 16.5002 | 16.5769 | 0.0767
ERAS-2025-030 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 32.6826 | 32.9729 | 0.2903
ERAS-2025-030 | 05 SOUTHWEST | 528400 | LEANTL_345 | 345 | 12.8608 | 12.9985 | 0.1377
ERAS-2025-030 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 11.3204 | 11.332 | 0.0116
ERAS-2025-030 | 05 SOUTHWEST | 599951 | LAMAR 6 | 345 | 60.6375 | 60.6375 | 0
ERAS-2025-030 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.5785 | 10.6924 | 0.1139
ERAS-2025-030 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 11.2596 | 11.9931 | 0.7335
ERAS-2025-030 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.4549 | 9.5449 | 0.09
ERAS-2025-030 | 05 SOUTHWEST | 788772 | ERA-18 | 230 | 7.919 | 8.0249 | 0.1059
ERAS-2025-030 | 05 SOUTHWEST | 788939 | ERA-20-TAP | 345 | 16.8094 | 16.9025 | 0.0931
ERAS-2025-030 | 05 SOUTHWEST | 788971 | ERA-30 | 230 | 4.6125 | 6.4996 | 1.8871
ERAS-2025-030 | 05 SOUTHWEST | 789915 | ERA-030-TAP | 230 | 4.6223 | 6.5088 | 1.8865
ERAS-2025-030 | 05 SOUTHWEST | 999997 | DUMMY | 230 | 4.6223 | 6.5088 | 1.8865
ERAS-2025-036 | 05 SOUTHWEST | 511584 | O.K.U.2-7 | 345 | 7.6305 | 7.6304 | -0.0001
ERAS-2025-036 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 14.8812 | 14.8848 | 0.0036
ERAS-2025-036 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.4495 | 12.452 | 0.0025
ERAS-2025-036 | 05 SOUTHWEST | 515634 | PALDR1W7 | 345 | 11.1026 | 11.1044 | 0.0018
ERAS-2025-036 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 14.2181 | 14.2206 | 0.0025
ERAS-2025-036 | 05 SOUTHWEST | 522800 | MU-TULIA 3 | 115 | 5.4865 | 5.4884 | 0.0019
ERAS-2025-036 | 05 SOUTHWEST | 523019 | OSLO-SYLVIE7 | 345 | 10.6203 | 10.6229 | 0.0026
ERAS-2025-036 | 05 SOUTHWEST | 523020 | SYLVIE 7 | 345 | 10.6203 | 10.6229 | 0.0026
ERAS-2025-036 | 05 SOUTHWEST | 523030 | OLSO 7 | 345 | 10.6203 | 10.6229 | 0.0026
ERAS-2025-036 | 05 SOUTHWEST | 523040 | OLYMPIA7 | 345 | 15.035 | 15.0407 | 0.0057
ERAS-2025-036 | 05 SOUTHWEST | 523041 | FRWLN7 | 345 | 12.1351 | 12.1388 | 0.0037
ERAS-2025-036 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 16.7568 | 16.7582 | 0.0014
ERAS-2025-036 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 15.5705 | 15.5755 | 0.005
ERAS-2025-036 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 15.3427 | 15.3487 | 0.006
ERAS-2025-036 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 12.2408 | 12.2417 | 0.0009
ERAS-2025-036 | 05 SOUTHWEST | 523131 | GRPLNS-HV2-3 | 115 | 11.4528 | 11.4536 | 0.0008
ERAS-2025-036 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.6602 | 4.6603 | 0.0001
ERAS-2025-036 | 05 SOUTHWEST | 523177 | RB-SPURLCK+3 | 115 | 6.3543 | 6.3563 | 0.002
ERAS-2025-036 | 05 SOUTHWEST | 523186 | SPEARMAN 3 | 115 | 9.571 | 9.5724 | 0.0014
ERAS-2025-036 | 05 SOUTHWEST | 523218 | RB-FARIA 3 | 115 | 5.882 | 5.8841 | 0.0021
ERAS-2025-036 | 05 SOUTHWEST | 523220 | XIT_INTG 3 | 115 | 7.3682 | 7.3722 | 0.004
ERAS-2025-036 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 6.1526 | 6.1589 | 0.0063
ERAS-2025-036 | 05 SOUTHWEST | 523222 | RB-WOLVES | 115 | 6.9503 | 6.9538 | 0.0035
ERAS-2025-036 | 05 SOUTHWEST | 523228 | DALLAM 3 | 115 | 7.3158 | 7.3196 | 0.0038
ERAS-2025-036 | 05 SOUTHWEST | 523256 | ETTER 3 | 115 | 6.8277 | 6.8304 | 0.0027
ERAS-2025-036 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 12.4363 | 12.4404 | 0.0041
ERAS-2025-036 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.58 | 4.582 | 0.002
ERAS-2025-036 | 05 SOUTHWEST | 523277 | VALERO 3 | 115 | 12.7312 | 12.7406 | 0.0094
ERAS-2025-036 | 05 SOUTHWEST | 523304 | MOORE_W 3 | 115 | 14.1203 | 14.1322 | 0.0119
ERAS-2025-036 | 05 SOUTHWEST | 523308 | MOORE_E 3 | 115 | 14.1203 | 14.1322 | 0.0119
ERAS-2025-036 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 9.2503 | 9.2621 | 0.0118
ERAS-2025-036 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 10.4176 | 10.4281 | 0.0105
ERAS-2025-036 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 10.5109 | 10.5379 | 0.027
ERAS-2025-036 | 05 SOUTHWEST | 523325 | EXELL 3 | 115 | 6.6619 | 6.666 | 0.0041
ERAS-2025-036 | 05 SOUTHWEST | 523331 | FOUR WAY 3 | 115 | 7.1711 | 7.1754 | 0.0043
ERAS-2025-036 | 05 SOUTHWEST | 523332 | EXELL_TP 3 | 115 | 8.2428 | 8.249 | 0.0062
ERAS-2025-036 | 05 SOUTHWEST | 523339 | FAIN 3 | 115 | 8.9805 | 8.9878 | 0.0073
ERAS-2025-036 | 05 SOUTHWEST | 523377 | RIVERVIEW 3 | 115 | 14.2913 | 14.2987 | 0.0074
ERAS-2025-036 | 05 SOUTHWEST | 523410 | CRMWA_#4 3 | 115 | 10.3097 | 10.3154 | 0.0057
ERAS-2025-036 | 05 SOUTHWEST | 523478 | Q_RYTON_TP 3 | 115 | 12.2343 | 12.2368 | 0.0025
ERAS-2025-036 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.9029 | 7.9092 | 0.0063
ERAS-2025-036 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 6.3261 | 6.3272 | 0.0011
ERAS-2025-036 | 05 SOUTHWEST | 523817 | MIDSTRM_TP 3 | 115 | 4.9055 | 4.9065 | 0.001
ERAS-2025-036 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.8204 | 6.8209 | 0.0005
ERAS-2025-036 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 10.668 | 10.6681 | 0.0001
ERAS-2025-036 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 5.7798 | 5.7881 | 0.0083
ERAS-2025-036 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 28.2093 | 28.515 | 0.3057
ERAS-2025-036 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 17.2622 | 17.334 | 0.0718
ERAS-2025-036 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 7.6284 | 7.6581 | 0.0297
ERAS-2025-036 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 31.1625 | 31.3157 | 0.1532
ERAS-2025-036 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 31.1625 | 31.3157 | 0.1532
ERAS-2025-036 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 31.1625 | 31.3157 | 0.1532
ERAS-2025-036 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 20.7427 | 20.7765 | 0.0338
ERAS-2025-036 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 19.822 | 19.8528 | 0.0308
ERAS-2025-036 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 23.5897 | 23.7222 | 0.1325
ERAS-2025-036 | 05 SOUTHWEST | 524016 | ASARCO 3 | 115 | 28.353 | 28.4001 | 0.0471
ERAS-2025-036 | 05 SOUTHWEST | 524018 | ASARCO_TP 3 | 115 | 30.8916 | 30.9463 | 0.0547
ERAS-2025-036 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 33.1121 | 33.1751 | 0.063
ERAS-2025-036 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 29.9269 | 30.063 | 0.1361
ERAS-2025-036 | 05 SOUTHWEST | 524058 | WHITAKER 3 | 115 | 23.4875 | 23.5227 | 0.0352
ERAS-2025-036 | 05 SOUTHWEST | 524079 | CONWAY 3 | 115 | 5.3033 | 5.3044 | 0.0011
ERAS-2025-036 | 05 SOUTHWEST | 524105 | NORTHWEST 2 | 69 | 6.063 | 6.0647 | 0.0017
ERAS-2025-036 | 05 SOUTHWEST | 524106 | NORTHWEST 3 | 115 | 12.4073 | 12.419 | 0.0117
ERAS-2025-036 | 05 SOUTHWEST | 524124 | BUSH 3 | 115 | 7.6627 | 7.6671 | 0.0044
ERAS-2025-036 | 05 SOUTHWEST | 524136 | HASTINGS 3 | 115 | 15.2235 | 15.2408 | 0.0173
ERAS-2025-036 | 05 SOUTHWEST | 524139 | ECHO 3 | 115 | 17.4825 | 17.5048 | 0.0223
ERAS-2025-036 | 05 SOUTHWEST | 524162 | EAST_PLANT 3 | 115 | 24.5333 | 24.5763 | 0.043
ERAS-2025-036 | 05 SOUTHWEST | 524163 | EAST_PLANT 6 | 230 | 15.7952 | 15.8323 | 0.0371
ERAS-2025-036 | 05 SOUTHWEST | 524243 | OUTPOST 3 | 115 | 11.092 | 11.1038 | 0.0118
ERAS-2025-036 | 05 SOUTHWEST | 524249 | SUNSET 3 | 115 | 12.7213 | 12.7336 | 0.0123
ERAS-2025-036 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 11.1046 | 11.117 | 0.0124
ERAS-2025-036 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.8766 | 10.9048 | 0.0282
ERAS-2025-036 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 5.4083 | 5.4145 | 0.0062
ERAS-2025-036 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 7.2886 | 7.3005 | 0.0119
ERAS-2025-036 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.8758 | 5.8835 | 0.0077
ERAS-2025-036 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.8758 | 5.8835 | 0.0077
ERAS-2025-036 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 22.7716 | 22.8095 | 0.0379
ERAS-2025-036 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.1702 | 16.2097 | 0.0395
ERAS-2025-036 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 16.4885 | 16.5092 | 0.0207
ERAS-2025-036 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 14.4863 | 14.5021 | 0.0158
ERAS-2025-036 | 05 SOUTHWEST | 524405 | OWENSCORN_E3 | 115 | 15.9566 | 15.9761 | 0.0195
ERAS-2025-036 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.8185 | 17.8428 | 0.0243
ERAS-2025-036 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 15.1388 | 15.1733 | 0.0345
ERAS-2025-036 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.7729 | 6.7764 | 0.0035
ERAS-2025-036 | 05 SOUTHWEST | 524560 | ARNOT 3 | 115 | 11.9545 | 11.967 | 0.0125
ERAS-2025-036 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 12.2316 | 12.2397 | 0.0081
ERAS-2025-036 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 12.2363 | 12.2444 | 0.0081
ERAS-2025-036 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.4447 | 8.453 | 0.0083
ERAS-2025-036 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.564 | 12.5726 | 0.0086
ERAS-2025-036 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 2.785 | 2.7854 | 0.0004
ERAS-2025-036 | 05 SOUTHWEST | 524733 | DS-#21 +3 | 115 | 10.9926 | 10.9981 | 0.0055
ERAS-2025-036 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 9.1123 | 9.1146 | 0.0023
ERAS-2025-036 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 11.8101 | 11.8164 | 0.0063
ERAS-2025-036 | 05 SOUTHWEST | 524748 | DS-#26 3 | 115 | 10.5369 | 10.5485 | 0.0116
ERAS-2025-036 | 05 SOUTHWEST | 524757 | BETHEL_COL 3 | 115 | 11.7528 | 11.759 | 0.0062
ERAS-2025-036 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 7.1398 | 7.1406 | 0.0008
ERAS-2025-036 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.9428 | 8.9439 | 0.0011
ERAS-2025-036 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.3409 | 11.3421 | 0.0012
ERAS-2025-036 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.6906 | 10.6924 | 0.0018
ERAS-2025-036 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.1485 | 5.149 | 0.0005
ERAS-2025-036 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4806 | 5.4812 | 0.0006
ERAS-2025-036 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.3729 | 5.3735 | 0.0006
ERAS-2025-036 | 05 SOUTHWEST | 525049 | BC-EARTH +3 | 115 | 8.5461 | 8.5485 | 0.0024
ERAS-2025-036 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 8.3069 | 8.3094 | 0.0025
ERAS-2025-036 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.5378 | 8.5402 | 0.0024
ERAS-2025-036 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.7924 | 7.7987 | 0.0063
ERAS-2025-036 | 05 SOUTHWEST | 525154 | HAPPY_INT 3 | 115 | 5.7781 | 5.7799 | 0.0018
ERAS-2025-036 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.8183 | 6.8212 | 0.0029
ERAS-2025-036 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.5001 | 4.5009 | 0.0008
ERAS-2025-036 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.405 | 12.416 | 0.011
ERAS-2025-036 | 05 SOUTHWEST | 525197 | SW-SW_155 2 | 69 | 2.9681 | 2.9685 | 0.0004
ERAS-2025-036 | 05 SOUTHWEST | 525203 | SW-KRESS 2 | 69 | 4.5001 | 4.5009 | 0.0008
ERAS-2025-036 | 05 SOUTHWEST | 525206 | SW-WILSON 2 | 69 | 3.6498 | 3.6503 | 0.0005
ERAS-2025-036 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.7691 | 11.7795 | 0.0104
ERAS-2025-036 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2018 | 11.2233 | 0.0215
ERAS-2025-036 | 05 SOUTHWEST | 525224 | KRESS_RURL 2 | 69 | 2.5902 | 2.5905 | 0.0003
ERAS-2025-036 | 05 SOUTHWEST | 525225 | KRESS_RURAL3 | 115 | 6.3261 | 6.3283 | 0.0022
ERAS-2025-036 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.8266 | 6.8293 | 0.0027
ERAS-2025-036 | 05 SOUTHWEST | 525257 | N_PLAINVEW 3 | 115 | 5.6784 | 5.6797 | 0.0013
ERAS-2025-036 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.9002 | 6.9015 | 0.0013
ERAS-2025-036 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 4.8745 | 4.8753 | 0.0008
ERAS-2025-036 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.9715 | 7.9748 | 0.0033
ERAS-2025-036 | 05 SOUTHWEST | 525439 | LC-S_OLTON 3 | 115 | 6.1939 | 6.1955 | 0.0016
ERAS-2025-036 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.392 | 7.3943 | 0.0023
ERAS-2025-036 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9487 | 6.9496 | 0.0009
ERAS-2025-036 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.843 | 10.8468 | 0.0038
ERAS-2025-036 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.1666 | 15.198 | 0.0314
ERAS-2025-036 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.9102 | 11.965 | 0.0548
ERAS-2025-036 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.9692 | 15.9758 | 0.0066
ERAS-2025-036 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 25.4642 | 25.4894 | 0.0252
ERAS-2025-036 | 05 SOUTHWEST | 525516 | XS1_MPT1PRI3 | 115 | 14.9551 | 14.9609 | 0.0058
ERAS-2025-036 | 05 SOUTHWEST | 525521 | EASTER_WND 6 | 230 | 8.123 | 8.129 | 0.006
ERAS-2025-036 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 33.7538 | 33.7794 | 0.0256
ERAS-2025-036 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 14.605 | 14.6161 | 0.0111
ERAS-2025-036 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.596 | 11.5984 | 0.0024
ERAS-2025-036 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.596 | 11.5984 | 0.0024
ERAS-2025-036 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 6.0501 | 6.0504 | 0.0003
ERAS-2025-036 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.7738 | 8.7749 | 0.0011
ERAS-2025-036 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0036 | 6.0045 | 0.0009
ERAS-2025-036 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0927 | 7.0928 | 0.0001
ERAS-2025-036 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.5236 | 4.5234 | -0.0002
ERAS-2025-036 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.9508 | 7.9502 | -0.0006
ERAS-2025-036 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 21.7582 | 21.7514 | -0.0068
ERAS-2025-036 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 29.0278 | 28.977 | -0.0508
ERAS-2025-036 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 29.0278 | 28.977 | -0.0508
ERAS-2025-036 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 22.4185 | 22.4092 | -0.0093
ERAS-2025-036 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.2572 | 10.2557 | -0.0015
ERAS-2025-036 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 28.7242 | 28.6746 | -0.0496
ERAS-2025-036 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 22.0934 | 22.0844 | -0.009
ERAS-2025-036 | 05 SOUTHWEST | 525851 | ELK_CT3 7 | 345 | 22.0724 | 22.0634 | -0.009
ERAS-2025-036 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 13.3676 | 13.3594 | -0.0082
ERAS-2025-036 | 05 SOUTHWEST | 526000 | CRWFSHDRW7 | 345 | 19.54 | 19.5398 | -0.0002
ERAS-2025-036 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.9063 | 5.9065 | 0.0002
ERAS-2025-036 | 05 SOUTHWEST | 526035 | LC-OPDYKE +3 | 115 | 6.257 | 6.2572 | 0.0002
ERAS-2025-036 | 05 SOUTHWEST | 526108 | SP-ERSKINE+3 | 115 | 12.4474 | 12.446 | -0.0014
ERAS-2025-036 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 14.8331 | 14.8312 | -0.0019
ERAS-2025-036 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.5624 | 11.5594 | -0.003
ERAS-2025-036 | 05 SOUTHWEST | 526242 | SP-LPRNO_TP3 | 115 | 14.2698 | 14.2684 | -0.0014
ERAS-2025-036 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.8112 | 16.808 | -0.0032
ERAS-2025-036 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.3245 | 12.3228 | -0.0017
ERAS-2025-036 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.955 | 18.9511 | -0.0039
ERAS-2025-036 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 10.4755 | 10.4757 | 0.0002
ERAS-2025-036 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 12.4794 | 12.4798 | 0.0004
ERAS-2025-036 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 12.0363 | 12.037 | 0.0007
ERAS-2025-036 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 11.5746 | 11.5749 | 0.0003
ERAS-2025-036 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.5977 | 10.5982 | 0.0005
ERAS-2025-036 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.863 | 12.8621 | -0.0009
ERAS-2025-036 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.8517 | 13.8496 | -0.0021
ERAS-2025-036 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6096 | 6.6091 | -0.0005
ERAS-2025-036 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.0569 | 21.058 | 0.0011
ERAS-2025-036 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 14.631 | 14.6393 | 0.0083
ERAS-2025-036 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.3135 | 14.3216 | 0.0081
ERAS-2025-036 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 17.8911 | 17.9042 | 0.0131
ERAS-2025-036 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 7.9429 | 7.9551 | 0.0122
ERAS-2025-036 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 9.6608 | 9.6583 | -0.0025
ERAS-2025-036 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 20.9681 | 20.972 | 0.0039
ERAS-2025-036 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 7.9473 | 7.9519 | 0.0046
ERAS-2025-036 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.8142 | 6.8146 | 0.0004
ERAS-2025-036 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.6906 | 10.6924 | 0.0018
ERAS-2025-036 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.1325 | 8.1385 | 0.006
ERAS-2025-036 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.6317 | 14.6359 | 0.0042
ERAS-2025-036 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.5611 | 11.6126 | 0.0515
ERAS-2025-036 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.5434 | 9.5449 | 0.0015
ERAS-2025-036 | 05 SOUTHWEST | 764980 | GEN-2020-008 | 345 | 6.8204 | 6.8209 | 0.0005
ERAS-2025-036 | 05 SOUTHWEST | 788765 | ERAS-016 | 230 | 33.0602 | 33.0847 | 0.0245
ERAS-2025-036 | 05 SOUTHWEST | 788940 | ERA-21-TAP | 345 | 13.5721 | 13.5691 | -0.003
ERAS-2025-036 | 05 SOUTHWEST | 788941 | ERA-28-TAP | 345 | 8.9671 | 8.9668 | -0.0003
ERAS-2025-036 | 05 SOUTHWEST | 789905 | ERAS-36-TAP | 230 | 10.0888 | 10.5266 | 0.4378
ERAS-2025-036 | 05 SOUTHWEST | 789913 | ERAS-36-GSU1 | 230 | 9.1894 | 9.6291 | 0.4397
ERAS-2025-011 | 01 NORTH | 67030 | MPC04000MPT | 230 | 11.1831 | 11.1875 | 0.0044
ERAS-2025-011 | 01 NORTH | 602006 | SHEYNNE4 | 230 | 11.55 | 11.5519 | 0.0019
ERAS-2025-011 | 01 NORTH | 602052 | MAGIC CITY 4 | 230 | 4.4904 | 4.4923 | 0.0019
ERAS-2025-011 | 01 NORTH | 603022 | SOURIS 7 | 115 | 9.0688 | 9.0768 | 0.008
ERAS-2025-011 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.3551 | 11.371 | 0.0159
ERAS-2025-011 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-011 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-011 | 01 NORTH | 608600 | BISONMP4 | 230 | 7.9908 | 7.9926 | 0.0018
ERAS-2025-011 | 01 NORTH | 608602 | SQBEAST4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-011 | 01 NORTH | 608603 | TRICNTY4 | 230 | 5.7424 | 5.7433 | 0.0009
ERAS-2025-011 | 01 NORTH | 608607 | NELSNLK4 | 230 | 23.5084 | 23.5302 | 0.0218
ERAS-2025-011 | 01 NORTH | 608833 | OLVRCTY2 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-011 | 01 NORTH | 608834 | OLVRCTY1 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-011 | 01 NORTH | 615145 | NEW FRONT W | 115 | 4.1542 | 4.1551 | 0.0009
ERAS-2025-011 | 01 NORTH | 615347 | GRE-MCHENRY4 | 230 | 6.5814 | 6.5847 | 0.0033
ERAS-2025-011 | 01 NORTH | 615348 | GRE-MCHENRY7 | 115 | 8.6099 | 8.614 | 0.0041
ERAS-2025-011 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-011 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 9.0583 | 9.0594 | 0.0011
ERAS-2025-011 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-011 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-011 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-011 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.3479 | 16.3645 | 0.0166
ERAS-2025-011 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.3996 | 18.4314 | 0.0318
ERAS-2025-011 | 01 NORTH | 615903 | GRE-BALTA 4 | 230 | 6.8666 | 6.8689 | 0.0023
ERAS-2025-011 | 01 NORTH | 615904 | GRE-BALTACB4 | 230 | 6.8666 | 6.8689 | 0.0023
ERAS-2025-011 | 01 NORTH | 620276 | NHARVEY7 | 115 | 3.2822 | 3.2824 | 0.0002
ERAS-2025-011 | 01 NORTH | 620290 | HARVEY 4 | 230 | 5.1325 | 5.1338 | 0.0013
ERAS-2025-011 | 01 NORTH | 620381 | UNDERWD4 | 230 | 15.2608 | 15.272 | 0.0112
ERAS-2025-011 | 01 NORTH | 652204 | VALLEYC8 | 69 | 2.2817 | 2.2818 | 0.0001
ERAS-2025-011 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.4396 | 7.451 | 0.0114
ERAS-2025-011 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1041 | 1.1047 | 0.0006
ERAS-2025-011 | 01 NORTH | 652296 | WARD 4 | 230 | 13.7303 | 13.7577 | 0.0274
ERAS-2025-011 | 01 NORTH | 652400 | WILISTN4 | 230 | 17.0489 | 17.0908 | 0.0419
ERAS-2025-011 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.0106 | 9.0162 | 0.0056
ERAS-2025-011 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0479 | 5.0513 | 0.0034
ERAS-2025-011 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.1151 | 7.1364 | 0.0213
ERAS-2025-011 | 01 NORTH | 652425 | BELFELD4 | 230 | 10.0005 | 10.0214 | 0.0209
ERAS-2025-011 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.1841 | 14.2254 | 0.0413
ERAS-2025-011 | 01 NORTH | 652427 | BISMARK7 | 115 | 15.9574 | 15.9774 | 0.02
ERAS-2025-011 | 01 NORTH | 652428 | CARNGTN7 | 115 | 2.7066 | 2.7068 | 0.0002
ERAS-2025-011 | 01 NORTH | 652432 | EDGELEY7 | 115 | 3.4506 | 3.4509 | 0.0003
ERAS-2025-011 | 01 NORTH | 652435 | FARGO 4 | 230 | 10.5765 | 10.5784 | 0.0019
ERAS-2025-011 | 01 NORTH | 652436 | FARGO 7 | 115 | 11.5444 | 11.5455 | 0.0011
ERAS-2025-011 | 01 NORTH | 652437 | GRNDFKS4 | 230 | 7.6864 | 7.6874 | 0.001
ERAS-2025-011 | 01 NORTH | 652440 | NELSON 7 | 115 | 7.4673 | 7.4734 | 0.0061
ERAS-2025-011 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.101 | 12.1581 | 0.0571
ERAS-2025-011 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.7612 | 15.7914 | 0.0302
ERAS-2025-011 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.3918 | 8.3974 | 0.0056
ERAS-2025-011 | 01 NORTH | 652445 | JAMESTN7 | 115 | 9.7203 | 9.7237 | 0.0034
ERAS-2025-011 | 01 NORTH | 652452 | RUGBY 7 | 115 | 8.4017 | 8.4039 | 0.0022
ERAS-2025-011 | 01 NORTH | 652454 | VALLEYC7 | 115 | 3.0886 | 3.0888 | 0.0002
ERAS-2025-011 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.6877 | 10.8196 | 0.1319
ERAS-2025-011 | 01 NORTH | 652464 | DENBIGH TAP7 | 115 | 4.6313 | 4.6323 | 0.001
ERAS-2025-011 | 01 NORTH | 652466 | HILKEN 4 | 230 | 8.0386 | 8.054 | 0.0154
ERAS-2025-011 | 01 NORTH | 652499 | CAMPBELL 4 | 230 | 3.7832 | 3.7843 | 0.0011
ERAS-2025-011 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 9.0971 | 9.1052 | 0.0081
ERAS-2025-011 | 01 NORTH | 652529 | WATERTN3 | 345 | 10.7997 | 10.804 | 0.0043
ERAS-2025-011 | 01 NORTH | 652568 | GROTONSOUTH7 | 115 | 17.5735 | 17.585 | 0.0115
ERAS-2025-011 | 01 NORTH | 652590 | SNAKECR7 | 115 | 5.8189 | 5.8235 | 0.0046
ERAS-2025-011 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 9.0317 | 9.0398 | 0.0081
ERAS-2025-011 | 01 NORTH | 654470 | CEG_CS | 230 | 3.776 | 3.7772 | 0.0012
ERAS-2025-011 | 01 NORTH | 655411 | CRANDALL-ER7 | 115 | 5.5747 | 5.5757 | 0.001
ERAS-2025-011 | 01 NORTH | 655419 | SW561-ER7 | 115 | 5.7794 | 5.7805 | 0.0011
ERAS-2025-011 | 01 NORTH | 655612 | HARVEY -CP7 | 115 | 3.861 | 3.8613 | 0.0003
ERAS-2025-011 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.3338 | 6.3403 | 0.0065
ERAS-2025-011 | 01 NORTH | 655643 | VOLTAIR -CP7 | 115 | 8.5473 | 8.5513 | 0.004
ERAS-2025-011 | 01 NORTH | 655647 | WARD -CP7 | 115 | 8.2963 | 8.3015 | 0.0052
ERAS-2025-011 | 01 NORTH | 655652 | E.BISMRK-CP7 | 115 | 15.5889 | 15.608 | 0.0191
ERAS-2025-011 | 01 NORTH | 655655 | E.RUTHVL-CP7 | 115 | 6.8218 | 6.8276 | 0.0058
ERAS-2025-011 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.1735 | 8.1834 | 0.0099
ERAS-2025-011 | 01 NORTH | 655658 | RUTHVILL-CP7 | 115 | 6.3332 | 6.3382 | 0.005
ERAS-2025-011 | 01 NORTH | 655690 | MAX_____-CP7 | 115 | 6.1689 | 6.1732 | 0.0043
ERAS-2025-011 | 01 NORTH | 655693 | WARD_SPR-CP7 | 115 | 3.1168 | 3.1175 | 0.0007
ERAS-2025-011 | 01 NORTH | 655702 | GARRISON-CP7 | 115 | 4.2712 | 4.274 | 0.0028
ERAS-2025-011 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9757 | 0.9762 | 0.0005
ERAS-2025-011 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9028 | 0.9032 | 0.0004
ERAS-2025-011 | 01 NORTH | 655733 | SOLEN -MG8 | 69 | 0.9526 | 0.9526 | 0
ERAS-2025-011 | 01 NORTH | 655734 | CANONBAL-MG8 | 69 | 1.0042 | 1.0042 | 0
ERAS-2025-011 | 01 NORTH | 655735 | CASINO -MG8 | 69 | 1.0589 | 1.0589 | 0
ERAS-2025-011 | 01 NORTH | 655736 | FORTYATE-MG8 | 69 | 1.1599 | 1.1599 | 0
ERAS-2025-011 | 01 NORTH | 655737 | SITTNGBL-MG8 | 69 | 1.1685 | 1.1685 | 0
ERAS-2025-011 | 01 NORTH | 655738 | SIOUX -MG8 | 69 | 1.2571 | 1.2572 | 0.0001
ERAS-2025-011 | 01 NORTH | 655739 | MCLAGLHN-MG8 | 69 | 1.4706 | 1.4707 | 0.0001
ERAS-2025-011 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9096 | 0.91 | 0.0004
ERAS-2025-011 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6894 | 0.6897 | 0.0003
ERAS-2025-011 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6179 | 0.0002
ERAS-2025-011 | 01 NORTH | 655743 | MCLAGHLN-MG7 | 115 | 1.4686 | 1.4686 | 0
ERAS-2025-011 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1103 | 1.1109 | 0.0006
ERAS-2025-011 | 01 NORTH | 655745 | NBCS7 -MG8 | 69 | 0.9409 | 0.941 | 0.0001
ERAS-2025-011 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1162 | 1.1168 | 0.0006
ERAS-2025-011 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1073 | 1.1083 | 0.001
ERAS-2025-011 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5137 | 1.5156 | 0.0019
ERAS-2025-011 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0232 | 1.0241 | 0.0009
ERAS-2025-011 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9906 | 0.9914 | 0.0008
ERAS-2025-011 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.991 | 0.9919 | 0.0009
ERAS-2025-011 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5514 | 1.5534 | 0.002
ERAS-2025-011 | 01 NORTH | 655761 | MOREAGRN-RM8 | 69 | 1.4516 | 1.4516 | 0
ERAS-2025-011 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.2191 | 4.2237 | 0.0046
ERAS-2025-011 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 2.3431 | 2.3445 | 0.0014
ERAS-2025-011 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.2495 | 8.2617 | 0.0122
ERAS-2025-011 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.4675 | 14.5059 | 0.0384
ERAS-2025-011 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 7.0297 | 7.0388 | 0.0091
ERAS-2025-011 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 7.6264 | 7.6371 | 0.0107
ERAS-2025-011 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.6058 | 5.614 | 0.0082
ERAS-2025-011 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.7163 | 3.7188 | 0.0025
ERAS-2025-011 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.2025 | 4.2042 | 0.0017
ERAS-2025-011 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.0106 | 9.0162 | 0.0056
ERAS-2025-011 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5729 | 7.575 | 0.0021
ERAS-2025-011 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.356 | 3.3571 | 0.0011
ERAS-2025-011 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.4721 | 5.475 | 0.0029
ERAS-2025-011 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.7408 | 4.7424 | 0.0016
ERAS-2025-011 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.3118 | 4.3136 | 0.0018
ERAS-2025-011 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3977 | 4.4011 | 0.0034
ERAS-2025-011 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.875 | 5.8811 | 0.0061
ERAS-2025-011 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 10.2312 | 10.25 | 0.0188
ERAS-2025-011 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5691 | 3.5703 | 0.0012
ERAS-2025-011 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9323 | 2.9345 | 0.0022
ERAS-2025-011 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5928 | 3.5962 | 0.0034
ERAS-2025-011 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.5114 | 8.5303 | 0.0189
ERAS-2025-011 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5792 | 3.5814 | 0.0022
ERAS-2025-011 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.8876 | 4.8893 | 0.0017
ERAS-2025-011 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.8564 | 6.8609 | 0.0045
ERAS-2025-011 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 1.7649 | 1.7657 | 0.0008
ERAS-2025-011 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.4309 | 4.4344 | 0.0035
ERAS-2025-011 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7965 | 3.799 | 0.0025
ERAS-2025-011 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3633 | 2.3638 | 0.0005
ERAS-2025-011 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.2106 | 3.2115 | 0.0009
ERAS-2025-011 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.8894 | 5.8956 | 0.0062
ERAS-2025-011 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 6.0438 | 6.0503 | 0.0065
ERAS-2025-011 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.1379 | 4.1409 | 0.003
ERAS-2025-011 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0627 | 3.0636 | 0.0009
ERAS-2025-011 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.8182 | 2.819 | 0.0008
ERAS-2025-011 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.7134 | 2.7141 | 0.0007
ERAS-2025-011 | 01 NORTH | 655871 | G9______-MK7 | 115 | 4.046 | 4.0476 | 0.0016
ERAS-2025-011 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.7037 | 4.7058 | 0.0021
ERAS-2025-011 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.1626 | 7.1717 | 0.0091
ERAS-2025-011 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.5247 | 6.5323 | 0.0076
ERAS-2025-011 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.8494 | 7.8537 | 0.0043
ERAS-2025-011 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.6529 | 8.6581 | 0.0052
ERAS-2025-011 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.3674 | 5.3694 | 0.002
ERAS-2025-011 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9793 | 3.9804 | 0.0011
ERAS-2025-011 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.7779 | 4.7795 | 0.0016
ERAS-2025-011 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.9093 | 5.9155 | 0.0062
ERAS-2025-011 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.8149 | 13.8491 | 0.0342
ERAS-2025-011 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.2848 | 10.3038 | 0.019
ERAS-2025-011 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 8.0342 | 8.0457 | 0.0115
ERAS-2025-011 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.5594 | 5.5649 | 0.0055
ERAS-2025-011 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.3176 | 4.3209 | 0.0033
ERAS-2025-011 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.1603 | 5.1651 | 0.0048
ERAS-2025-011 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.5458 | 3.547 | 0.0012
ERAS-2025-011 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.5666 | 6.5707 | 0.0041
ERAS-2025-011 | 01 NORTH | 655890 | WERNER -MK7 | 115 | 4.4615 | 4.4666 | 0.0051
ERAS-2025-011 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.8787 | 4.8818 | 0.0031
ERAS-2025-011 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.1455 | 4.1472 | 0.0017
ERAS-2025-011 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.3384 | 6.3489 | 0.0105
ERAS-2025-011 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5735 | 3.5769 | 0.0034
ERAS-2025-011 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.3664 | 4.3678 | 0.0014
ERAS-2025-011 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.5042 | 3.5064 | 0.0022
ERAS-2025-011 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.4182 | 5.4234 | 0.0052
ERAS-2025-011 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1482 | 3.1489 | 0.0007
ERAS-2025-011 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.5681 | 6.5757 | 0.0076
ERAS-2025-011 | 01 NORTH | 655901 | BROOKBNK-MW7 | 115 | 9.0176 | 9.0341 | 0.0165
ERAS-2025-011 | 01 NORTH | 655903 | ROSS -MW7 | 115 | 6.995 | 7.004 | 0.009
ERAS-2025-011 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 10.7963 | 10.823 | 0.0267
ERAS-2025-011 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 14.7666 | 14.8231 | 0.0565
ERAS-2025-011 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 15.9604 | 16.027 | 0.0666
ERAS-2025-011 | 01 NORTH | 655907 | E.NEWTWN-MW7 | 115 | 10.5976 | 10.6251 | 0.0275
ERAS-2025-011 | 01 NORTH | 655908 | PARSHALL-MW7 | 115 | 7.5893 | 7.6025 | 0.0132
ERAS-2025-011 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 7.0217 | 7.0329 | 0.0112
ERAS-2025-011 | 01 NORTH | 655914 | NE.ROSS_-MW7 | 115 | 4.2917 | 4.2955 | 0.0038
ERAS-2025-011 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 7.273 | 7.2834 | 0.0104
ERAS-2025-011 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 7.0945 | 7.1049 | 0.0104
ERAS-2025-011 | 01 NORTH | 655918 | PALGASPL-MW7 | 115 | 6.1349 | 6.1423 | 0.0074
ERAS-2025-011 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 10.3562 | 10.3827 | 0.0265
ERAS-2025-011 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 11.042 | 11.0721 | 0.0301
ERAS-2025-011 | 01 NORTH | 655921 | LOSTWOOD-MW7 | 115 | 3.5282 | 3.5308 | 0.0026
ERAS-2025-011 | 01 NORTH | 655929 | RATLAK.T-MW7 | 115 | 9.5625 | 9.5788 | 0.0163
ERAS-2025-011 | 01 NORTH | 655932 | VNHKCOMP-MW7 | 115 | 11.8089 | 11.8446 | 0.0357
ERAS-2025-011 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.5831 | 6.5921 | 0.009
ERAS-2025-011 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 8.7939 | 8.8082 | 0.0143
ERAS-2025-011 | 01 NORTH | 655950 | LOSTWD_T-MW7 | 115 | 5.8042 | 5.8111 | 0.0069
ERAS-2025-011 | 01 NORTH | 655951 | NE.ROS_T-MW7 | 115 | 4.8194 | 4.8242 | 0.0048
ERAS-2025-011 | 01 NORTH | 655960 | BIGBEND -MW7 | 115 | 5.1564 | 5.1629 | 0.0065
ERAS-2025-011 | 01 NORTH | 655963 | HOWIE -MW7 | 115 | 4.2182 | 4.2226 | 0.0044
ERAS-2025-011 | 01 NORTH | 655967 | SATTER -MW7 | 115 | 10.4184 | 10.4433 | 0.0249
ERAS-2025-011 | 01 NORTH | 655968 | MUSKRAT -MW7 | 115 | 4.3501 | 4.3548 | 0.0047
ERAS-2025-011 | 01 NORTH | 655969 | E.NESON2-MW7 | 115 | 8.3914 | 8.4039 | 0.0125
ERAS-2025-011 | 01 NORTH | 655970 | RATLAKE -MW7 | 115 | 8.0843 | 8.096 | 0.0117
ERAS-2025-011 | 01 NORTH | 655973 | OWAN -MW4 | 230 | 17.445 | 17.49 | 0.045
ERAS-2025-011 | 01 NORTH | 657751 | CENTER 4 | 230 | 20.804 | 20.8221 | 0.0181
ERAS-2025-011 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-011 | 01 NORTH | 657759 | PICKERT4 | 230 | 4.2341 | 4.2348 | 0.0007
ERAS-2025-011 | 01 NORTH | 657791 | CENTER 3 | 345 | 12.9963 | 13.0044 | 0.0081
ERAS-2025-011 | 01 NORTH | 657804 | MPC-VCY8 | 69 | 2.2817 | 2.2818 | 0.0001
ERAS-2025-011 | 01 NORTH | 657848 | YNG2 4 | 230 | 19.4055 | 19.4184 | 0.0129
ERAS-2025-011 | 01 NORTH | 657923 | PICKERT8 | 69 | 3.2393 | 3.2394 | 0.0001
ERAS-2025-011 | 01 NORTH | 658209 | MOORHDW4 | 230 | 7.2565 | 7.2573 | 0.0008
ERAS-2025-011 | 01 NORTH | 659010 | CRANECREEK2 | 115 | 14.412 | 14.4664 | 0.0544
ERAS-2025-011 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 17.2715 | 17.815 | 0.5435
ERAS-2025-011 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-011 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.5804 | 26.7325 | 1.1521
ERAS-2025-011 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.5057 | 6.5272 | 0.0215
ERAS-2025-011 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4235 | 5.4483 | 0.0248
ERAS-2025-011 | 01 NORTH | 659120 | BROADLND-BE3 | 345 | 4.2012 | 4.2057 | 0.0045
ERAS-2025-011 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.2324 | 7.2417 | 0.0093
ERAS-2025-011 | 01 NORTH | 659128 | HERBERTW-KM4 | 230 | 5.0261 | 5.0298 | 0.0037
ERAS-2025-011 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.414 | 6.4224 | 0.0084
ERAS-2025-011 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.6716 | 12.7073 | 0.0357
ERAS-2025-011 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 13.7808 | 13.8001 | 0.0193
ERAS-2025-011 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 5.4656 | 5.4736 | 0.008
ERAS-2025-011 | 01 NORTH | 659141 | NRTSHORE-BE7 | 115 | 10.8895 | 10.9115 | 0.022
ERAS-2025-011 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.1413 | 6.1542 | 0.0129
ERAS-2025-011 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 9.0968 | 9.1121 | 0.0153
ERAS-2025-011 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.9955 | 7.9968 | 0.0013
ERAS-2025-011 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.1659 | 11.1851 | 0.0192
ERAS-2025-011 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.2715 | 6.28 | 0.0085
ERAS-2025-011 | 01 NORTH | 659165 | CROCKER_-BE3 | 345 | 6.5266 | 6.532 | 0.0054
ERAS-2025-011 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.3705 | 3.3717 | 0.0012
ERAS-2025-011 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.5963 | 14.6354 | 0.0391
ERAS-2025-011 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.8194 | 11.9063 | 0.0869
ERAS-2025-011 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.3992 | 4.4019 | 0.0027
ERAS-2025-011 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7668 | 3.7694 | 0.0026
ERAS-2025-011 | 01 NORTH | 659187 | GROTON__-BE7 | 115 | 17.5475 | 17.559 | 0.0115
ERAS-2025-011 | 01 NORTH | 659190 | ND.PW1__-BE7 | 115 | 7.4673 | 7.4734 | 0.0061
ERAS-2025-011 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 23.1728 | 24.1106 | 0.9378
ERAS-2025-011 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.3044 | 10.3122 | 0.0078
ERAS-2025-011 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 16.46 | 16.953 | 0.493
ERAS-2025-011 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 17.2715 | 17.815 | 0.5435
ERAS-2025-011 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.7068 | 9.7401 | 0.0333
ERAS-2025-011 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.3096 | 7.3285 | 0.0189
ERAS-2025-011 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.7326 | 5.7382 | 0.0056
ERAS-2025-011 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.2157 | 4.2176 | 0.0019
ERAS-2025-011 | 01 NORTH | 659275 | GROTON_G-BE7 | 115 | 17.164 | 17.1747 | 0.0107
ERAS-2025-011 | 01 NORTH | 659280 | POMONA__-PP7 | 115 | 2.5803 | 2.5805 | 0.0002
ERAS-2025-011 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 6.876 | 6.887 | 0.011
ERAS-2025-011 | 01 NORTH | 659288 | DAY_CNTY-PP7 | 115 | 3.926 | 3.9264 | 0.0004
ERAS-2025-011 | 01 NORTH | 659300 | STANTN.T-BE7 | 115 | 8.0569 | 8.0626 | 0.0057
ERAS-2025-011 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 12.4908 | 12.5502 | 0.0594
ERAS-2025-011 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3183 | 2.3189 | 0.0006
ERAS-2025-011 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 10.0005 | 10.0214 | 0.0209
ERAS-2025-011 | 01 NORTH | 659330 | SPRNGBRK-BE3 | 345 | 9.5807 | 9.6047 | 0.024
ERAS-2025-011 | 01 NORTH | 659331 | SPRNGBRK-BE7 | 115 | 16.1922 | 16.2121 | 0.0199
ERAS-2025-011 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 13.4425 | 13.4847 | 0.0422
ERAS-2025-011 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 17.445 | 17.49 | 0.045
ERAS-2025-011 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.7072 | 8.7362 | 0.029
ERAS-2025-011 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.6327 | 12.6683 | 0.0356
ERAS-2025-011 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.9594 | 7.9607 | 0.0013
ERAS-2025-011 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 13.0653 | 13.0766 | 0.0113
ERAS-2025-011 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 13.1524 | 13.1639 | 0.0115
ERAS-2025-011 | 01 NORTH | 659355 | CRANECRK-BE3 | 345 | 6.2528 | 6.2858 | 0.033
ERAS-2025-011 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 9.2895 | 9.3034 | 0.0139
ERAS-2025-011 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 6.876 | 6.887 | 0.011
ERAS-2025-011 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 10.4997 | 10.5863 | 0.0866
ERAS-2025-011 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.3014 | 12.3408 | 0.0394
ERAS-2025-011 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 8.3126 | 8.3498 | 0.0372
ERAS-2025-011 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 15.4157 | 15.4583 | 0.0426
ERAS-2025-011 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 12.0746 | 12.1242 | 0.0496
ERAS-2025-011 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 21.1841 | 21.2274 | 0.0433
ERAS-2025-011 | 01 NORTH | 659404 | HAUGEN__-PP3 | 345 | 4.592 | 4.5994 | 0.0074
ERAS-2025-011 | 01 NORTH | 659408 | CAMPBL._-PP4 | 230 | 3.5194 | 3.5203 | 0.0009
ERAS-2025-011 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 17.2715 | 17.815 | 0.5435
ERAS-2025-011 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.2012 | 4.2057 | 0.0045
ERAS-2025-011 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-011 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.2715 | 6.28 | 0.0085
ERAS-2025-011 | 01 NORTH | 659424 | LO.LS-CC-BE3 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-011 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.7072 | 8.7362 | 0.029
ERAS-2025-011 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.3837 | 6.392 | 0.0083
ERAS-2025-011 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.3523 | 6.3604 | 0.0081
ERAS-2025-011 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9418 | 1.9422 | 0.0004
ERAS-2025-011 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7467 | 1.747 | 0.0003
ERAS-2025-011 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.8451 | 6.8524 | 0.0073
ERAS-2025-011 | 01 NORTH | 659450 | BRADY___-PP4 | 230 | 4.7828 | 4.7859 | 0.0031
ERAS-2025-011 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 21.0723 | 21.1154 | 0.0431
ERAS-2025-011 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 21.0858 | 21.129 | 0.0432
ERAS-2025-011 | 01 NORTH | 659472 | CROCKER_-UA3 | 345 | 6.0307 | 6.0352 | 0.0045
ERAS-2025-011 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.2164 | 6.2303 | 0.0139
ERAS-2025-011 | 01 NORTH | 659490 | OLIVR4.H-UA3 | 345 | 12.9114 | 13.5922 | 0.6808
ERAS-2025-011 | 01 NORTH | 659509 | REDBUTTE-UA4 | 230 | 7.6045 | 7.6929 | 0.0884
ERAS-2025-011 | 01 NORTH | 659543 | PICKCITY-RR7 | 115 | 10.3151 | 10.3265 | 0.0114
ERAS-2025-011 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9418 | 1.9422 | 0.0004
ERAS-2025-011 | 01 NORTH | 659575 | PIONEER_-BE3 | 345 | 12.7236 | 12.7549 | 0.0313
ERAS-2025-011 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.3548 | 7.366 | 0.0112
ERAS-2025-011 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.5775 | 9.5829 | 0.0054
ERAS-2025-011 | 01 NORTH | 661029 | ESTBMRK7 | 115 | 15.93 | 15.9499 | 0.0199
ERAS-2025-011 | 01 NORTH | 661035 | GLENHAM7 | 115 | 3.8642 | 3.8647 | 0.0005
ERAS-2025-011 | 01 NORTH | 661037 | BOWDLE_EAST7 | 115 | 1.5952 | 1.5953 | 0.0001
ERAS-2025-011 | 01 NORTH | 661038 | GLENHAM4 | 230 | 3.7352 | 3.7361 | 0.0009
ERAS-2025-011 | 01 NORTH | 661039 | MOBRIDG7 | 115 | 2.5483 | 2.5485 | 0.0002
ERAS-2025-011 | 01 NORTH | 661041 | MCINTSH7 | 115 | 0.9962 | 0.9962 | 0
ERAS-2025-011 | 01 NORTH | 661053 | MANDAN 4 | 230 | 15.2141 | 15.2404 | 0.0263
ERAS-2025-011 | 01 NORTH | 661060 | LINTON_NW7 | 115 | 1.3971 | 1.3973 | 0.0002
ERAS-2025-011 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.6716 | 12.7073 | 0.0357
ERAS-2025-011 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.7157 | 13.7347 | 0.019
ERAS-2025-011 | 01 NORTH | 672603 | BDV 4 | 230 | 4.6311 | 4.6332 | 0.0021
ERAS-2025-011 | 01 NORTH | 672665 | TABLELAND 4 | 230 | 10.0058 | 10.0086 | 0.0028
ERAS-2025-011 | 01 NORTH | 672702 | TB-PST1 | 230 | 4.2176 | 4.2192 | 0.0016
ERAS-2025-011 | 01 NORTH | 673665 | ES-PV-POI | 230 | 8.1986 | 8.2005 | 0.0019
ERAS-2025-011 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.2316 | 3.2359 | 0.0043
ERAS-2025-011 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-011 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 11.8123 | 11.8598 | 0.0475
ERAS-2025-011 | 01 NORTH | 788737 | ERA-11 | 345 | 18.7926 | 20.4972 | 1.7046
ERAS-2025-011 | 01 NORTH | 788740 | ERA-12 | 345 | 18.9706 | 20.4972 | 1.5266
ERAS-2025-012 | 01 NORTH | 67030 | MPC04000MPT | 230 | 11.1831 | 11.1875 | 0.0044
ERAS-2025-012 | 01 NORTH | 602006 | SHEYNNE4 | 230 | 11.55 | 11.5519 | 0.0019
ERAS-2025-012 | 01 NORTH | 602052 | MAGIC CITY 4 | 230 | 4.4904 | 4.4923 | 0.0019
ERAS-2025-012 | 01 NORTH | 603022 | SOURIS 7 | 115 | 9.0688 | 9.0768 | 0.008
ERAS-2025-012 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.3551 | 11.371 | 0.0159
ERAS-2025-012 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-012 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-012 | 01 NORTH | 608600 | BISONMP4 | 230 | 7.9908 | 7.9926 | 0.0018
ERAS-2025-012 | 01 NORTH | 608602 | SQBEAST4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-012 | 01 NORTH | 608603 | TRICNTY4 | 230 | 5.7424 | 5.7433 | 0.0009
ERAS-2025-012 | 01 NORTH | 608607 | NELSNLK4 | 230 | 23.5084 | 23.5302 | 0.0218
ERAS-2025-012 | 01 NORTH | 608833 | OLVRCTY2 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-012 | 01 NORTH | 608834 | OLVRCTY1 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-012 | 01 NORTH | 615145 | NEW FRONT W | 115 | 4.1542 | 4.1551 | 0.0009
ERAS-2025-012 | 01 NORTH | 615347 | GRE-MCHENRY4 | 230 | 6.5814 | 6.5847 | 0.0033
ERAS-2025-012 | 01 NORTH | 615348 | GRE-MCHENRY7 | 115 | 8.6099 | 8.614 | 0.0041
ERAS-2025-012 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-012 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 9.0583 | 9.0594 | 0.0011
ERAS-2025-012 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-012 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-012 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 19.4389 | 19.4571 | 0.0182
ERAS-2025-012 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.3479 | 16.3645 | 0.0166
ERAS-2025-012 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.3996 | 18.4314 | 0.0318
ERAS-2025-012 | 01 NORTH | 615903 | GRE-BALTA 4 | 230 | 6.8666 | 6.8689 | 0.0023
ERAS-2025-012 | 01 NORTH | 615904 | GRE-BALTACB4 | 230 | 6.8666 | 6.8689 | 0.0023
ERAS-2025-012 | 01 NORTH | 620276 | NHARVEY7 | 115 | 3.2822 | 3.2824 | 0.0002
ERAS-2025-012 | 01 NORTH | 620290 | HARVEY 4 | 230 | 5.1325 | 5.1338 | 0.0013
ERAS-2025-012 | 01 NORTH | 620381 | UNDERWD4 | 230 | 15.2608 | 15.272 | 0.0112
ERAS-2025-012 | 01 NORTH | 652204 | VALLEYC8 | 69 | 2.2817 | 2.2818 | 0.0001
ERAS-2025-012 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.4396 | 7.451 | 0.0114
ERAS-2025-012 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1041 | 1.1047 | 0.0006
ERAS-2025-012 | 01 NORTH | 652296 | WARD 4 | 230 | 13.7303 | 13.7577 | 0.0274
ERAS-2025-012 | 01 NORTH | 652400 | WILISTN4 | 230 | 17.0489 | 17.0908 | 0.0419
ERAS-2025-012 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.0106 | 9.0162 | 0.0056
ERAS-2025-012 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0479 | 5.0513 | 0.0034
ERAS-2025-012 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.1151 | 7.1364 | 0.0213
ERAS-2025-012 | 01 NORTH | 652425 | BELFELD4 | 230 | 10.0005 | 10.0214 | 0.0209
ERAS-2025-012 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.1841 | 14.2254 | 0.0413
ERAS-2025-012 | 01 NORTH | 652427 | BISMARK7 | 115 | 15.9574 | 15.9774 | 0.02
ERAS-2025-012 | 01 NORTH | 652428 | CARNGTN7 | 115 | 2.7066 | 2.7068 | 0.0002
ERAS-2025-012 | 01 NORTH | 652432 | EDGELEY7 | 115 | 3.4506 | 3.4509 | 0.0003
ERAS-2025-012 | 01 NORTH | 652435 | FARGO 4 | 230 | 10.5765 | 10.5784 | 0.0019
ERAS-2025-012 | 01 NORTH | 652436 | FARGO 7 | 115 | 11.5444 | 11.5455 | 0.0011
ERAS-2025-012 | 01 NORTH | 652437 | GRNDFKS4 | 230 | 7.6864 | 7.6874 | 0.001
ERAS-2025-012 | 01 NORTH | 652440 | NELSON 7 | 115 | 7.4673 | 7.4734 | 0.0061
ERAS-2025-012 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.101 | 12.1581 | 0.0571
ERAS-2025-012 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.7612 | 15.7914 | 0.0302
ERAS-2025-012 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.3918 | 8.3974 | 0.0056
ERAS-2025-012 | 01 NORTH | 652445 | JAMESTN7 | 115 | 9.7203 | 9.7237 | 0.0034
ERAS-2025-012 | 01 NORTH | 652452 | RUGBY 7 | 115 | 8.4017 | 8.4039 | 0.0022
ERAS-2025-012 | 01 NORTH | 652454 | VALLEYC7 | 115 | 3.0886 | 3.0888 | 0.0002
ERAS-2025-012 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.6877 | 10.8196 | 0.1319
ERAS-2025-012 | 01 NORTH | 652464 | DENBIGH TAP7 | 115 | 4.6313 | 4.6323 | 0.001
ERAS-2025-012 | 01 NORTH | 652466 | HILKEN 4 | 230 | 8.0386 | 8.054 | 0.0154
ERAS-2025-012 | 01 NORTH | 652499 | CAMPBELL 4 | 230 | 3.7832 | 3.7843 | 0.0011
ERAS-2025-012 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 9.0971 | 9.1052 | 0.0081
ERAS-2025-012 | 01 NORTH | 652529 | WATERTN3 | 345 | 10.7997 | 10.804 | 0.0043
ERAS-2025-012 | 01 NORTH | 652568 | GROTONSOUTH7 | 115 | 17.5735 | 17.585 | 0.0115
ERAS-2025-012 | 01 NORTH | 652590 | SNAKECR7 | 115 | 5.8189 | 5.8235 | 0.0046
ERAS-2025-012 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 9.0317 | 9.0398 | 0.0081
ERAS-2025-012 | 01 NORTH | 654470 | CEG_CS | 230 | 3.776 | 3.7772 | 0.0012
ERAS-2025-012 | 01 NORTH | 655411 | CRANDALL-ER7 | 115 | 5.5747 | 5.5757 | 0.001
ERAS-2025-012 | 01 NORTH | 655419 | SW561-ER7 | 115 | 5.7794 | 5.7805 | 0.0011
ERAS-2025-012 | 01 NORTH | 655612 | HARVEY -CP7 | 115 | 3.861 | 3.8613 | 0.0003
ERAS-2025-012 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.3338 | 6.3403 | 0.0065
ERAS-2025-012 | 01 NORTH | 655643 | VOLTAIR -CP7 | 115 | 8.5473 | 8.5513 | 0.004
ERAS-2025-012 | 01 NORTH | 655647 | WARD -CP7 | 115 | 8.2963 | 8.3015 | 0.0052
ERAS-2025-012 | 01 NORTH | 655652 | E.BISMRK-CP7 | 115 | 15.5889 | 15.608 | 0.0191
ERAS-2025-012 | 01 NORTH | 655655 | E.RUTHVL-CP7 | 115 | 6.8218 | 6.8276 | 0.0058
ERAS-2025-012 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.1735 | 8.1834 | 0.0099
ERAS-2025-012 | 01 NORTH | 655658 | RUTHVILL-CP7 | 115 | 6.3332 | 6.3382 | 0.005
ERAS-2025-012 | 01 NORTH | 655690 | MAX_____-CP7 | 115 | 6.1689 | 6.1732 | 0.0043
ERAS-2025-012 | 01 NORTH | 655693 | WARD_SPR-CP7 | 115 | 3.1168 | 3.1175 | 0.0007
ERAS-2025-012 | 01 NORTH | 655702 | GARRISON-CP7 | 115 | 4.2712 | 4.274 | 0.0028
ERAS-2025-012 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9757 | 0.9762 | 0.0005
ERAS-2025-012 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9028 | 0.9032 | 0.0004
ERAS-2025-012 | 01 NORTH | 655733 | SOLEN -MG8 | 69 | 0.9526 | 0.9526 | 0
ERAS-2025-012 | 01 NORTH | 655734 | CANONBAL-MG8 | 69 | 1.0042 | 1.0042 | 0
ERAS-2025-012 | 01 NORTH | 655735 | CASINO -MG8 | 69 | 1.0589 | 1.0589 | 0
ERAS-2025-012 | 01 NORTH | 655736 | FORTYATE-MG8 | 69 | 1.1599 | 1.1599 | 0
ERAS-2025-012 | 01 NORTH | 655737 | SITTNGBL-MG8 | 69 | 1.1685 | 1.1685 | 0
ERAS-2025-012 | 01 NORTH | 655738 | SIOUX -MG8 | 69 | 1.2571 | 1.2572 | 0.0001
ERAS-2025-012 | 01 NORTH | 655739 | MCLAGLHN-MG8 | 69 | 1.4706 | 1.4707 | 0.0001
ERAS-2025-012 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9096 | 0.91 | 0.0004
ERAS-2025-012 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6894 | 0.6897 | 0.0003
ERAS-2025-012 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6179 | 0.0002
ERAS-2025-012 | 01 NORTH | 655743 | MCLAGHLN-MG7 | 115 | 1.4686 | 1.4686 | 0
ERAS-2025-012 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1103 | 1.1109 | 0.0006
ERAS-2025-012 | 01 NORTH | 655745 | NBCS7 -MG8 | 69 | 0.9409 | 0.941 | 0.0001
ERAS-2025-012 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1162 | 1.1168 | 0.0006
ERAS-2025-012 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1073 | 1.1083 | 0.001
ERAS-2025-012 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5137 | 1.5156 | 0.0019
ERAS-2025-012 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0232 | 1.0241 | 0.0009
ERAS-2025-012 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9906 | 0.9914 | 0.0008
ERAS-2025-012 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.991 | 0.9919 | 0.0009
ERAS-2025-012 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5514 | 1.5534 | 0.002
ERAS-2025-012 | 01 NORTH | 655761 | MOREAGRN-RM8 | 69 | 1.4516 | 1.4516 | 0
ERAS-2025-012 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.2191 | 4.2237 | 0.0046
ERAS-2025-012 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 2.3431 | 2.3445 | 0.0014
ERAS-2025-012 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.2495 | 8.2617 | 0.0122
ERAS-2025-012 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.4675 | 14.5059 | 0.0384
ERAS-2025-012 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 7.0297 | 7.0388 | 0.0091
ERAS-2025-012 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 7.6264 | 7.6371 | 0.0107
ERAS-2025-012 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.6058 | 5.614 | 0.0082
ERAS-2025-012 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.7163 | 3.7188 | 0.0025
ERAS-2025-012 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.2025 | 4.2042 | 0.0017
ERAS-2025-012 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.0106 | 9.0162 | 0.0056
ERAS-2025-012 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5729 | 7.575 | 0.0021
ERAS-2025-012 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.356 | 3.3571 | 0.0011
ERAS-2025-012 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.4721 | 5.475 | 0.0029
ERAS-2025-012 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.7408 | 4.7424 | 0.0016
ERAS-2025-012 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.3118 | 4.3136 | 0.0018
ERAS-2025-012 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3977 | 4.4011 | 0.0034
ERAS-2025-012 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.875 | 5.8811 | 0.0061
ERAS-2025-012 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 10.2312 | 10.25 | 0.0188
ERAS-2025-012 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5691 | 3.5703 | 0.0012
ERAS-2025-012 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9323 | 2.9345 | 0.0022
ERAS-2025-012 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5928 | 3.5962 | 0.0034
ERAS-2025-012 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.5114 | 8.5303 | 0.0189
ERAS-2025-012 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5792 | 3.5814 | 0.0022
ERAS-2025-012 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.8876 | 4.8893 | 0.0017
ERAS-2025-012 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.8564 | 6.8609 | 0.0045
ERAS-2025-012 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 1.7649 | 1.7657 | 0.0008
ERAS-2025-012 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.4309 | 4.4344 | 0.0035
ERAS-2025-012 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7965 | 3.799 | 0.0025
ERAS-2025-012 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3633 | 2.3638 | 0.0005
ERAS-2025-012 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.2106 | 3.2115 | 0.0009
ERAS-2025-012 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.8894 | 5.8956 | 0.0062
ERAS-2025-012 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 6.0438 | 6.0503 | 0.0065
ERAS-2025-012 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.1379 | 4.1409 | 0.003
ERAS-2025-012 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0627 | 3.0636 | 0.0009
ERAS-2025-012 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.8182 | 2.819 | 0.0008
ERAS-2025-012 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.7134 | 2.7141 | 0.0007
ERAS-2025-012 | 01 NORTH | 655871 | G9______-MK7 | 115 | 4.046 | 4.0476 | 0.0016
ERAS-2025-012 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.7037 | 4.7058 | 0.0021
ERAS-2025-012 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.1626 | 7.1717 | 0.0091
ERAS-2025-012 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.5247 | 6.5323 | 0.0076
ERAS-2025-012 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.8494 | 7.8537 | 0.0043
ERAS-2025-012 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.6529 | 8.6581 | 0.0052
ERAS-2025-012 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.3674 | 5.3694 | 0.002
ERAS-2025-012 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9793 | 3.9804 | 0.0011
ERAS-2025-012 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.7779 | 4.7795 | 0.0016
ERAS-2025-012 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.9093 | 5.9155 | 0.0062
ERAS-2025-012 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.8149 | 13.8491 | 0.0342
ERAS-2025-012 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.2848 | 10.3038 | 0.019
ERAS-2025-012 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 8.0342 | 8.0457 | 0.0115
ERAS-2025-012 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.5594 | 5.5649 | 0.0055
ERAS-2025-012 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.3176 | 4.3209 | 0.0033
ERAS-2025-012 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.1603 | 5.1651 | 0.0048
ERAS-2025-012 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.5458 | 3.547 | 0.0012
ERAS-2025-012 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.5666 | 6.5707 | 0.0041
ERAS-2025-012 | 01 NORTH | 655890 | WERNER -MK7 | 115 | 4.4615 | 4.4666 | 0.0051
ERAS-2025-012 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.8787 | 4.8818 | 0.0031
ERAS-2025-012 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.1455 | 4.1472 | 0.0017
ERAS-2025-012 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.3384 | 6.3489 | 0.0105
ERAS-2025-012 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5735 | 3.5769 | 0.0034
ERAS-2025-012 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.3664 | 4.3678 | 0.0014
ERAS-2025-012 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.5042 | 3.5064 | 0.0022
ERAS-2025-012 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.4182 | 5.4234 | 0.0052
ERAS-2025-012 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1482 | 3.1489 | 0.0007
ERAS-2025-012 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.5681 | 6.5757 | 0.0076
ERAS-2025-012 | 01 NORTH | 655901 | BROOKBNK-MW7 | 115 | 9.0176 | 9.0341 | 0.0165
ERAS-2025-012 | 01 NORTH | 655903 | ROSS -MW7 | 115 | 6.995 | 7.004 | 0.009
ERAS-2025-012 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 10.7963 | 10.823 | 0.0267
ERAS-2025-012 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 14.7666 | 14.8231 | 0.0565
ERAS-2025-012 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 15.9604 | 16.027 | 0.0666
ERAS-2025-012 | 01 NORTH | 655907 | E.NEWTWN-MW7 | 115 | 10.5976 | 10.6251 | 0.0275
ERAS-2025-012 | 01 NORTH | 655908 | PARSHALL-MW7 | 115 | 7.5893 | 7.6025 | 0.0132
ERAS-2025-012 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 7.0217 | 7.0329 | 0.0112
ERAS-2025-012 | 01 NORTH | 655914 | NE.ROSS_-MW7 | 115 | 4.2917 | 4.2955 | 0.0038
ERAS-2025-012 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 7.273 | 7.2834 | 0.0104
ERAS-2025-012 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 7.0945 | 7.1049 | 0.0104
ERAS-2025-012 | 01 NORTH | 655918 | PALGASPL-MW7 | 115 | 6.1349 | 6.1423 | 0.0074
ERAS-2025-012 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 10.3562 | 10.3827 | 0.0265
ERAS-2025-012 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 11.042 | 11.0721 | 0.0301
ERAS-2025-012 | 01 NORTH | 655921 | LOSTWOOD-MW7 | 115 | 3.5282 | 3.5308 | 0.0026
ERAS-2025-012 | 01 NORTH | 655929 | RATLAK.T-MW7 | 115 | 9.5625 | 9.5788 | 0.0163
ERAS-2025-012 | 01 NORTH | 655932 | VNHKCOMP-MW7 | 115 | 11.8089 | 11.8446 | 0.0357
ERAS-2025-012 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.5831 | 6.5921 | 0.009
ERAS-2025-012 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 8.7939 | 8.8082 | 0.0143
ERAS-2025-012 | 01 NORTH | 655950 | LOSTWD_T-MW7 | 115 | 5.8042 | 5.8111 | 0.0069
ERAS-2025-012 | 01 NORTH | 655951 | NE.ROS_T-MW7 | 115 | 4.8194 | 4.8242 | 0.0048
ERAS-2025-012 | 01 NORTH | 655960 | BIGBEND -MW7 | 115 | 5.1564 | 5.1629 | 0.0065
ERAS-2025-012 | 01 NORTH | 655963 | HOWIE -MW7 | 115 | 4.2182 | 4.2226 | 0.0044
ERAS-2025-012 | 01 NORTH | 655967 | SATTER -MW7 | 115 | 10.4184 | 10.4433 | 0.0249
ERAS-2025-012 | 01 NORTH | 655968 | MUSKRAT -MW7 | 115 | 4.3501 | 4.3548 | 0.0047
ERAS-2025-012 | 01 NORTH | 655969 | E.NESON2-MW7 | 115 | 8.3914 | 8.4039 | 0.0125
ERAS-2025-012 | 01 NORTH | 655970 | RATLAKE -MW7 | 115 | 8.0843 | 8.096 | 0.0117
ERAS-2025-012 | 01 NORTH | 655973 | OWAN -MW4 | 230 | 17.445 | 17.49 | 0.045
ERAS-2025-012 | 01 NORTH | 657751 | CENTER 4 | 230 | 20.804 | 20.8221 | 0.0181
ERAS-2025-012 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 23.955 | 23.9771 | 0.0221
ERAS-2025-012 | 01 NORTH | 657759 | PICKERT4 | 230 | 4.2341 | 4.2348 | 0.0007
ERAS-2025-012 | 01 NORTH | 657791 | CENTER 3 | 345 | 12.9963 | 13.0044 | 0.0081
ERAS-2025-012 | 01 NORTH | 657804 | MPC-VCY8 | 69 | 2.2817 | 2.2818 | 0.0001
ERAS-2025-012 | 01 NORTH | 657848 | YNG2 4 | 230 | 19.4055 | 19.4184 | 0.0129
ERAS-2025-012 | 01 NORTH | 657923 | PICKERT8 | 69 | 3.2393 | 3.2394 | 0.0001
ERAS-2025-012 | 01 NORTH | 658209 | MOORHDW4 | 230 | 7.2565 | 7.2573 | 0.0008
ERAS-2025-012 | 01 NORTH | 659010 | CRANECREEK2 | 115 | 14.412 | 14.4664 | 0.0544
ERAS-2025-012 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 17.2715 | 17.815 | 0.5435
ERAS-2025-012 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-012 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.5804 | 26.7325 | 1.1521
ERAS-2025-012 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.5057 | 6.5272 | 0.0215
ERAS-2025-012 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4235 | 5.4483 | 0.0248
ERAS-2025-012 | 01 NORTH | 659120 | BROADLND-BE3 | 345 | 4.2012 | 4.2057 | 0.0045
ERAS-2025-012 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.2324 | 7.2417 | 0.0093
ERAS-2025-012 | 01 NORTH | 659128 | HERBERTW-KM4 | 230 | 5.0261 | 5.0298 | 0.0037
ERAS-2025-012 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.414 | 6.4224 | 0.0084
ERAS-2025-012 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.6716 | 12.7073 | 0.0357
ERAS-2025-012 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 13.7808 | 13.8001 | 0.0193
ERAS-2025-012 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 5.4656 | 5.4736 | 0.008
ERAS-2025-012 | 01 NORTH | 659141 | NRTSHORE-BE7 | 115 | 10.8895 | 10.9115 | 0.022
ERAS-2025-012 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.1413 | 6.1542 | 0.0129
ERAS-2025-012 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 9.0968 | 9.1121 | 0.0153
ERAS-2025-012 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.9955 | 7.9968 | 0.0013
ERAS-2025-012 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.1659 | 11.1851 | 0.0192
ERAS-2025-012 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.2715 | 6.28 | 0.0085
ERAS-2025-012 | 01 NORTH | 659165 | CROCKER_-BE3 | 345 | 6.5266 | 6.532 | 0.0054
ERAS-2025-012 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.3705 | 3.3717 | 0.0012
ERAS-2025-012 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.5963 | 14.6354 | 0.0391
ERAS-2025-012 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.8194 | 11.9063 | 0.0869
ERAS-2025-012 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.3992 | 4.4019 | 0.0027
ERAS-2025-012 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7668 | 3.7694 | 0.0026
ERAS-2025-012 | 01 NORTH | 659187 | GROTON__-BE7 | 115 | 17.5475 | 17.559 | 0.0115
ERAS-2025-012 | 01 NORTH | 659190 | ND.PW1__-BE7 | 115 | 7.4673 | 7.4734 | 0.0061
ERAS-2025-012 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 23.1728 | 24.1106 | 0.9378
ERAS-2025-012 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.3044 | 10.3122 | 0.0078
ERAS-2025-012 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 16.46 | 16.953 | 0.493
ERAS-2025-012 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 17.2715 | 17.815 | 0.5435
ERAS-2025-012 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.7068 | 9.7401 | 0.0333
ERAS-2025-012 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.3096 | 7.3285 | 0.0189
ERAS-2025-012 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.7326 | 5.7382 | 0.0056
ERAS-2025-012 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.2157 | 4.2176 | 0.0019
ERAS-2025-012 | 01 NORTH | 659275 | GROTON_G-BE7 | 115 | 17.164 | 17.1747 | 0.0107
ERAS-2025-012 | 01 NORTH | 659280 | POMONA__-PP7 | 115 | 2.5803 | 2.5805 | 0.0002
ERAS-2025-012 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 6.876 | 6.887 | 0.011
ERAS-2025-012 | 01 NORTH | 659288 | DAY_CNTY-PP7 | 115 | 3.926 | 3.9264 | 0.0004
ERAS-2025-012 | 01 NORTH | 659300 | STANTN.T-BE7 | 115 | 8.0569 | 8.0626 | 0.0057
ERAS-2025-012 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 12.4908 | 12.5502 | 0.0594
ERAS-2025-012 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3183 | 2.3189 | 0.0006
ERAS-2025-012 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 10.0005 | 10.0214 | 0.0209
ERAS-2025-012 | 01 NORTH | 659330 | SPRNGBRK-BE3 | 345 | 9.5807 | 9.6047 | 0.024
ERAS-2025-012 | 01 NORTH | 659331 | SPRNGBRK-BE7 | 115 | 16.1922 | 16.2121 | 0.0199
ERAS-2025-012 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 13.4425 | 13.4847 | 0.0422
ERAS-2025-012 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 17.445 | 17.49 | 0.045
ERAS-2025-012 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.7072 | 8.7362 | 0.029
ERAS-2025-012 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.6327 | 12.6683 | 0.0356
ERAS-2025-012 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.9594 | 7.9607 | 0.0013
ERAS-2025-012 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 13.0653 | 13.0766 | 0.0113
ERAS-2025-012 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 13.1524 | 13.1639 | 0.0115
ERAS-2025-012 | 01 NORTH | 659355 | CRANECRK-BE3 | 345 | 6.2528 | 6.2858 | 0.033
ERAS-2025-012 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 9.2895 | 9.3034 | 0.0139
ERAS-2025-012 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 6.876 | 6.887 | 0.011
ERAS-2025-012 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 10.4997 | 10.5863 | 0.0866
ERAS-2025-012 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.3014 | 12.3408 | 0.0394
ERAS-2025-012 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 8.3126 | 8.3498 | 0.0372
ERAS-2025-012 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 15.4157 | 15.4583 | 0.0426
ERAS-2025-012 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 12.0746 | 12.1242 | 0.0496
ERAS-2025-012 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 21.1841 | 21.2274 | 0.0433
ERAS-2025-012 | 01 NORTH | 659404 | HAUGEN__-PP3 | 345 | 4.592 | 4.5994 | 0.0074
ERAS-2025-012 | 01 NORTH | 659408 | CAMPBL._-PP4 | 230 | 3.5194 | 3.5203 | 0.0009
ERAS-2025-012 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 17.2715 | 17.815 | 0.5435
ERAS-2025-012 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.2012 | 4.2057 | 0.0045
ERAS-2025-012 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-012 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.2715 | 6.28 | 0.0085
ERAS-2025-012 | 01 NORTH | 659424 | LO.LS-CC-BE3 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-012 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.7072 | 8.7362 | 0.029
ERAS-2025-012 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.3837 | 6.392 | 0.0083
ERAS-2025-012 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.3523 | 6.3604 | 0.0081
ERAS-2025-012 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9418 | 1.9422 | 0.0004
ERAS-2025-012 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7467 | 1.747 | 0.0003
ERAS-2025-012 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.8451 | 6.8524 | 0.0073
ERAS-2025-012 | 01 NORTH | 659450 | BRADY___-PP4 | 230 | 4.7828 | 4.7859 | 0.0031
ERAS-2025-012 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 21.0723 | 21.1154 | 0.0431
ERAS-2025-012 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 21.0858 | 21.129 | 0.0432
ERAS-2025-012 | 01 NORTH | 659472 | CROCKER_-UA3 | 345 | 6.0307 | 6.0352 | 0.0045
ERAS-2025-012 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.2164 | 6.2303 | 0.0139
ERAS-2025-012 | 01 NORTH | 659490 | OLIVR4.H-UA3 | 345 | 12.9114 | 13.5922 | 0.6808
ERAS-2025-012 | 01 NORTH | 659509 | REDBUTTE-UA4 | 230 | 7.6045 | 7.6929 | 0.0884
ERAS-2025-012 | 01 NORTH | 659543 | PICKCITY-RR7 | 115 | 10.3151 | 10.3265 | 0.0114
ERAS-2025-012 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9418 | 1.9422 | 0.0004
ERAS-2025-012 | 01 NORTH | 659575 | PIONEER_-BE3 | 345 | 12.7236 | 12.7549 | 0.0313
ERAS-2025-012 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.3548 | 7.366 | 0.0112
ERAS-2025-012 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.5775 | 9.5829 | 0.0054
ERAS-2025-012 | 01 NORTH | 661029 | ESTBMRK7 | 115 | 15.93 | 15.9499 | 0.0199
ERAS-2025-012 | 01 NORTH | 661035 | GLENHAM7 | 115 | 3.8642 | 3.8647 | 0.0005
ERAS-2025-012 | 01 NORTH | 661037 | BOWDLE_EAST7 | 115 | 1.5952 | 1.5953 | 0.0001
ERAS-2025-012 | 01 NORTH | 661038 | GLENHAM4 | 230 | 3.7352 | 3.7361 | 0.0009
ERAS-2025-012 | 01 NORTH | 661039 | MOBRIDG7 | 115 | 2.5483 | 2.5485 | 0.0002
ERAS-2025-012 | 01 NORTH | 661041 | MCINTSH7 | 115 | 0.9962 | 0.9962 | 0
ERAS-2025-012 | 01 NORTH | 661053 | MANDAN 4 | 230 | 15.2141 | 15.2404 | 0.0263
ERAS-2025-012 | 01 NORTH | 661060 | LINTON_NW7 | 115 | 1.3971 | 1.3973 | 0.0002
ERAS-2025-012 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.6716 | 12.7073 | 0.0357
ERAS-2025-012 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.7157 | 13.7347 | 0.019
ERAS-2025-012 | 01 NORTH | 672603 | BDV 4 | 230 | 4.6311 | 4.6332 | 0.0021
ERAS-2025-012 | 01 NORTH | 672665 | TABLELAND 4 | 230 | 10.0058 | 10.0086 | 0.0028
ERAS-2025-012 | 01 NORTH | 672702 | TB-PST1 | 230 | 4.2176 | 4.2192 | 0.0016
ERAS-2025-012 | 01 NORTH | 673665 | ES-PV-POI | 230 | 8.1986 | 8.2005 | 0.0019
ERAS-2025-012 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.2316 | 3.2359 | 0.0043
ERAS-2025-012 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 19.8583 | 21.5549 | 1.6966
ERAS-2025-012 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 11.8123 | 11.8598 | 0.0475
ERAS-2025-012 | 01 NORTH | 788737 | ERA-11 | 345 | 18.9706 | 20.4972 | 1.5266
ERAS-2025-012 | 01 NORTH | 788740 | ERA-12 | 345 | 18.7926 | 20.4972 | 1.7046
ERAS-2025-035 | 01 NORTH | 620362 | OAKES 4 | 230 | 5.8844 | 5.8906 | 0.0062
ERAS-2025-035 | 01 NORTH | 652209 | SUMMIT-8 | 69 | 2.833 | 2.8337 | 0.0007
ERAS-2025-035 | 01 NORTH | 652242 | WATERT18 | 69 | 4.1546 | 4.155 | 0.0004
ERAS-2025-035 | 01 NORTH | 652250 | GROTON18 | 69 | 4.2687 | 4.2767 | 0.008
ERAS-2025-035 | 01 NORTH | 652253 | GROTON2 8 | 69 | 1.9361 | 1.9377 | 0.0016
ERAS-2025-035 | 01 NORTH | 652284 | HURON 8 | 69 | 4.3145 | 4.3161 | 0.0016
ERAS-2025-035 | 01 NORTH | 652361 | ROBERTSCTY8 | 69 | 2.1389 | 2.1392 | 0.0003
ERAS-2025-035 | 01 NORTH | 652432 | EDGELEY7 | 115 | 3.4494 | 3.4509 | 0.0015
ERAS-2025-035 | 01 NORTH | 652438 | FORMAN 7 | 115 | 7.9163 | 7.9202 | 0.0039
ERAS-2025-035 | 01 NORTH | 652455 | ROBERTSCTY7 | 115 | 3.3632 | 3.3644 | 0.0012
ERAS-2025-035 | 01 NORTH | 652512 | GROTON 7 | 115 | 17.2857 | 17.5054 | 0.2197
ERAS-2025-035 | 01 NORTH | 652514 | HURON 4 | 230 | 11.3624 | 11.3783 | 0.0159
ERAS-2025-035 | 01 NORTH | 652515 | HURON 7 | 115 | 15.5399 | 15.576 | 0.0361
ERAS-2025-035 | 01 NORTH | 652522 | SUMMIT-7 | 115 | 4.9205 | 4.924 | 0.0035
ERAS-2025-035 | 01 NORTH | 652528 | WOONSKT7 | 115 | 5.7178 | 5.7192 | 0.0014
ERAS-2025-035 | 01 NORTH | 652530 | WATERTN4 | 230 | 15.1404 | 15.157 | 0.0166
ERAS-2025-035 | 01 NORTH | 652531 | WATERTN7 | 115 | 14.5817 | 14.5893 | 0.0076
ERAS-2025-035 | 01 NORTH | 652568 | GROTONSOUTH7 | 115 | 17.3654 | 17.585 | 0.2196
ERAS-2025-035 | 01 NORTH | 652630 | WATERTNCAP 4 | 230 | 14.9609 | 14.9771 | 0.0162
ERAS-2025-035 | 01 NORTH | 655035 | MOS-ARLG-ER8 | 69 | 1.8067 | 1.8067 | 0
ERAS-2025-035 | 01 NORTH | 655046 | MOS-LKPR-ER8 | 69 | 2.0017 | 2.0018 | 0.0001
ERAS-2025-035 | 01 NORTH | 655047 | MOS-BRES-ER8 | 69 | 2.3763 | 2.3764 | 0.0001
ERAS-2025-035 | 01 NORTH | 655054 | MOS-RDFL-ER8 | 69 | 2.1047 | 2.1055 | 0.0008
ERAS-2025-035 | 01 NORTH | 655055 | SW-YALE-ER8 | 69 | 1.2205 | 1.2206 | 0.0001
ERAS-2025-035 | 01 NORTH | 655057 | MOS-LADL-ER8 | 69 | 1.6117 | 1.6121 | 0.0004
ERAS-2025-035 | 01 NORTH | 655058 | MOS-HRON-ER8 | 69 | 2.9993 | 3.0001 | 0.0008
ERAS-2025-035 | 01 NORTH | 655059 | MOS-ASHT-ER8 | 69 | 1.6838 | 1.6843 | 0.0005
ERAS-2025-035 | 01 NORTH | 655061 | MOS-TULR-ER8 | 69 | 1.5239 | 1.5243 | 0.0004
ERAS-2025-035 | 01 NORTH | 655062 | MOS-YALE-ER8 | 69 | 1.4479 | 1.448 | 0.0001
ERAS-2025-035 | 01 NORTH | 655063 | SW-HURN1-ER8 | 69 | 4.244 | 4.2455 | 0.0015
ERAS-2025-035 | 01 NORTH | 655065 | MOS-YLTI-ER8 | 69 | 1.6794 | 1.6797 | 0.0003
ERAS-2025-035 | 01 NORTH | 655067 | SW-HURN3-ER8 | 69 | 4.299 | 4.3006 | 0.0016
ERAS-2025-035 | 01 NORTH | 655068 | MOS-CRKR-ER8 | 69 | 1.4718 | 1.4721 | 0.0003
ERAS-2025-035 | 01 NORTH | 655069 | MOS-WOLS-ER8 | 69 | 2.3312 | 2.3317 | 0.0005
ERAS-2025-035 | 01 NORTH | 655071 | MOS-DAK-ER8 | 69 | 1.0817 | 1.0818 | 0.0001
ERAS-2025-035 | 01 NORTH | 655072 | SW-SANDC-ER8 | 69 | 2.43 | 2.4302 | 0.0002
ERAS-2025-035 | 01 NORTH | 655082 | MOS-CLRM-ER8 | 69 | 2.9368 | 2.9445 | 0.0077
ERAS-2025-035 | 01 NORTH | 655083 | MOS-BRTO-ER8 | 69 | 1.9106 | 1.9116 | 0.001
ERAS-2025-035 | 01 NORTH | 655085 | MOS-SWAB-ER8 | 69 | 1.2892 | 1.2949 | 0.0057
ERAS-2025-035 | 01 NORTH | 655088 | MOS-MINA-ER8 | 69 | 3.166 | 3.2009 | 0.0349
ERAS-2025-035 | 01 NORTH | 655089 | SW-IPABD-ER8 | 69 | 3.0015 | 3.0094 | 0.0079
ERAS-2025-035 | 01 NORTH | 655090 | MOS-STRF-ER8 | 69 | 1.8174 | 1.8189 | 0.0015
ERAS-2025-035 | 01 NORTH | 655107 | MOS-CSTL-ER8 | 69 | 2.1072 | 2.1072 | 0
ERAS-2025-035 | 01 NORTH | 655108 | MOS-RVLE-ER8 | 69 | 2.9216 | 2.9218 | 0.0002
ERAS-2025-035 | 01 NORTH | 655110 | MOS-BGST-ER8 | 69 | 1.3144 | 1.3146 | 0.0002
ERAS-2025-035 | 01 NORTH | 655111 | SW-SHERI-ER8 | 69 | 3.4674 | 3.4676 | 0.0002
ERAS-2025-035 | 01 NORTH | 655112 | MOS-DMPS-ER8 | 69 | 1.82 | 1.82 | 0
ERAS-2025-035 | 01 NORTH | 655115 | MOS-CLRK-ER8 | 69 | 1.1654 | 1.1656 | 0.0002
ERAS-2025-035 | 01 NORTH | 655117 | SW-HENRY-ER8 | 69 | 1.3344 | 1.3345 | 0.0001
ERAS-2025-035 | 01 NORTH | 655118 | MOS-MARV-ER8 | 69 | 1.8616 | 1.8619 | 0.0003
ERAS-2025-035 | 01 NORTH | 655120 | SW-HAYTI-ER8 | 69 | 1.5339 | 1.534 | 0.0001
ERAS-2025-035 | 01 NORTH | 655121 | MOS-PEEV-ER8 | 69 | 1.2326 | 1.2327 | 0.0001
ERAS-2025-035 | 01 NORTH | 655122 | MOS-FLRN-ER8 | 69 | 1.3273 | 1.3273 | 0
ERAS-2025-035 | 01 NORTH | 655123 | SW-VICTP-ER8 | 69 | 1.9532 | 1.9535 | 0.0003
ERAS-2025-035 | 01 NORTH | 655125 | MOS-ORTY-ER8 | 69 | 1.8808 | 1.8811 | 0.0003
ERAS-2025-035 | 01 NORTH | 655156 | SW-IPSWI-ER8 | 69 | 2.293 | 2.3114 | 0.0184
ERAS-2025-035 | 01 NORTH | 655157 | SW-WETON-ER8 | 69 | 3.573 | 3.6174 | 0.0444
ERAS-2025-035 | 01 NORTH | 655159 | RICHMOND-ER8 | 69 | 4.2343 | 4.2964 | 0.0621
ERAS-2025-035 | 01 NORTH | 655164 | MOS-LMIS-ER8 | 69 | 1.2623 | 1.2623 | 0
ERAS-2025-035 | 01 NORTH | 655207 | CTYARLG1-ER8 | 69 | 1.7155 | 1.7156 | 0.0001
ERAS-2025-035 | 01 NORTH | 655219 | BRUCE-ER8 | 69 | 2.1464 | 2.1464 | 0
ERAS-2025-035 | 01 NORTH | 655220 | ESTELINE-ER8 | 69 | 1.9117 | 1.9118 | 0.0001
ERAS-2025-035 | 01 NORTH | 655227 | REDFIELD-ER8 | 69 | 2.1023 | 2.103 | 0.0007
ERAS-2025-035 | 01 NORTH | 655228 | YALE-ER8 | 69 | 1.2021 | 1.2022 | 0.0001
ERAS-2025-035 | 01 NORTH | 655231 | HURON-ER8 | 69 | 2.9956 | 2.9963 | 0.0007
ERAS-2025-035 | 01 NORTH | 655232 | ASHTON-ER8 | 69 | 1.6552 | 1.6557 | 0.0005
ERAS-2025-035 | 01 NORTH | 655235 | TULARE-ER8 | 69 | 1.1274 | 1.1276 | 0.0002
ERAS-2025-035 | 01 NORTH | 655236 | MORNINGS-ER8 | 69 | 1.9161 | 1.9164 | 0.0003
ERAS-2025-035 | 01 NORTH | 655238 | FRANKFRT-ER8 | 69 | 2.1231 | 2.1238 | 0.0007
ERAS-2025-035 | 01 NORTH | 655239 | WOLSEY-ER8 | 69 | 1.3694 | 1.3695 | 0.0001
ERAS-2025-035 | 01 NORTH | 655241 | VIRGIL-ER8 | 69 | 1.9219 | 1.9222 | 0.0003
ERAS-2025-035 | 01 NORTH | 655242 | CAVOUR-ER8 | 69 | 1.2203 | 1.2204 | 0.0001
ERAS-2025-035 | 01 NORTH | 655243 | CROCKER-ER8 | 69 | 1.3657 | 1.366 | 0.0003
ERAS-2025-035 | 01 NORTH | 655244 | DAKOTA-ER8 | 69 | 1.0048 | 1.0049 | 0.0001
ERAS-2025-035 | 01 NORTH | 655245 | SANDCRK-ER8 | 69 | 2.1344 | 2.1345 | 0.0001
ERAS-2025-035 | 01 NORTH | 655246 | LETCHER-ER8 | 69 | 1.435 | 1.435 | 0
ERAS-2025-035 | 01 NORTH | 655256 | FERNEY-ER8 | 69 | 2.8236 | 2.8271 | 0.0035
ERAS-2025-035 | 01 NORTH | 655257 | ANDOVER-ER8 | 69 | 1.6461 | 1.6471 | 0.001
ERAS-2025-035 | 01 NORTH | 655258 | LANGFORD-ER8 | 69 | 1.1695 | 1.1698 | 0.0003
ERAS-2025-035 | 01 NORTH | 655259 | BRITTON-ER8 | 69 | 0.9198 | 0.92 | 0.0002
ERAS-2025-035 | 01 NORTH | 655260 | WEBSTER-ER8 | 69 | 1.576 | 1.5766 | 0.0006
ERAS-2025-035 | 01 NORTH | 655261 | MANFIELD-ER8 | 69 | 1.3426 | 1.3434 | 0.0008
ERAS-2025-035 | 01 NORTH | 655262 | ABERDEEN-ER8 | 69 | 4.5922 | 4.6191 | 0.0269
ERAS-2025-035 | 01 NORTH | 655263 | IPWEBSTR-ER8 | 69 | 1.4019 | 1.4024 | 0.0005
ERAS-2025-035 | 01 NORTH | 655264 | IPABRDEN-ER8 | 69 | 2.6423 | 2.6485 | 0.0062
ERAS-2025-035 | 01 NORTH | 655265 | NWABRDN-ER8 | 69 | 3.8112 | 3.8442 | 0.033
ERAS-2025-035 | 01 NORTH | 655266 | CLAREMNT-ER8 | 69 | 1.5925 | 1.5945 | 0.002
ERAS-2025-035 | 01 NORTH | 655267 | GROTON-ER8 | 69 | 2.7544 | 2.7577 | 0.0033
ERAS-2025-035 | 01 NORTH | 655268 | SWABRDN-ER8 | 69 | 1.7409 | 1.7514 | 0.0105
ERAS-2025-035 | 01 NORTH | 655269 | BATH-ER8 | 69 | 3.1181 | 3.1268 | 0.0087
ERAS-2025-035 | 01 NORTH | 655270 | CRESBARD-ER8 | 69 | 0.7592 | 0.7594 | 0.0002
ERAS-2025-035 | 01 NORTH | 655286 | GRENVILE-ER8 | 69 | 1.018 | 1.0181 | 0.0001
ERAS-2025-035 | 01 NORTH | 655287 | BIGSTONE-ER8 | 69 | 1.314 | 1.3142 | 0.0002
ERAS-2025-035 | 01 NORTH | 655288 | SHERIDAN-ER8 | 69 | 3.4628 | 3.4631 | 0.0003
ERAS-2025-035 | 01 NORTH | 655291 | HENRY-ER8 | 69 | 1.3159 | 1.316 | 0.0001
ERAS-2025-035 | 01 NORTH | 655292 | MARVIN-ER8 | 69 | 1.5672 | 1.5674 | 0.0002
ERAS-2025-035 | 01 NORTH | 655295 | HAYTI-ER8 | 69 | 1.4404 | 1.4404 | 0
ERAS-2025-035 | 01 NORTH | 655297 | WAVERLY-ER8 | 69 | 1.8945 | 1.8946 | 0.0001
ERAS-2025-035 | 01 NORTH | 655298 | DEMPSTER-ER8 | 69 | 1.4496 | 1.4496 | 0
ERAS-2025-035 | 01 NORTH | 655299 | PEEVER-ER8 | 69 | 1.2311 | 1.2312 | 0.0001
ERAS-2025-035 | 01 NORTH | 655300 | FLORENCE-ER8 | 69 | 0.9373 | 0.9373 | 0
ERAS-2025-035 | 01 NORTH | 655301 | VICTOR-ER8 | 69 | 1.3501 | 1.3502 | 0.0001
ERAS-2025-035 | 01 NORTH | 655302 | WILMOT-ER8 | 69 | 1.7797 | 1.7799 | 0.0002
ERAS-2025-035 | 01 NORTH | 655303 | SISSETON-ER8 | 69 | 1.9896 | 1.9898 | 0.0002
ERAS-2025-035 | 01 NORTH | 655305 | RAUVILLE-ER8 | 69 | 1.2622 | 1.2622 | 0
ERAS-2025-035 | 01 NORTH | 655306 | ORTLEY-ER8 | 69 | 1.8029 | 1.8032 | 0.0003
ERAS-2025-035 | 01 NORTH | 655336 | BURKMERE-ER8 | 69 | 0.5513 | 0.5514 | 0.0001
ERAS-2025-035 | 01 NORTH | 655337 | IPSWICH-ER8 | 69 | 2.2046 | 2.2216 | 0.017
ERAS-2025-035 | 01 NORTH | 655338 | WETONKA-ER8 | 69 | 3.0049 | 3.0357 | 0.0308
ERAS-2025-035 | 01 NORTH | 655339 | PEMBROOK-ER8 | 69 | 3.7922 | 3.8413 | 0.0491
ERAS-2025-035 | 01 NORTH | 655344 | LOOMIS-ER8 | 69 | 1.1775 | 1.1776 | 0.0001
ERAS-2025-035 | 01 NORTH | 655350 | WOODLAND-ER8 | 69 | 1.2132 | 1.2134 | 0.0002
ERAS-2025-035 | 01 NORTH | 655351 | HECLA-ER8 | 69 | 1.207 | 1.2081 | 0.0011
ERAS-2025-035 | 01 NORTH | 655355 | WOONSKT-ER8 | 69 | 3.7987 | 3.7991 | 0.0004
ERAS-2025-035 | 01 NORTH | 655369 | NWPS6661-ER8 | 69 | 1.3949 | 1.3954 | 0.0005
ERAS-2025-035 | 01 NORTH | 655392 | MOS-GRNV-ER8 | 69 | 1.5666 | 1.5668 | 0.0002
ERAS-2025-035 | 01 NORTH | 655395 | NWPS509-ER8 | 69 | 4.2595 | 4.2674 | 0.0079
ERAS-2025-035 | 01 NORTH | 655411 | CRANDALL-ER7 | 115 | 5.5565 | 5.5757 | 0.0192
ERAS-2025-035 | 01 NORTH | 655419 | SW561-ER7 | 115 | 5.7597 | 5.7805 | 0.0208
ERAS-2025-035 | 01 NORTH | 655421 | MOS-CRSB-ER8 | 69 | 0.7597 | 0.76 | 0.0003
ERAS-2025-035 | 01 NORTH | 655422 | MOS-MNFD-ER8 | 69 | 1.3432 | 1.344 | 0.0008
ERAS-2025-035 | 01 NORTH | 655433 | SW-LANGF-ER8 | 69 | 1.1867 | 1.1871 | 0.0004
ERAS-2025-035 | 01 NORTH | 655455 | VEBLEN-ER8 | 69 | 1.2535 | 1.2536 | 0.0001
ERAS-2025-035 | 01 NORTH | 655456 | HILLHEAD-ER8 | 69 | 1.0282 | 1.0282 | 0
ERAS-2025-035 | 01 NORTH | 655457 | BRISTOL-ER7 | 115 | 4.6924 | 4.7021 | 0.0097
ERAS-2025-035 | 01 NORTH | 655458 | BRISTOL-ER8 | 69 | 2.4895 | 2.4912 | 0.0017
ERAS-2025-035 | 01 NORTH | 655462 | ARLNGTN-ER7 | 115 | 6.4321 | 6.433 | 0.0009
ERAS-2025-035 | 01 NORTH | 655463 | ARLNGTN-ER8 | 69 | 3.0703 | 3.0704 | 0.0001
ERAS-2025-035 | 01 NORTH | 655481 | REDFELD-ER7 | 115 | 4.2246 | 4.2302 | 0.0056
ERAS-2025-035 | 01 NORTH | 655482 | REDFELD-ER8 | 69 | 2.8717 | 2.8731 | 0.0014
ERAS-2025-035 | 01 NORTH | 655491 | ORDWAY-ER8 | 69 | 5.874 | 5.9052 | 0.0312
ERAS-2025-035 | 01 NORTH | 655514 | LKPONSET-ER8 | 69 | 2.4871 | 2.4872 | 0.0001
ERAS-2025-035 | 01 NORTH | 655516 | MCSINCRK-ER8 | 69 | 3.8847 | 3.9142 | 0.0295
ERAS-2025-035 | 01 NORTH | 655522 | RICHMOND-ER7 | 115 | 3.98 | 4.1273 | 0.1473
ERAS-2025-035 | 01 NORTH | 655525 | FREDRK-ER7 | 115 | 3.472 | 3.4786 | 0.0066
ERAS-2025-035 | 01 NORTH | 655526 | ELMLAKE-ER7 | 115 | 2.6226 | 2.6263 | 0.0037
ERAS-2025-035 | 01 NORTH | 655527 | LEOLA-ER7 | 115 | 1.6178 | 1.6192 | 0.0014
ERAS-2025-035 | 01 NORTH | 655528 | BROWNCO-ER7 | 115 | 3.4723 | 3.4789 | 0.0066
ERAS-2025-035 | 01 NORTH | 655530 | SW7117-ER8 | 69 | 2.4982 | 2.4988 | 0.0006
ERAS-2025-035 | 01 NORTH | 655536 | ONAKA-ER8 | 69 | 0.5609 | 0.5611 | 0.0002
ERAS-2025-035 | 01 NORTH | 655537 | SW-ONAK-ER8 | 69 | 0.6048 | 0.605 | 0.0002
ERAS-2025-035 | 01 NORTH | 655541 | TRNTO-ER7 | 115 | 4.8248 | 4.8253 | 0.0005
ERAS-2025-035 | 01 NORTH | 655552 | DEUELCO-ER7 | 115 | 5.3163 | 5.3169 | 0.0006
ERAS-2025-035 | 01 NORTH | 658088 | WTREAST7 | 115 | 11.2127 | 11.2169 | 0.0042
ERAS-2025-035 | 01 NORTH | 658089 | WTR15AV7 | 115 | 12.4477 | 12.4531 | 0.0054
ERAS-2025-035 | 01 NORTH | 658090 | WTRTNPP | 115 | 10.7807 | 10.7845 | 0.0038
ERAS-2025-035 | 01 NORTH | 658092 | WTRWEST7 | 115 | 9.7917 | 9.795 | 0.0033
ERAS-2025-035 | 01 NORTH | 658094 | WTRPELI7 | 115 | 9.8913 | 9.8947 | 0.0034
ERAS-2025-035 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.2454 | 6.28 | 0.0346
ERAS-2025-035 | 01 NORTH | 659165 | CROCKER_-BE3 | 345 | 6.5106 | 6.532 | 0.0214
ERAS-2025-035 | 01 NORTH | 659172 | LUDDEN -CP7 | 115 | 2.1911 | 2.1914 | 0.0003
ERAS-2025-035 | 01 NORTH | 659187 | GROTON__-BE7 | 115 | 17.3417 | 17.559 | 0.2173
ERAS-2025-035 | 01 NORTH | 659275 | GROTON_G-BE7 | 115 | 16.9708 | 17.1747 | 0.2039
ERAS-2025-035 | 01 NORTH | 659280 | POMONA__-PP7 | 115 | 2.5797 | 2.5805 | 0.0008
ERAS-2025-035 | 01 NORTH | 659288 | DAY_CNTY-PP7 | 115 | 3.9179 | 3.9264 | 0.0085
ERAS-2025-035 | 01 NORTH | 659310 | ORDWAY__-BE7 | 115 | 7.4504 | 7.4982 | 0.0478
ERAS-2025-035 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.2454 | 6.28 | 0.0346
ERAS-2025-035 | 01 NORTH | 659472 | CROCKER_-UA3 | 345 | 6.0172 | 6.0352 | 0.018
ERAS-2025-035 | 01 NORTH | 660000 | ABR JCT | 115 | 6.4911 | 6.9638 | 0.4727
ERAS-2025-035 | 01 NORTH | 660001 | ABR SIEBRCHT | 115 | 7.3626 | 8.1334 | 0.7708
ERAS-2025-035 | 01 NORTH | 660002 | REDFIELD | 115 | 4.1132 | 4.1675 | 0.0543
ERAS-2025-035 | 01 NORTH | 660003 | HUR WESTPARK | 115 | 9.7888 | 9.8007 | 0.0119
ERAS-2025-035 | 01 NORTH | 660008 | MIT NO.WEST | 115 | 6.0587 | 6.0593 | 0.0006
ERAS-2025-035 | 01 NORTH | 660009 | HUR B TAP | 115 | 15.1587 | 15.1944 | 0.0357
ERAS-2025-035 | 01 NORTH | 660012 | HUR WESTPARK | 69 | 7.2389 | 7.2417 | 0.0028
ERAS-2025-035 | 01 NORTH | 660015 | REDFIELD | 69 | 1.0058 | 1.0072 | 0.0014
ERAS-2025-035 | 01 NORTH | 660021 | ABR INDUSTPK | 115 | 6.1281 | 6.6055 | 0.4774
ERAS-2025-035 | 01 NORTH | 660022 | ABR CITY | 115 | 6.0733 | 6.5136 | 0.4403
ERAS-2025-035 | 01 NORTH | 660040 | DAKOTAACCESS | 115 | 4.5765 | 4.6175 | 0.041
ERAS-2025-035 | 01 NORTH | 660045 | CLARK JCT | 69 | 0.6518 | 0.6519 | 0.0001
ERAS-2025-035 | 01 NORTH | 660092 | WTRTOWN WEST | 69 | 1.3877 | 1.3877 | 0
ERAS-2025-035 | 01 NORTH | 660309 | HUR 9THST J | 69 | 6.3171 | 6.3189 | 0.0018
ERAS-2025-035 | 01 NORTH | 660310 | HUR SO.WEST | 69 | 5.9994 | 6.001 | 0.0016
ERAS-2025-035 | 01 NORTH | 660311 | HUR SO.EAST | 69 | 5.6243 | 5.6255 | 0.0012
ERAS-2025-035 | 01 NORTH | 660312 | HUR GT PLANT | 69 | 5.0942 | 5.095 | 0.0008
ERAS-2025-035 | 01 NORTH | 660313 | HUR 4TH ST | 69 | 5.3544 | 5.3559 | 0.0015
ERAS-2025-035 | 01 NORTH | 660314 | HUR CITY | 69 | 4.5659 | 4.567 | 0.0011
ERAS-2025-035 | 01 NORTH | 660350 | FRANKFORT | 69 | 0.8898 | 0.8908 | 0.001
ERAS-2025-035 | 01 NORTH | 660351 | DOLAND | 69 | 0.8046 | 0.8053 | 0.0007
ERAS-2025-035 | 01 NORTH | 660352 | RAYMOND | 69 | 0.7419 | 0.7425 | 0.0006
ERAS-2025-035 | 01 NORTH | 660353 | OAKTREE W T | 69 | 0.6891 | 0.6896 | 0.0005
ERAS-2025-035 | 01 NORTH | 660354 | GARDENCTYJCT | 69 | 0.7855 | 0.7855 | 0
ERAS-2025-035 | 01 NORTH | 660355 | HENRY | 69 | 0.8288 | 0.8288 | 0
ERAS-2025-035 | 01 NORTH | 660430 | GROTON | 69 | 1.6025 | 1.6036 | 0.0011
ERAS-2025-035 | 01 NORTH | 660431 | GROTON CITY | 69 | 1.5893 | 1.5904 | 0.0011
ERAS-2025-035 | 01 NORTH | 660432 | ANDOVER | 69 | 1.2145 | 1.2152 | 0.0007
ERAS-2025-035 | 01 NORTH | 660433 | BRISTOL JCT | 69 | 0.8412 | 0.8415 | 0.0003
ERAS-2025-035 | 01 NORTH | 660440 | WEBSTER NW | 69 | 0.7133 | 0.7135 | 0.0002
ERAS-2025-035 | 01 NORTH | 660441 | WEBSTER CITY | 69 | 0.6886 | 0.6888 | 0.0002
ERAS-2025-035 | 01 NORTH | 661000 | LEOLA 7 | 115 | 1.5848 | 1.5866 | 0.0018
ERAS-2025-035 | 01 NORTH | 661026 | ELLENDL4 | 230 | 9.1126 | 9.1341 | 0.0215
ERAS-2025-035 | 01 NORTH | 661027 | ELLENDL7 | 115 | 8.109 | 8.1583 | 0.0493
ERAS-2025-035 | 01 NORTH | 661092 | FOXTAIL 4 | 230 | 7.2174 | 7.2272 | 0.0098
ERAS-2025-035 | 01 NORTH | 661093 | MERRCRT4 | 230 | 7.4238 | 7.433 | 0.0092
ERAS-2025-035 | 01 NORTH | 661097 | ELLENDL345 3 | 345 | 6.4184 | 6.4268 | 0.0084
ERAS-2025-035 | 01 NORTH | 661098 | ELLENDL345 4 | 230 | 9.1126 | 9.1341 | 0.0215
ERAS-2025-035 | 01 NORTH | 661992 | G359 MRCRT 4 | 230 | 7.4238 | 7.433 | 0.0092
ERAS-2025-035 | 01 NORTH | 788911 | ERA-2025-035 | 115 | 7.0868 | 7.8606 | 0.7738
ERAS-2025-001 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.4425 | 23.4531 | 0.0106
ERAS-2025-001 | 02 NEBRASKA | 640155 | DAVEY 7 | 115 | 11.6178 | 11.7113 | 0.0935
ERAS-2025-001 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 6.0441 | 6.0474 | 0.0033
ERAS-2025-001 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 5.3773 | 5.387 | 0.0097
ERAS-2025-001 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 30.5411 | 30.5727 | 0.0316
ERAS-2025-001 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.602 | 12.6196 | 0.0176
ERAS-2025-001 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 36.2587 | 36.2853 | 0.0266
ERAS-2025-001 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 22.2125 | 22.2307 | 0.0182
ERAS-2025-001 | 02 NEBRASKA | 647014 | S914A 8 | 69 | 11.3584 | 11.3621 | 0.0037
ERAS-2025-001 | 02 NEBRASKA | 647846 | S6846 8 | 69 | 7.3653 | 7.3663 | 0.001
ERAS-2025-001 | 02 NEBRASKA | 647914 | S914 8 | 69 | 7.7928 | 7.7942 | 0.0014
ERAS-2025-001 | 02 NEBRASKA | 647988 | S988 8 | 69 | 2.886 | 2.8863 | 0.0003
ERAS-2025-001 | 02 NEBRASKA | 648530 | PLTV 8 | 69 | 7.3564 | 7.3574 | 0.001
ERAS-2025-001 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 18.1049 | 18.1563 | 0.0514
ERAS-2025-001 | 02 NEBRASKA | 650169 | 70&BLUFF 5 | 161 | 8.8988 | 8.937 | 0.0382
ERAS-2025-001 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.7244 | 21.8074 | 0.083
ERAS-2025-001 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.7827 | 21.8425 | 0.0598
ERAS-2025-001 | 02 NEBRASKA | 650205 | 4&MORTON 7 | 115 | 21.7244 | 21.9165 | 0.1921
ERAS-2025-001 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.6397 | 21.7525 | 0.1128
ERAS-2025-001 | 02 NEBRASKA | 650212 | NW5&BENTON7 | 115 | 21.6891 | 21.8695 | 0.1804
ERAS-2025-001 | 02 NEBRASKA | 650215 | 19&ALVO 7 | 115 | 24.2376 | 24.5004 | 0.2628
ERAS-2025-001 | 02 NEBRASKA | 650226 | NW12&ARBOR7 | 115 | 18.0884 | 18.2089 | 0.1205
ERAS-2025-001 | 02 NEBRASKA | 650228 | 27FLETCHER7 | 115 | 22.3041 | 22.5192 | 0.2151
ERAS-2025-001 | 02 NEBRASKA | 650233 | 33SUPERIOR7 | 115 | 22.9203 | 23.1355 | 0.2152
ERAS-2025-001 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 27.7995 | 28.0299 | 0.2304
ERAS-2025-001 | 02 NEBRASKA | 650257 | 56&ELK TAP7 | 115 | 25.8685 | 26.1002 | 0.2317
ERAS-2025-001 | 02 NEBRASKA | 650259 | 59CRNHUSKR7 | 115 | 21.9237 | 22.1227 | 0.199
ERAS-2025-001 | 02 NEBRASKA | 650260 | 56&Q 7 | 115 | 23.3639 | 23.5798 | 0.2159
ERAS-2025-001 | 02 NEBRASKA | 650261 | 56&I80 7 | 115 | 23.2283 | 23.6147 | 0.3864
ERAS-2025-001 | 02 NEBRASKA | 650262 | 57&GARLAND7 | 115 | 25.8511 | 26.1313 | 0.2802
ERAS-2025-001 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.9218 | 30.3248 | 0.403
ERAS-2025-001 | 02 NEBRASKA | 650269 | 70&BLUFF 7 | 115 | 25.9542 | 26.5056 | 0.5514
ERAS-2025-001 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.936 | 28.2073 | 0.2713
ERAS-2025-001 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.5245 | 25.7319 | 0.2074
ERAS-2025-001 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 22.1536 | 22.346 | 0.1924
ERAS-2025-001 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 22.9119 | 23.1293 | 0.2174
ERAS-2025-001 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 22.0783 | 22.2145 | 0.1362
ERAS-2025-001 | 02 NEBRASKA | 650275 | 84&BLUFF 7 | 115 | 27.2912 | 28.0109 | 0.7197
ERAS-2025-001 | 02 NEBRASKA | 650277 | TBGS_A 7 | 115 | 25.9394 | 26.6638 | 0.7244
ERAS-2025-001 | 02 NEBRASKA | 650278 | TBGS_B 7 | 115 | 26.1271 | 26.7777 | 0.6506
ERAS-2025-001 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.9248 | 22.1839 | 0.2591
ERAS-2025-001 | 02 NEBRASKA | 650283 | WAVERLY 7 | 115 | 21.3951 | 21.7057 | 0.3106
ERAS-2025-001 | 02 NEBRASKA | 650284 | 84FLETCHER7 | 115 | 25.2612 | 25.7088 | 0.4476
ERAS-2025-001 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.6612 | 33.0117 | 0.3505
ERAS-2025-001 | 02 NEBRASKA | 788700 | ERAS-01 | 115 | 24.5947 | 25.32 | 0.7253
ERAS-2025-006 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0224 | 16.0244 | 0.002
ERAS-2025-006 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.3875 | 24.3879 | 0.0004
ERAS-2025-006 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.0332 | 13.0342 | 0.001
ERAS-2025-006 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.6247 | 12.6316 | 0.0069
ERAS-2025-006 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 19.4414 | 19.4484 | 0.007
ERAS-2025-006 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 13.4863 | 13.4939 | 0.0076
ERAS-2025-006 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 13.4637 | 13.4712 | 0.0075
ERAS-2025-006 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 13.097 | 13.1108 | 0.0138
ERAS-2025-006 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.9794 | 14.9848 | 0.0054
ERAS-2025-006 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.6583 | 12.6652 | 0.0069
ERAS-2025-006 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.4183 | 11.4286 | 0.0103
ERAS-2025-006 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.7697 | 8.7711 | 0.0014
ERAS-2025-006 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.7895 | 14.8033 | 0.0138
ERAS-2025-006 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 14.9168 | 14.921 | 0.0042
ERAS-2025-006 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.6461 | 10.6482 | 0.0021
ERAS-2025-006 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.0536 | 12.0563 | 0.0027
ERAS-2025-006 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.461 | 6.4716 | 0.0106
ERAS-2025-006 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 6.461 | 6.4716 | 0.0106
ERAS-2025-006 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.5332 | 4.5391 | 0.0059
ERAS-2025-006 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 6.4077 | 6.4175 | 0.0098
ERAS-2025-006 | 03 CENTRAL | 530623 | RICE 3 | 115 | 7.4168 | 7.4303 | 0.0135
ERAS-2025-006 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.7308 | 4.7433 | 0.0125
ERAS-2025-006 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 3.0664 | 3.0707 | 0.0043
ERAS-2025-006 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 5.2218 | 5.2279 | 0.0061
ERAS-2025-006 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.9882 | 10.9961 | 0.0079
ERAS-2025-006 | 03 CENTRAL | 530724 | CENTENNIAL3 | 115 | 5.903 | 5.9184 | 0.0154
ERAS-2025-006 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 19.8947 | 19.9057 | 0.011
ERAS-2025-006 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 23.9972 | 24.0341 | 0.0369
ERAS-2025-006 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.9974 | 11.0515 | 0.0541
ERAS-2025-006 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 17.5223 | 17.5462 | 0.0239
ERAS-2025-006 | 03 CENTRAL | 532769 | LANG 7 | 345 | 17.4125 | 17.4361 | 0.0236
ERAS-2025-006 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.1915 | 13.2079 | 0.0164
ERAS-2025-006 | 03 CENTRAL | 532771 | RENO 7 | 345 | 13.1363 | 14.3712 | 1.2349
ERAS-2025-006 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 13.0458 | 13.2814 | 0.2356
ERAS-2025-006 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0071 | 17.0171 | 0.01
ERAS-2025-006 | 03 CENTRAL | 532776 | READWF 7 | 345 | 14.522 | 14.5382 | 0.0162
ERAS-2025-006 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7765 | 9.7844 | 0.0079
ERAS-2025-006 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4099 | 9.4172 | 0.0073
ERAS-2025-006 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 22.7384 | 22.9825 | 0.2441
ERAS-2025-006 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2585 | 7.2773 | 0.0188
ERAS-2025-006 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0287 | 6.0409 | 0.0122
ERAS-2025-006 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0075 | 5.0156 | 0.0081
ERAS-2025-006 | 03 CENTRAL | 532786 | FR3 WF7 | 345 | 4.6684 | 4.6716 | 0.0032
ERAS-2025-006 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.4103 | 7.4243 | 0.014
ERAS-2025-006 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.9609 | 20.0701 | 0.1092
ERAS-2025-006 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.1884 | 7.1965 | 0.0081
ERAS-2025-006 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 17.9255 | 17.9293 | 0.0038
ERAS-2025-006 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 19.2297 | 19.2895 | 0.0598
ERAS-2025-006 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.7458 | 5.7507 | 0.0049
ERAS-2025-006 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 26.116 | 26.5127 | 0.3967
ERAS-2025-006 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.192 | 18.2026 | 0.0106
ERAS-2025-006 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 15.8398 | 15.8907 | 0.0509
ERAS-2025-006 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.2395 | 16.2471 | 0.0076
ERAS-2025-006 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.4058 | 10.4162 | 0.0104
ERAS-2025-006 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.175 | 9.183 | 0.008
ERAS-2025-006 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.597 | 13.6023 | 0.0053
ERAS-2025-006 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.6435 | 10.6736 | 0.0301
ERAS-2025-006 | 03 CENTRAL | 532814 | FR4345KV-TAP | 345 | 8.6878 | 8.7006 | 0.0128
ERAS-2025-006 | 03 CENTRAL | 532837 | G15052_T | 345 | 12.8341 | 12.8488 | 0.0147
ERAS-2025-006 | 03 CENTRAL | 532852 | JEC 6 | 230 | 24.349 | 24.3712 | 0.0222
ERAS-2025-006 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.9685 | 21.9808 | 0.0123
ERAS-2025-006 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.3448 | 14.3653 | 0.0205
ERAS-2025-006 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 10.8506 | 10.9454 | 0.0948
ERAS-2025-006 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 9.6723 | 9.7345 | 0.0622
ERAS-2025-006 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 15.1483 | 15.2818 | 0.1335
ERAS-2025-006 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.3448 | 8.3643 | 0.0195
ERAS-2025-006 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 5.5633 | 5.5713 | 0.008
ERAS-2025-006 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 9.9378 | 9.9421 | 0.0043
ERAS-2025-006 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 10.9653 | 10.9709 | 0.0056
ERAS-2025-006 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 5.8714 | 5.873 | 0.0016
ERAS-2025-006 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 30.3012 | 30.3967 | 0.0955
ERAS-2025-006 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 12.0702 | 12.0812 | 0.011
ERAS-2025-006 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 20.1 | 20.1409 | 0.0409
ERAS-2025-006 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 12.2045 | 12.2163 | 0.0118
ERAS-2025-006 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 23.3435 | 23.3881 | 0.0446
ERAS-2025-006 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.3005 | 6.3023 | 0.0018
ERAS-2025-006 | 03 CENTRAL | 532994 | WICHTA11_4 | 138 | 38.918 | 39.1511 | 0.2331
ERAS-2025-006 | 03 CENTRAL | 532997 | WICHTA12_4 | 138 | 39.4567 | 39.6957 | 0.239
ERAS-2025-006 | 03 CENTRAL | 532998 | G16-111-TAP | 345 | 11.91 | 12.6933 | 0.7833
ERAS-2025-006 | 03 CENTRAL | 532999 | GEN-2016-111 | 345 | 7.4671 | 7.7483 | 0.2812
ERAS-2025-006 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 10.8459 | 10.8933 | 0.0474
ERAS-2025-006 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.7824 | 7.8138 | 0.0314
ERAS-2025-006 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 12.9091 | 12.9561 | 0.047
ERAS-2025-006 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 9.4203 | 9.4454 | 0.0251
ERAS-2025-006 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 20.8002 | 20.844 | 0.0438
ERAS-2025-006 | 03 CENTRAL | 533025 | CT-SOLAR | 138 | 35.7243 | 35.9179 | 0.1936
ERAS-2025-006 | 03 CENTRAL | 533031 | GODDARD4 | 138 | 20.1216 | 20.1873 | 0.0657
ERAS-2025-006 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 23.3506 | 23.4144 | 0.0638
ERAS-2025-006 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 16.0517 | 16.0775 | 0.0258
ERAS-2025-006 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 19.7649 | 19.804 | 0.0391
ERAS-2025-006 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 24.482 | 24.5698 | 0.0878
ERAS-2025-006 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 26.1688 | 26.2258 | 0.057
ERAS-2025-006 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 40.2088 | 40.4554 | 0.2466
ERAS-2025-006 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 40.1521 | 40.3977 | 0.2456
ERAS-2025-006 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 24.2544 | 24.3165 | 0.0621
ERAS-2025-006 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 24.2543 | 24.3164 | 0.0621
ERAS-2025-006 | 03 CENTRAL | 533047 | GILL 4 | 138 | 24.2505 | 24.3126 | 0.0621
ERAS-2025-006 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 21.7879 | 21.8421 | 0.0542
ERAS-2025-006 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 19.305 | 19.3551 | 0.0501
ERAS-2025-006 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 23.5648 | 23.6412 | 0.0764
ERAS-2025-006 | 03 CENTRAL | 533056 | WHARV4 | 138 | 7.9705 | 8.003 | 0.0325
ERAS-2025-006 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 21.7694 | 21.816 | 0.0466
ERAS-2025-006 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 32.3721 | 32.4501 | 0.078
ERAS-2025-006 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 9.7907 | 9.7961 | 0.0054
ERAS-2025-006 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 22.9143 | 23.0116 | 0.0973
ERAS-2025-006 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 21.0661 | 21.1045 | 0.0384
ERAS-2025-006 | 03 CENTRAL | 533069 | BUFFALO4 | 138 | 33.875 | 34.0831 | 0.2081
ERAS-2025-006 | 03 CENTRAL | 533071 | WACO 4 | 138 | 23.4185 | 23.4769 | 0.0584
ERAS-2025-006 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 29.5591 | 29.6905 | 0.1314
ERAS-2025-006 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 26.9824 | 27.0427 | 0.0603
ERAS-2025-006 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.8414 | 15.8499 | 0.0085
ERAS-2025-006 | 03 CENTRAL | 533310 | WMBROS 3 | 115 | 7.3958 | 7.3989 | 0.0031
ERAS-2025-006 | 03 CENTRAL | 533311 | WMBROSJ3 | 115 | 7.4746 | 7.4778 | 0.0032
ERAS-2025-006 | 03 CENTRAL | 533320 | CLAYCSS3 | 115 | 2.446 | 2.4467 | 0.0007
ERAS-2025-006 | 03 CENTRAL | 533323 | CLAYCTR3 | 115 | 3.1203 | 3.1215 | 0.0012
ERAS-2025-006 | 03 CENTRAL | 533324 | TCRILEY 3 | 115 | 2.1448 | 2.1453 | 0.0005
ERAS-2025-006 | 03 CENTRAL | 533325 | CLAYGEN3 | 115 | 2.3272 | 2.3279 | 0.0007
ERAS-2025-006 | 03 CENTRAL | 533328 | FT JCT 3 | 115 | 16.2151 | 16.2428 | 0.0277
ERAS-2025-006 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 19.601 | 19.6298 | 0.0288
ERAS-2025-006 | 03 CENTRAL | 533336 | GEARY 3 | 115 | 20.4215 | 20.4695 | 0.048
ERAS-2025-006 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8868 | 3.8889 | 0.0021
ERAS-2025-006 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.4638 | 3.4655 | 0.0017
ERAS-2025-006 | 03 CENTRAL | 533362 | CHAPMAN3 | 115 | 12.0688 | 12.0858 | 0.017
ERAS-2025-006 | 03 CENTRAL | 533366 | FLORENC3 | 115 | 2.9951 | 2.9973 | 0.0022
ERAS-2025-006 | 03 CENTRAL | 533367 | BERG 3 | 115 | 12.102 | 12.141 | 0.039
ERAS-2025-006 | 03 CENTRAL | 533369 | JADE 3 | 115 | 3.2775 | 3.2811 | 0.0036
ERAS-2025-006 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.9808 | 13.0207 | 0.0399
ERAS-2025-006 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 13.4637 | 13.5119 | 0.0482
ERAS-2025-006 | 03 CENTRAL | 533377 | SCHILNG3 | 115 | 11.2891 | 11.3223 | 0.0332
ERAS-2025-006 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 11.0452 | 11.0778 | 0.0326
ERAS-2025-006 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 19.4278 | 19.5295 | 0.1017
ERAS-2025-006 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.9254 | 7.9434 | 0.018
ERAS-2025-006 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 11.6095 | 11.6888 | 0.0793
ERAS-2025-006 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 11.8722 | 11.9552 | 0.083
ERAS-2025-006 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 27.0781 | 27.5618 | 0.4837
ERAS-2025-006 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 10.1821 | 10.2534 | 0.0713
ERAS-2025-006 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 11.7779 | 11.8762 | 0.0983
ERAS-2025-006 | 03 CENTRAL | 533416 | RENO 3 | 115 | 29.4608 | 30.3753 | 0.9145
ERAS-2025-006 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 15.1041 | 15.1725 | 0.0684
ERAS-2025-006 | 03 CENTRAL | 533419 | HEC 3 | 115 | 24.7287 | 25.1323 | 0.4036
ERAS-2025-006 | 03 CENTRAL | 533420 | WHARV3 | 115 | 8.9131 | 8.954 | 0.0409
ERAS-2025-006 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 26.3527 | 26.8049 | 0.4522
ERAS-2025-006 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 11.5829 | 11.6194 | 0.0365
ERAS-2025-006 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 14.2759 | 14.3363 | 0.0604
ERAS-2025-006 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 15.0354 | 15.102 | 0.0666
ERAS-2025-006 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 9.1688 | 9.2161 | 0.0473
ERAS-2025-006 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 7.0661 | 7.0942 | 0.0281
ERAS-2025-006 | 03 CENTRAL | 533434 | SALTCRK3 | 115 | 10.5849 | 10.6615 | 0.0766
ERAS-2025-006 | 03 CENTRAL | 533435 | 3 VANBU3 | 115 | 11.2597 | 11.3459 | 0.0862
ERAS-2025-006 | 03 CENTRAL | 533437 | MOHAWK3 | 115 | 11.4983 | 11.536 | 0.0377
ERAS-2025-006 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 15.3041 | 15.3764 | 0.0723
ERAS-2025-006 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 8.2465 | 8.266 | 0.0195
ERAS-2025-006 | 03 CENTRAL | 533440 | 43LORAN | 115 | 16.3022 | 16.479 | 0.1768
ERAS-2025-006 | 03 CENTRAL | 533455 | TWR 33 3 | 115 | 13.1653 | 13.2816 | 0.1163
ERAS-2025-006 | 03 CENTRAL | 533502 | CESSNA 2 | 69 | 4.77 | 4.7789 | 0.0089
ERAS-2025-006 | 03 CENTRAL | 533503 | CESSNAJ2 | 69 | 4.8388 | 4.848 | 0.0092
ERAS-2025-006 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.2839 | 4.2914 | 0.0075
ERAS-2025-006 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.3141 | 4.3217 | 0.0076
ERAS-2025-006 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 8.6154 | 8.6464 | 0.031
ERAS-2025-006 | 03 CENTRAL | 533507 | 18&PLUM2 | 69 | 4.9529 | 4.9625 | 0.0096
ERAS-2025-006 | 03 CENTRAL | 533508 | E MADSN2 | 69 | 8.2074 | 8.2353 | 0.0279
ERAS-2025-006 | 03 CENTRAL | 533509 | 11HALST2 | 69 | 5.6691 | 5.6817 | 0.0126
ERAS-2025-006 | 03 CENTRAL | 533510 | F MONRO2 | 69 | 8.0004 | 8.0269 | 0.0265
ERAS-2025-006 | 03 CENTRAL | 533511 | 14LORAN2 | 69 | 5.3087 | 5.3197 | 0.011
ERAS-2025-006 | 03 CENTRAL | 533513 | HEC 2 | 69 | 7.5117 | 7.5337 | 0.022
ERAS-2025-006 | 03 CENTRAL | 533516 | MAPLE J2 | 69 | 8.1368 | 8.1643 | 0.0275
ERAS-2025-006 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 7.1386 | 7.1599 | 0.0213
ERAS-2025-006 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.8935 | 6.9133 | 0.0198
ERAS-2025-006 | 03 CENTRAL | 533520 | 2ND ELM2 | 69 | 6.8688 | 6.8883 | 0.0195
ERAS-2025-006 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.0638 | 6.0782 | 0.0144
ERAS-2025-006 | 03 CENTRAL | 533522 | 17HUXMN2 | 69 | 5.4687 | 5.4804 | 0.0117
ERAS-2025-006 | 03 CENTRAL | 533523 | 17 PLUM2 | 69 | 5.0071 | 5.0169 | 0.0098
ERAS-2025-006 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 7.3668 | 7.3894 | 0.0226
ERAS-2025-006 | 03 CENTRAL | 533597 | MIDIAN 2 | 69 | 18.4985 | 18.512 | 0.0135
ERAS-2025-006 | 03 CENTRAL | 533624 | BURLING2 | 69 | 5.4528 | 5.453 | 0.0002
ERAS-2025-006 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 4.5907 | 4.5909 | 0.0002
ERAS-2025-006 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 10.5273 | 10.528 | 0.0007
ERAS-2025-006 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 5.4494 | 5.4496 | 0.0002
ERAS-2025-006 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 11.2195 | 11.2202 | 0.0007
ERAS-2025-006 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 24.7376 | 24.7414 | 0.0038
ERAS-2025-006 | 03 CENTRAL | 533655 | BUFFALO2 | 69 | 13.3733 | 13.3886 | 0.0153
ERAS-2025-006 | 03 CENTRAL | 533736 | HALSTED2 | 69 | 8.1341 | 8.1464 | 0.0123
ERAS-2025-006 | 03 CENTRAL | 533742 | MOUND 2 | 69 | 6.1024 | 6.1105 | 0.0081
ERAS-2025-006 | 03 CENTRAL | 533747 | YOST 2 | 69 | 5.4701 | 5.476 | 0.0059
ERAS-2025-006 | 03 CENTRAL | 533785 | CHENEY 2 | 69 | 4.1237 | 4.1249 | 0.0012
ERAS-2025-006 | 03 CENTRAL | 533794 | GALE 2 | 69 | 2.2899 | 2.2903 | 0.0004
ERAS-2025-006 | 03 CENTRAL | 533845 | GALE TP2 | 69 | 6.5997 | 6.6031 | 0.0034
ERAS-2025-006 | 03 CENTRAL | 533872 | SG4ANDL2 | 69 | 6.5948 | 6.5981 | 0.0033
ERAS-2025-006 | 03 CENTRAL | 533875 | SG11KOC2 | 69 | 2.6463 | 2.6468 | 0.0005
ERAS-2025-006 | 03 CENTRAL | 534109 | GEN-2016-073 | 345 | 5.6887 | 5.7038 | 0.0151
ERAS-2025-006 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.9362 | 5.939 | 0.0028
ERAS-2025-006 | 03 CENTRAL | 539008 | MILAN_GOAB4 | 138 | 12.6415 | 12.6546 | 0.0131
ERAS-2025-006 | 03 CENTRAL | 539009 | CONWAY 4 | 138 | 12.1274 | 12.1391 | 0.0117
ERAS-2025-006 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 11.0374 | 11.0442 | 0.0068
ERAS-2025-006 | 03 CENTRAL | 539634 | MRWYP26 | 230 | 7.3049 | 7.3172 | 0.0123
ERAS-2025-006 | 03 CENTRAL | 539637 | MRWYP16 | 230 | 9.0733 | 9.0925 | 0.0192
ERAS-2025-006 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.576 | 16.592 | 0.016
ERAS-2025-006 | 03 CENTRAL | 539639 | ELMCREK6 | 230 | 10.265 | 10.2898 | 0.0248
ERAS-2025-006 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 12.5601 | 12.573 | 0.0129
ERAS-2025-006 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.6212 | 8.6322 | 0.011
ERAS-2025-006 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.2082 | 13.219 | 0.0108
ERAS-2025-006 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 17.565 | 17.6117 | 0.0467
ERAS-2025-006 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.6531 | 18.6734 | 0.0203
ERAS-2025-006 | 03 CENTRAL | 539805 | ELMCREEK7 | 345 | 9.2564 | 9.2951 | 0.0387
ERAS-2025-006 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0681 | 11.0756 | 0.0075
ERAS-2025-006 | 03 CENTRAL | 539816 | SADDLE7 | 345 | 11.7205 | 11.728 | 0.0075
ERAS-2025-006 | 03 CENTRAL | 539823 | IRONSTAR7 | 345 | 10.2125 | 10.2181 | 0.0056
ERAS-2025-006 | 03 CENTRAL | 539824 | IRS7 115 KV | 115 | 15.0005 | 15.004 | 0.0035
ERAS-2025-006 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.9499 | 10.957 | 0.0071
ERAS-2025-006 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.1927 | 9.1976 | 0.0049
ERAS-2025-006 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.1946 | 9.1995 | 0.0049
ERAS-2025-006 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.5655 | 8.5697 | 0.0042
ERAS-2025-006 | 03 CENTRAL | 539863 | CIRRUS7 | 345 | 9.1386 | 9.1843 | 0.0457
ERAS-2025-006 | 03 CENTRAL | 539871 | PIXLEY-SOLAR | 345 | 16.7747 | 16.8172 | 0.0425
ERAS-2025-006 | 03 CENTRAL | 539881 | SPRVLSTR | 138 | 7.3552 | 7.3592 | 0.004
ERAS-2025-006 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.7271 | 28.7334 | 0.0063
ERAS-2025-006 | 03 CENTRAL | 562020 | PRSCRKII 7 | 345 | 9.7887 | 9.7905 | 0.0018
ERAS-2025-006 | 03 CENTRAL | 562900 | G15052_1 | 345 | 12.7827 | 12.7973 | 0.0146
ERAS-2025-006 | 03 CENTRAL | 585241 | GEN-2015-088 | 345 | 13.0595 | 13.0674 | 0.0079
ERAS-2025-006 | 03 CENTRAL | 585420 | SUBST HS | 345 | 6.7761 | 6.7769 | 0.0008
ERAS-2025-006 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 7.9602 | 7.9945 | 0.0343
ERAS-2025-006 | 03 CENTRAL | 640525 | TOBIAS 3 | 345 | 13.0595 | 13.0674 | 0.0079
ERAS-2025-006 | 03 CENTRAL | 643370 | GEN-17-181B1 | 345 | 6.5098 | 6.5117 | 0.0019
ERAS-2025-006 | 03 CENTRAL | 643371 | GEN-2017-181 | 345 | 6.5098 | 6.5117 | 0.0019
ERAS-2025-006 | 03 CENTRAL | 643377 | GEN-2017-182 | 345 | 6.5098 | 6.5117 | 0.0019
ERAS-2025-006 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 22.6084 | 22.8496 | 0.2412
ERAS-2025-006 | 03 CENTRAL | 760578 | GEN-2017-119 | 345 | 6.8262 | 6.8467 | 0.0205
ERAS-2025-006 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 39.9384 | 40.1816 | 0.2432
ERAS-2025-006 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 8.5887 | 8.592 | 0.0033
ERAS-2025-006 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.649 | 28.6553 | 0.0063
ERAS-2025-006 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 28.5661 | 28.5724 | 0.0063
ERAS-2025-006 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.3155 | 7.3233 | 0.0078
ERAS-2025-006 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 19.6503 | 19.706 | 0.0557
ERAS-2025-006 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.678 | 11.6936 | 0.0156
ERAS-2025-006 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.9317 | 12.951 | 0.0193
ERAS-2025-006 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 17.1669 | 17.1724 | 0.0055
ERAS-2025-006 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6555 | 9.6602 | 0.0047
ERAS-2025-006 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.72 | 11.7271 | 0.0071
ERAS-2025-006 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 14.9168 | 14.921 | 0.0042
ERAS-2025-006 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.7261 | 6.7366 | 0.0105
ERAS-2025-006 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.8124 | 6.8232 | 0.0108
ERAS-2025-006 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.9299 | 12.9402 | 0.0103
ERAS-2025-006 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 23.266 | 23.2694 | 0.0034
ERAS-2025-006 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.8255 | 25.8297 | 0.0042
ERAS-2025-006 | 03 CENTRAL | 788725 | ERAS-06 | 345 | 13.0023 | 14.2383 | 1.236
ERAS-2025-006 | 03 CENTRAL | 788730 | ERAS-08 | 345 | 15.6754 | 15.7251 | 0.0497
ERAS-2025-006 | 03 CENTRAL | 852252 | TEST-FR4 | 345 | 8.6878 | 8.7006 | 0.0128
ERAS-2025-006 | 03 CENTRAL | 852253 | TEST-FR5-0 | 345 | 8.6878 | 8.7006 | 0.0128
ERAS-2025-007 | 03 CENTRAL | 44888 | J1490_POI | 345 | 17.6365 | 17.638 | 0.0015
ERAS-2025-007 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 13.0074 | 13.0121 | 0.0047
ERAS-2025-007 | 03 CENTRAL | 300043 | 7KINGDM | 345 | 14.9726 | 14.974 | 0.0014
ERAS-2025-007 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 17.4103 | 17.4122 | 0.0019
ERAS-2025-007 | 03 CENTRAL | 300049 | 7THOMHL | 345 | 14.2978 | 14.2984 | 0.0006
ERAS-2025-007 | 03 CENTRAL | 300500 | 5HUNTSDLB1 | 161 | 11.1552 | 11.1561 | 0.0009
ERAS-2025-007 | 03 CENTRAL | 301503 | 7THOMHLGSU3 | 345 | 14.2052 | 14.2057 | 0.0005
ERAS-2025-007 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 11.0265 | 11.0269 | 0.0004
ERAS-2025-007 | 03 CENTRAL | 345072 | 5MCBAINE | 161 | 14.8077 | 14.8086 | 0.0009
ERAS-2025-007 | 03 CENTRAL | 345219 | 5MOBERLY 2 | 161 | 15.561 | 15.5616 | 0.0006
ERAS-2025-007 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.4423 | 12.4463 | 0.004
ERAS-2025-007 | 03 CENTRAL | 345409 | 5OVERTON 1 | 161 | 23.5154 | 23.52 | 0.0046
ERAS-2025-007 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 23.5154 | 23.52 | 0.0046
ERAS-2025-007 | 03 CENTRAL | 346086 | 2OVERTON 2 | 69 | 2.8017 | 2.8018 | 0.0001
ERAS-2025-007 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 8.7566 | 9.6131 | 0.8565
ERAS-2025-007 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 21.447 | 21.4652 | 0.0182
ERAS-2025-007 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 20.8816 | 20.8934 | 0.0118
ERAS-2025-007 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.2778 | 19.3047 | 0.0269
ERAS-2025-007 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.2497 | 21.3653 | 0.1156
ERAS-2025-007 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.2608 | 27.2935 | 0.0327
ERAS-2025-007 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 14.2008 | 14.2061 | 0.0053
ERAS-2025-007 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 35.5481 | 35.5634 | 0.0153
ERAS-2025-007 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.8082 | 19.8179 | 0.0097
ERAS-2025-007 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 16.6059 | 16.6084 | 0.0025
ERAS-2025-007 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.9108 | 7.9112 | 0.0004
ERAS-2025-007 | 03 CENTRAL | 541243 | LKWINBG5 | 161 | 26.5111 | 26.5197 | 0.0086
ERAS-2025-007 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 14.1035 | 14.1106 | 0.0071
ERAS-2025-007 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.8243 | 28.8562 | 0.0319
ERAS-2025-007 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 6.6924 | 6.693 | 0.0006
ERAS-2025-007 | 03 CENTRAL | 541280 | PHILL 2 | 69 | 13.6951 | 13.6956 | 0.0005
ERAS-2025-007 | 03 CENTRAL | 541313 | HARRIS | 161 | 26.9022 | 26.911 | 0.0088
ERAS-2025-007 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 25.9362 | 25.9437 | 0.0075
ERAS-2025-007 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.408 | 7.4084 | 0.0004
ERAS-2025-007 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 8.3415 | 9.115 | 0.7735
ERAS-2025-007 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 8.3415 | 9.115 | 0.7735
ERAS-2025-007 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 8.3415 | 9.115 | 0.7735
ERAS-2025-007 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.9624 | 19.0543 | 0.0919
ERAS-2025-007 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 8.2349 | 8.5611 | 0.3262
ERAS-2025-007 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.2207 | 8.5457 | 0.325
ERAS-2025-007 | 03 CENTRAL | 541510 | HOLT 7 | 345 | 9.6598 | 10.2218 | 0.562
ERAS-2025-007 | 03 CENTRAL | 541511 | ROCKCK7 | 345 | 7.3968 | 7.6917 | 0.2949
ERAS-2025-007 | 03 CENTRAL | 541517 | HOLT_REACT7 | 345 | 9.6068 | 10.1624 | 0.5556
ERAS-2025-007 | 03 CENTRAL | 541543 | OUTLAW_WF7 | 345 | 6.0293 | 6.216 | 0.1867
ERAS-2025-007 | 03 CENTRAL | 541553 | OUTLAW_WFTP7 | 345 | 7.3702 | 7.6628 | 0.2926
ERAS-2025-007 | 03 CENTRAL | 542954 | SHALE 7 | 345 | 21.2761 | 21.3112 | 0.0351
ERAS-2025-007 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 26.5506 | 26.566 | 0.0154
ERAS-2025-007 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.731 | 22.7786 | 0.0476
ERAS-2025-007 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 56.8351 | 56.891 | 0.0559
ERAS-2025-007 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 51.2754 | 51.3202 | 0.0448
ERAS-2025-007 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.908 | 23.9334 | 0.0254
ERAS-2025-007 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 42.3214 | 42.3515 | 0.0301
ERAS-2025-007 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 34.9851 | 35.0046 | 0.0195
ERAS-2025-007 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 32.0938 | 32.1113 | 0.0175
ERAS-2025-007 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 56.0535 | 56.1079 | 0.0544
ERAS-2025-007 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 57.3571 | 57.4143 | 0.0572
ERAS-2025-007 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.5052 | 25.5243 | 0.0191
ERAS-2025-007 | 03 CENTRAL | 635000 | CBLUFFS3 | 345 | 31.4266 | 31.448 | 0.0214
ERAS-2025-007 | 03 CENTRAL | 635017 | ATCHISON 3 | 345 | 17.684 | 17.6957 | 0.0117
ERAS-2025-007 | 03 CENTRAL | 635027 | FRMR CTY WF | 345 | 17.684 | 17.6957 | 0.0117
ERAS-2025-007 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 29.2696 | 29.31 | 0.0404
ERAS-2025-007 | 03 CENTRAL | 640140 | COOPER 5 | 161 | 18.3654 | 18.3719 | 0.0065
ERAS-2025-007 | 03 CENTRAL | 640141 | COOPER_ESST8 | 69 | 4.689 | 4.6892 | 0.0002
ERAS-2025-007 | 03 CENTRAL | 640446 | COOPER 8 | 69 | 4.7869 | 4.7871 | 0.0002
ERAS-2025-007 | 03 CENTRAL | 640600 | S3771 | 345 | 22.6815 | 22.7022 | 0.0207
ERAS-2025-007 | 03 CENTRAL | 645454 | S3454 3 | 345 | 29.4482 | 29.488 | 0.0398
ERAS-2025-007 | 03 CENTRAL | 645455 | S3455 3 | 345 | 32.4392 | 32.4855 | 0.0463
ERAS-2025-007 | 03 CENTRAL | 645456 | S3456 3 | 345 | 34.0621 | 34.1061 | 0.044
ERAS-2025-007 | 03 CENTRAL | 645458 | S3458 3 | 345 | 32.1135 | 32.314 | 0.2005
ERAS-2025-007 | 03 CENTRAL | 645459 | S3459 3 | 345 | 24.8587 | 24.8787 | 0.02
ERAS-2025-007 | 03 CENTRAL | 645558 | S3458-HOLT 3 | 345 | 32.1135 | 32.314 | 0.2005
ERAS-2025-007 | 03 CENTRAL | 645740 | S3740 3 | 345 | 26.193 | 26.2504 | 0.0574
ERAS-2025-007 | 03 CENTRAL | 646206 | S1206 5 | 161 | 43.4538 | 43.4765 | 0.0227
ERAS-2025-007 | 03 CENTRAL | 650189 | 103&ROKEBY3 | 345 | 20.9854 | 21.0061 | 0.0207
ERAS-2025-007 | 03 CENTRAL | 762691 | GEN-2018-033 | 345 | 24.8856 | 24.9374 | 0.0518
ERAS-2025-007 | 03 CENTRAL | 764795 | GEN-2020-094 | 345 | 11.5936 | 11.6078 | 0.0142
ERAS-2025-007 | 03 CENTRAL | 764805 | G20-094-TAP | 345 | 16.5215 | 16.5503 | 0.0288
ERAS-2025-007 | 03 CENTRAL | 788727 | ERAS-07 | 345 | 8.7422 | 9.5988 | 0.8566
ERAS-2025-007 | 03 CENTRAL | 788990 | ERAS-13 | 345 | 8.745 | 9.5988 | 0.8538
ERAS-2025-008 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.0211 | 16.0244 | 0.0033
ERAS-2025-008 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.3869 | 24.3879 | 0.001
ERAS-2025-008 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.0327 | 13.0342 | 0.0015
ERAS-2025-008 | 03 CENTRAL | 514714 | WOODRNG4 | 138 | 20.2452 | 20.2659 | 0.0207
ERAS-2025-008 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 18.694 | 18.7941 | 0.1001
ERAS-2025-008 | 03 CENTRAL | 514804 | MIDLTNT4 | 138 | 8.5124 | 8.5227 | 0.0103
ERAS-2025-008 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.6153 | 12.6316 | 0.0163
ERAS-2025-008 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 19.4324 | 19.4484 | 0.016
ERAS-2025-008 | 03 CENTRAL | 515426 | RDRUNNR4 | 138 | 8.7008 | 8.7198 | 0.019
ERAS-2025-008 | 03 CENTRAL | 515427 | RCKFALL4 | 138 | 6.3324 | 6.3416 | 0.0092
ERAS-2025-008 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 13.3374 | 13.4939 | 0.1565
ERAS-2025-008 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 13.3153 | 13.4712 | 0.1559
ERAS-2025-008 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.7987 | 13.1108 | 0.3121
ERAS-2025-008 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.8787 | 14.9848 | 0.1061
ERAS-2025-008 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.7219 | 6.7412 | 0.0193
ERAS-2025-008 | 03 CENTRAL | 515547 | GRANTCO2 | 69 | 7.7793 | 7.7892 | 0.0099
ERAS-2025-008 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.9033 | 11.9641 | 0.0608
ERAS-2025-008 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.6488 | 12.6652 | 0.0164
ERAS-2025-008 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.1939 | 11.4286 | 0.2347
ERAS-2025-008 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.7678 | 8.7711 | 0.0033
ERAS-2025-008 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 14.7783 | 14.8033 | 0.025
ERAS-2025-008 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 14.9093 | 14.921 | 0.0117
ERAS-2025-008 | 03 CENTRAL | 515875 | REDNGTN7 | 345 | 17.6994 | 17.7393 | 0.0399
ERAS-2025-008 | 03 CENTRAL | 515877 | REDDIRT7 | 345 | 17.6951 | 17.735 | 0.0399
ERAS-2025-008 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 10.6434 | 10.6482 | 0.0048
ERAS-2025-008 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.0502 | 12.0563 | 0.0061
ERAS-2025-008 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 4.7966 | 4.8022 | 0.0056
ERAS-2025-008 | 03 CENTRAL | 516010 | PINTAIL7 | 345 | 16.092 | 16.1324 | 0.0404
ERAS-2025-008 | 03 CENTRAL | 516019 | KINGWD 7 | 345 | 16.0331 | 16.0732 | 0.0401
ERAS-2025-008 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.9877 | 11.0405 | 0.0528
ERAS-2025-008 | 03 CENTRAL | 520434 | WAKTASW4 | 138 | 6.4957 | 6.5073 | 0.0116
ERAS-2025-008 | 03 CENTRAL | 521198 | CHILOCCO4 | 138 | 6.5474 | 6.5535 | 0.0061
ERAS-2025-008 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.6639 | 7.6891 | 0.0252
ERAS-2025-008 | 03 CENTRAL | 522398 | PONDCRK4 | 138 | 5.254 | 5.2658 | 0.0118
ERAS-2025-008 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 24.0306 | 24.0341 | 0.0035
ERAS-2025-008 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 11.0489 | 11.0515 | 0.0026
ERAS-2025-008 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 17.5348 | 17.5462 | 0.0114
ERAS-2025-008 | 03 CENTRAL | 532769 | LANG 7 | 345 | 17.4248 | 17.4361 | 0.0113
ERAS-2025-008 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 13.2038 | 13.2079 | 0.0041
ERAS-2025-008 | 03 CENTRAL | 532771 | RENO 7 | 345 | 14.33 | 14.3712 | 0.0412
ERAS-2025-008 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 13.2723 | 13.2814 | 0.0091
ERAS-2025-008 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.0135 | 17.0171 | 0.0036
ERAS-2025-008 | 03 CENTRAL | 532776 | READWF 7 | 345 | 14.5305 | 14.5382 | 0.0077
ERAS-2025-008 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7713 | 9.7844 | 0.0131
ERAS-2025-008 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.405 | 9.4172 | 0.0122
ERAS-2025-008 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 22.6952 | 22.9825 | 0.2873
ERAS-2025-008 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2551 | 7.2773 | 0.0222
ERAS-2025-008 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.0266 | 6.0409 | 0.0143
ERAS-2025-008 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.0061 | 5.0156 | 0.0095
ERAS-2025-008 | 03 CENTRAL | 532786 | FR3 WF7 | 345 | 4.5893 | 4.6716 | 0.0823
ERAS-2025-008 | 03 CENTRAL | 532790 | EXPED WF7 | 345 | 7.4111 | 7.4243 | 0.0132
ERAS-2025-008 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.9185 | 20.0701 | 0.1516
ERAS-2025-008 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.9886 | 7.1965 | 0.2079
ERAS-2025-008 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 17.923 | 17.9293 | 0.0063
ERAS-2025-008 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 19.1904 | 19.2895 | 0.0991
ERAS-2025-008 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6244 | 5.7507 | 0.1263
ERAS-2025-008 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 26.0653 | 26.5127 | 0.4474
ERAS-2025-008 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.1872 | 18.2026 | 0.0154
ERAS-2025-008 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.6571 | 15.8907 | 1.2336
ERAS-2025-008 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.2363 | 16.2471 | 0.0108
ERAS-2025-008 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.399 | 10.4162 | 0.0172
ERAS-2025-008 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.1697 | 9.183 | 0.0133
ERAS-2025-008 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5948 | 13.6023 | 0.0075
ERAS-2025-008 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.6453 | 10.6736 | 0.0283
ERAS-2025-008 | 03 CENTRAL | 532814 | FR4345KV-TAP | 345 | 8.3779 | 8.7006 | 0.3227
ERAS-2025-008 | 03 CENTRAL | 532837 | G15052_T | 345 | 12.8211 | 12.8488 | 0.0277
ERAS-2025-008 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.9776 | 21.9808 | 0.0032
ERAS-2025-008 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.3622 | 14.3653 | 0.0031
ERAS-2025-008 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 10.9406 | 10.9454 | 0.0048
ERAS-2025-008 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 15.2756 | 15.2818 | 0.0062
ERAS-2025-008 | 03 CENTRAL | 532981 | CRESWLN4 | 138 | 8.8827 | 8.8967 | 0.014
ERAS-2025-008 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 9.9124 | 9.9421 | 0.0297
ERAS-2025-008 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 10.9324 | 10.9709 | 0.0385
ERAS-2025-008 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 5.863 | 5.873 | 0.01
ERAS-2025-008 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 30.2467 | 30.3967 | 0.15
ERAS-2025-008 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 12.0621 | 12.0812 | 0.0191
ERAS-2025-008 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 20.0735 | 20.1409 | 0.0674
ERAS-2025-008 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 12.196 | 12.2163 | 0.0203
ERAS-2025-008 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 23.2963 | 23.3881 | 0.0918
ERAS-2025-008 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.2908 | 6.3023 | 0.0115
ERAS-2025-008 | 03 CENTRAL | 532994 | WICHTA11_4 | 138 | 38.8498 | 39.1511 | 0.3013
ERAS-2025-008 | 03 CENTRAL | 532997 | WICHTA12_4 | 138 | 39.3865 | 39.6957 | 0.3092
ERAS-2025-008 | 03 CENTRAL | 532998 | G16-111-TAP | 345 | 12.6673 | 12.6933 | 0.026
ERAS-2025-008 | 03 CENTRAL | 532999 | GEN-2016-111 | 345 | 7.7392 | 7.7483 | 0.0091
ERAS-2025-008 | 03 CENTRAL | 533007 | MULVANE 4 | 138 | 11.4803 | 11.5135 | 0.0332
ERAS-2025-008 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 7.8075 | 7.8138 | 0.0063
ERAS-2025-008 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 12.9304 | 12.9561 | 0.0257
ERAS-2025-008 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 9.4317 | 9.4454 | 0.0137
ERAS-2025-008 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 20.7719 | 20.844 | 0.0721
ERAS-2025-008 | 03 CENTRAL | 533025 | CT-SOLAR | 138 | 35.6663 | 35.9179 | 0.2516
ERAS-2025-008 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 18.4049 | 18.5166 | 0.1117
ERAS-2025-008 | 03 CENTRAL | 533031 | GODDARD4 | 138 | 20.0899 | 20.1873 | 0.0974
ERAS-2025-008 | 03 CENTRAL | 533034 | CENTENN4 | 138 | 18.4823 | 18.5852 | 0.1029
ERAS-2025-008 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 23.3106 | 23.4144 | 0.1038
ERAS-2025-008 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 15.9127 | 16.0775 | 0.1648
ERAS-2025-008 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 19.7383 | 19.804 | 0.0657
ERAS-2025-008 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 24.4181 | 24.5698 | 0.1517
ERAS-2025-008 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 26.0782 | 26.2258 | 0.1476
ERAS-2025-008 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 40.1356 | 40.4554 | 0.3198
ERAS-2025-008 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 40.0787 | 40.3977 | 0.319
ERAS-2025-008 | 03 CENTRAL | 533042 | FARBER 4 | 138 | 16.7426 | 16.8068 | 0.0642
ERAS-2025-008 | 03 CENTRAL | 533044 | GILL E 4 | 138 | 23.9731 | 24.2319 | 0.2588
ERAS-2025-008 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 24.0557 | 24.3165 | 0.2608
ERAS-2025-008 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 24.0557 | 24.3164 | 0.2607
ERAS-2025-008 | 03 CENTRAL | 533047 | GILL 4 | 138 | 24.0516 | 24.3126 | 0.261
ERAS-2025-008 | 03 CENTRAL | 533051 | INTERST4 | 138 | 17.2399 | 17.3404 | 0.1005
ERAS-2025-008 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 21.7546 | 21.8421 | 0.0875
ERAS-2025-008 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 19.261 | 19.3551 | 0.0941
ERAS-2025-008 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 23.5331 | 23.6412 | 0.1081
ERAS-2025-008 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 21.7354 | 21.816 | 0.0806
ERAS-2025-008 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 32.2937 | 32.4501 | 0.1564
ERAS-2025-008 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 9.7688 | 9.7961 | 0.0273
ERAS-2025-008 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 22.9145 | 23.0116 | 0.0971
ERAS-2025-008 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 21.0186 | 21.1045 | 0.0859
ERAS-2025-008 | 03 CENTRAL | 533069 | BUFFALO4 | 138 | 33.8226 | 34.0831 | 0.2605
ERAS-2025-008 | 03 CENTRAL | 533070 | SLATECRK4 | 138 | 6.2013 | 6.2074 | 0.0061
ERAS-2025-008 | 03 CENTRAL | 533071 | WACO 4 | 138 | 23.2277 | 23.4769 | 0.2492
ERAS-2025-008 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 29.5027 | 29.6905 | 0.1878
ERAS-2025-008 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 26.0729 | 27.0427 | 0.9698
ERAS-2025-008 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.8467 | 15.8499 | 0.0032
ERAS-2025-008 | 03 CENTRAL | 533369 | JADE 3 | 115 | 3.2806 | 3.2811 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 7.9426 | 7.9434 | 0.0008
ERAS-2025-008 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 11.6848 | 11.6888 | 0.004
ERAS-2025-008 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 11.951 | 11.9552 | 0.0042
ERAS-2025-008 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 27.5385 | 27.5618 | 0.0233
ERAS-2025-008 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 10.2489 | 10.2534 | 0.0045
ERAS-2025-008 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 11.8689 | 11.8762 | 0.0073
ERAS-2025-008 | 03 CENTRAL | 533416 | RENO 3 | 115 | 30.3348 | 30.3753 | 0.0405
ERAS-2025-008 | 03 CENTRAL | 533419 | HEC 3 | 115 | 25.1127 | 25.1323 | 0.0196
ERAS-2025-008 | 03 CENTRAL | 533420 | WHARV3 | 115 | 8.948 | 8.954 | 0.006
ERAS-2025-008 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 26.7831 | 26.8049 | 0.0218
ERAS-2025-008 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 15.0989 | 15.102 | 0.0031
ERAS-2025-008 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 9.2104 | 9.2161 | 0.0057
ERAS-2025-008 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 7.0908 | 7.0942 | 0.0034
ERAS-2025-008 | 03 CENTRAL | 533437 | MOHAWK3 | 115 | 11.5342 | 11.536 | 0.0018
ERAS-2025-008 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 15.3731 | 15.3764 | 0.0033
ERAS-2025-008 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 8.2651 | 8.266 | 0.0009
ERAS-2025-008 | 03 CENTRAL | 533502 | CESSNA 2 | 69 | 4.7784 | 4.7789 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533503 | CESSNAJ2 | 69 | 4.8475 | 4.848 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533504 | CITYSVC2 | 69 | 4.2909 | 4.2914 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533505 | NCTYSVC2 | 69 | 4.3212 | 4.3217 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 8.6443 | 8.6464 | 0.0021
ERAS-2025-008 | 03 CENTRAL | 533507 | 18&PLUM2 | 69 | 4.9621 | 4.9625 | 0.0004
ERAS-2025-008 | 03 CENTRAL | 533509 | 11HALST2 | 69 | 5.6811 | 5.6817 | 0.0006
ERAS-2025-008 | 03 CENTRAL | 533511 | 14LORAN2 | 69 | 5.3192 | 5.3197 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533513 | HEC 2 | 69 | 7.5327 | 7.5337 | 0.001
ERAS-2025-008 | 03 CENTRAL | 533518 | MWIRON 2 | 69 | 7.1584 | 7.1599 | 0.0015
ERAS-2025-008 | 03 CENTRAL | 533519 | MWIRONJ2 | 69 | 6.912 | 6.9133 | 0.0013
ERAS-2025-008 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.0775 | 6.0782 | 0.0007
ERAS-2025-008 | 03 CENTRAL | 533522 | 17HUXMN2 | 69 | 5.4799 | 5.4804 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533523 | 17 PLUM2 | 69 | 5.0164 | 5.0169 | 0.0005
ERAS-2025-008 | 03 CENTRAL | 533529 | MWIRNJ22 | 69 | 7.3879 | 7.3894 | 0.0015
ERAS-2025-008 | 03 CENTRAL | 533541 | AKRON 2 | 69 | 7.2948 | 7.3009 | 0.0061
ERAS-2025-008 | 03 CENTRAL | 533543 | CRESWLN2 | 69 | 12.8016 | 12.8161 | 0.0145
ERAS-2025-008 | 03 CENTRAL | 533545 | FLORAL 2 | 69 | 2.5591 | 2.5598 | 0.0007
ERAS-2025-008 | 03 CENTRAL | 533546 | FLORALJ2 | 69 | 2.9038 | 2.9047 | 0.0009
ERAS-2025-008 | 03 CENTRAL | 533551 | SC1KING2 | 69 | 3.5049 | 3.5062 | 0.0013
ERAS-2025-008 | 03 CENTRAL | 533555 | SC7CRES2 | 69 | 12.7829 | 12.7974 | 0.0145
ERAS-2025-008 | 03 CENTRAL | 533557 | TIMBER 2 | 69 | 2.5722 | 2.5729 | 0.0007
ERAS-2025-008 | 03 CENTRAL | 533558 | TIMBJCT2 | 69 | 8.9009 | 8.9101 | 0.0092
ERAS-2025-008 | 03 CENTRAL | 533559 | UDALL 2 | 69 | 7.6146 | 7.6211 | 0.0065
ERAS-2025-008 | 03 CENTRAL | 533561 | WINFLD 2 | 69 | 7.9336 | 7.9384 | 0.0048
ERAS-2025-008 | 03 CENTRAL | 533573 | CRESWLS2 | 69 | 12.8018 | 12.8163 | 0.0145
ERAS-2025-008 | 03 CENTRAL | 533597 | MIDIAN 2 | 69 | 18.4884 | 18.512 | 0.0236
ERAS-2025-008 | 03 CENTRAL | 533624 | BURLING2 | 69 | 5.4528 | 5.453 | 0.0002
ERAS-2025-008 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 4.5907 | 4.5909 | 0.0002
ERAS-2025-008 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 10.527 | 10.528 | 0.001
ERAS-2025-008 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 5.4494 | 5.4496 | 0.0002
ERAS-2025-008 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 11.2191 | 11.2202 | 0.0011
ERAS-2025-008 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 24.7359 | 24.7414 | 0.0055
ERAS-2025-008 | 03 CENTRAL | 533655 | BUFFALO2 | 69 | 13.3674 | 13.3886 | 0.0212
ERAS-2025-008 | 03 CENTRAL | 533785 | CHENEY 2 | 69 | 4.1227 | 4.1249 | 0.0022
ERAS-2025-008 | 03 CENTRAL | 533794 | GALE 2 | 69 | 2.2896 | 2.2903 | 0.0007
ERAS-2025-008 | 03 CENTRAL | 533795 | GILL E 2 | 69 | 28.2258 | 28.3656 | 0.1398
ERAS-2025-008 | 03 CENTRAL | 533796 | GILL W 2 | 69 | 28.2226 | 28.3624 | 0.1398
ERAS-2025-008 | 03 CENTRAL | 533802 | HAYSVJS2 | 69 | 8.1628 | 8.1736 | 0.0108
ERAS-2025-008 | 03 CENTRAL | 533803 | HAYSV 2 | 69 | 9.4135 | 9.4273 | 0.0138
ERAS-2025-008 | 03 CENTRAL | 533804 | HAYSVJN2 | 69 | 15.2668 | 15.3039 | 0.0371
ERAS-2025-008 | 03 CENTRAL | 533812 | LIN 2 | 69 | 9.874 | 9.8902 | 0.0162
ERAS-2025-008 | 03 CENTRAL | 533813 | MACARTH2 | 69 | 23.8691 | 23.9521 | 0.083
ERAS-2025-008 | 03 CENTRAL | 533825 | OATVILL2 | 69 | 21.6425 | 21.7134 | 0.0709
ERAS-2025-008 | 03 CENTRAL | 533845 | GALE TP2 | 69 | 6.5974 | 6.6031 | 0.0057
ERAS-2025-008 | 03 CENTRAL | 533872 | SG4ANDL2 | 69 | 6.5924 | 6.5981 | 0.0057
ERAS-2025-008 | 03 CENTRAL | 533875 | SG11KOC2 | 69 | 2.6459 | 2.6468 | 0.0009
ERAS-2025-008 | 03 CENTRAL | 533990 | EAST SUB 2 | 69 | 6.2032 | 6.2056 | 0.0024
ERAS-2025-008 | 03 CENTRAL | 533991 | WEST SUB 2 | 69 | 6.1126 | 6.1152 | 0.0026
ERAS-2025-008 | 03 CENTRAL | 533992 | VIKING SUB 2 | 69 | 5.8441 | 5.8463 | 0.0022
ERAS-2025-008 | 03 CENTRAL | 534109 | GEN-2016-073 | 345 | 5.686 | 5.7038 | 0.0178
ERAS-2025-008 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 4.1312 | 4.1415 | 0.0103
ERAS-2025-008 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.3454 | 5.3668 | 0.0214
ERAS-2025-008 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 5.0057 | 5.0282 | 0.0225
ERAS-2025-008 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.9011 | 5.939 | 0.0379
ERAS-2025-008 | 03 CENTRAL | 539008 | MILAN_GOAB4 | 138 | 12.4494 | 12.6546 | 0.2052
ERAS-2025-008 | 03 CENTRAL | 539009 | CONWAY 4 | 138 | 11.9635 | 12.1391 | 0.1756
ERAS-2025-008 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 11.0285 | 11.0442 | 0.0157
ERAS-2025-008 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 16.555 | 16.592 | 0.037
ERAS-2025-008 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.5914 | 7.626 | 0.0346
ERAS-2025-008 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 12.3704 | 12.573 | 0.2026
ERAS-2025-008 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.2081 | 13.219 | 0.0109
ERAS-2025-008 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 17.5437 | 17.6117 | 0.068
ERAS-2025-008 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 18.6307 | 18.6734 | 0.0427
ERAS-2025-008 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.068 | 11.0756 | 0.0076
ERAS-2025-008 | 03 CENTRAL | 539816 | SADDLE7 | 345 | 11.7212 | 11.728 | 0.0068
ERAS-2025-008 | 03 CENTRAL | 539823 | IRONSTAR7 | 345 | 10.213 | 10.2181 | 0.0051
ERAS-2025-008 | 03 CENTRAL | 539824 | IRS7 115 KV | 115 | 15.0008 | 15.004 | 0.0032
ERAS-2025-008 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.9499 | 10.957 | 0.0071
ERAS-2025-008 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.1926 | 9.1976 | 0.005
ERAS-2025-008 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.1945 | 9.1995 | 0.005
ERAS-2025-008 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.5654 | 8.5697 | 0.0043
ERAS-2025-008 | 03 CENTRAL | 539863 | CIRRUS7 | 345 | 9.1824 | 9.1843 | 0.0019
ERAS-2025-008 | 03 CENTRAL | 539871 | PIXLEY-SOLAR | 345 | 16.7554 | 16.8172 | 0.0618
ERAS-2025-008 | 03 CENTRAL | 539881 | SPRVLSTR | 138 | 7.3114 | 7.3592 | 0.0478
ERAS-2025-008 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 28.7305 | 28.7334 | 0.0029
ERAS-2025-008 | 03 CENTRAL | 562020 | PRSCRKII 7 | 345 | 9.7864 | 9.7905 | 0.0041
ERAS-2025-008 | 03 CENTRAL | 562900 | G15052_1 | 345 | 12.7698 | 12.7973 | 0.0275
ERAS-2025-008 | 03 CENTRAL | 585420 | SUBST HS | 345 | 6.775 | 6.7769 | 0.0019
ERAS-2025-008 | 03 CENTRAL | 587480 | GEN-2016-071 | 138 | 6.8872 | 6.8939 | 0.0067
ERAS-2025-008 | 03 CENTRAL | 588190 | GEN-2016-128 | 345 | 4.5477 | 4.5527 | 0.005
ERAS-2025-008 | 03 CENTRAL | 588490 | GEN-2017-004 | 345 | 7.9931 | 7.9945 | 0.0014
ERAS-2025-008 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 22.5658 | 22.8496 | 0.2838
ERAS-2025-008 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 39.8663 | 40.1816 | 0.3153
ERAS-2025-008 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 8.5696 | 8.592 | 0.0224
ERAS-2025-008 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 28.6524 | 28.6553 | 0.0029
ERAS-2025-008 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 28.5695 | 28.5724 | 0.0029
ERAS-2025-008 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 11.0391 | 11.0739 | 0.0348
ERAS-2025-008 | 03 CENTRAL | 762342 | GEN-2017-178 | 345 | 7.8319 | 7.8495 | 0.0176
ERAS-2025-008 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.312 | 7.3233 | 0.0113
ERAS-2025-008 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 19.6337 | 19.706 | 0.0723
ERAS-2025-008 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.3213 | 11.6936 | 0.3723
ERAS-2025-008 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.4936 | 12.951 | 0.4574
ERAS-2025-008 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 17.1599 | 17.1724 | 0.0125
ERAS-2025-008 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6561 | 9.6602 | 0.0041
ERAS-2025-008 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.7209 | 11.7271 | 0.0062
ERAS-2025-008 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 14.9093 | 14.921 | 0.0117
ERAS-2025-008 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.9298 | 12.9402 | 0.0104
ERAS-2025-008 | 03 CENTRAL | 765085 | GEN-2020-003 | 69 | 6.2032 | 6.2056 | 0.0024
ERAS-2025-008 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 23.2662 | 23.2694 | 0.0032
ERAS-2025-008 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.8256 | 25.8297 | 0.0041
ERAS-2025-008 | 03 CENTRAL | 788725 | ERAS-06 | 345 | 14.198 | 14.2383 | 0.0403
ERAS-2025-008 | 03 CENTRAL | 788730 | ERAS-08 | 345 | 14.4904 | 15.7251 | 1.2347
ERAS-2025-008 | 03 CENTRAL | 852252 | TEST-FR4 | 345 | 8.3779 | 8.7006 | 0.3227
ERAS-2025-008 | 03 CENTRAL | 852253 | TEST-FR5-0 | 345 | 8.3779 | 8.7006 | 0.3227
ERAS-2025-013 | 03 CENTRAL | 44888 | J1490_POI | 345 | 17.6365 | 17.638 | 0.0015
ERAS-2025-013 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 13.0074 | 13.0121 | 0.0047
ERAS-2025-013 | 03 CENTRAL | 300043 | 7KINGDM | 345 | 14.9726 | 14.974 | 0.0014
ERAS-2025-013 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 17.4103 | 17.4122 | 0.0019
ERAS-2025-013 | 03 CENTRAL | 300049 | 7THOMHL | 345 | 14.2978 | 14.2984 | 0.0006
ERAS-2025-013 | 03 CENTRAL | 300500 | 5HUNTSDLB1 | 161 | 11.1552 | 11.1561 | 0.0009
ERAS-2025-013 | 03 CENTRAL | 301503 | 7THOMHLGSU3 | 345 | 14.2052 | 14.2057 | 0.0005
ERAS-2025-013 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 11.0265 | 11.0269 | 0.0004
ERAS-2025-013 | 03 CENTRAL | 345072 | 5MCBAINE | 161 | 14.8077 | 14.8086 | 0.0009
ERAS-2025-013 | 03 CENTRAL | 345219 | 5MOBERLY 2 | 161 | 15.561 | 15.5616 | 0.0006
ERAS-2025-013 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.4423 | 12.4463 | 0.004
ERAS-2025-013 | 03 CENTRAL | 345409 | 5OVERTON 1 | 161 | 23.5154 | 23.52 | 0.0046
ERAS-2025-013 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 23.5154 | 23.52 | 0.0046
ERAS-2025-013 | 03 CENTRAL | 346086 | 2OVERTON 2 | 69 | 2.8017 | 2.8018 | 0.0001
ERAS-2025-013 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 8.7566 | 9.6131 | 0.8565
ERAS-2025-013 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 21.447 | 21.4652 | 0.0182
ERAS-2025-013 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 20.8816 | 20.8934 | 0.0118
ERAS-2025-013 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 19.2778 | 19.3047 | 0.0269
ERAS-2025-013 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.2497 | 21.3653 | 0.1156
ERAS-2025-013 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 27.2608 | 27.2935 | 0.0327
ERAS-2025-013 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 14.2008 | 14.2061 | 0.0053
ERAS-2025-013 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 35.5481 | 35.5634 | 0.0153
ERAS-2025-013 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.8082 | 19.8179 | 0.0097
ERAS-2025-013 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 16.6059 | 16.6084 | 0.0025
ERAS-2025-013 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.9108 | 7.9112 | 0.0004
ERAS-2025-013 | 03 CENTRAL | 541243 | LKWINBG5 | 161 | 26.5111 | 26.5197 | 0.0086
ERAS-2025-013 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 14.1035 | 14.1106 | 0.0071
ERAS-2025-013 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.8243 | 28.8562 | 0.0319
ERAS-2025-013 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 6.6924 | 6.693 | 0.0006
ERAS-2025-013 | 03 CENTRAL | 541280 | PHILL 2 | 69 | 13.6951 | 13.6956 | 0.0005
ERAS-2025-013 | 03 CENTRAL | 541313 | HARRIS | 161 | 26.9022 | 26.911 | 0.0088
ERAS-2025-013 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 25.9362 | 25.9437 | 0.0075
ERAS-2025-013 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.408 | 7.4084 | 0.0004
ERAS-2025-013 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 8.3415 | 9.115 | 0.7735
ERAS-2025-013 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 8.3415 | 9.115 | 0.7735
ERAS-2025-013 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 8.3415 | 9.115 | 0.7735
ERAS-2025-013 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.9624 | 19.0543 | 0.0919
ERAS-2025-013 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 8.2349 | 8.5611 | 0.3262
ERAS-2025-013 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 8.2207 | 8.5457 | 0.325
ERAS-2025-013 | 03 CENTRAL | 541510 | HOLT 7 | 345 | 9.6598 | 10.2218 | 0.562
ERAS-2025-013 | 03 CENTRAL | 541511 | ROCKCK7 | 345 | 7.3968 | 7.6917 | 0.2949
ERAS-2025-013 | 03 CENTRAL | 541517 | HOLT_REACT7 | 345 | 9.6068 | 10.1624 | 0.5556
ERAS-2025-013 | 03 CENTRAL | 541543 | OUTLAW_WF7 | 345 | 6.0293 | 6.216 | 0.1867
ERAS-2025-013 | 03 CENTRAL | 541553 | OUTLAW_WFTP7 | 345 | 7.3702 | 7.6628 | 0.2926
ERAS-2025-013 | 03 CENTRAL | 542954 | SHALE 7 | 345 | 21.2761 | 21.3112 | 0.0351
ERAS-2025-013 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 26.5506 | 26.566 | 0.0154
ERAS-2025-013 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.731 | 22.7786 | 0.0476
ERAS-2025-013 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 56.8351 | 56.891 | 0.0559
ERAS-2025-013 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 51.2754 | 51.3202 | 0.0448
ERAS-2025-013 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.908 | 23.9334 | 0.0254
ERAS-2025-013 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 42.3214 | 42.3515 | 0.0301
ERAS-2025-013 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 34.9851 | 35.0046 | 0.0195
ERAS-2025-013 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 32.0938 | 32.1113 | 0.0175
ERAS-2025-013 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 56.0535 | 56.1079 | 0.0544
ERAS-2025-013 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 57.3571 | 57.4143 | 0.0572
ERAS-2025-013 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.5052 | 25.5243 | 0.0191
ERAS-2025-013 | 03 CENTRAL | 635000 | CBLUFFS3 | 345 | 31.4266 | 31.448 | 0.0214
ERAS-2025-013 | 03 CENTRAL | 635017 | ATCHISON 3 | 345 | 17.684 | 17.6957 | 0.0117
ERAS-2025-013 | 03 CENTRAL | 635027 | FRMR CTY WF | 345 | 17.684 | 17.6957 | 0.0117
ERAS-2025-013 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 29.2696 | 29.31 | 0.0404
ERAS-2025-013 | 03 CENTRAL | 640140 | COOPER 5 | 161 | 18.3654 | 18.3719 | 0.0065
ERAS-2025-013 | 03 CENTRAL | 640141 | COOPER_ESST8 | 69 | 4.689 | 4.6892 | 0.0002
ERAS-2025-013 | 03 CENTRAL | 640446 | COOPER 8 | 69 | 4.7869 | 4.7871 | 0.0002
ERAS-2025-013 | 03 CENTRAL | 640600 | S3771 | 345 | 22.6815 | 22.7022 | 0.0207
ERAS-2025-013 | 03 CENTRAL | 645454 | S3454 3 | 345 | 29.4482 | 29.488 | 0.0398
ERAS-2025-013 | 03 CENTRAL | 645455 | S3455 3 | 345 | 32.4392 | 32.4855 | 0.0463
ERAS-2025-013 | 03 CENTRAL | 645456 | S3456 3 | 345 | 34.0621 | 34.1061 | 0.044
ERAS-2025-013 | 03 CENTRAL | 645458 | S3458 3 | 345 | 32.1135 | 32.314 | 0.2005
ERAS-2025-013 | 03 CENTRAL | 645459 | S3459 3 | 345 | 24.8587 | 24.8787 | 0.02
ERAS-2025-013 | 03 CENTRAL | 645558 | S3458-HOLT 3 | 345 | 32.1135 | 32.314 | 0.2005
ERAS-2025-013 | 03 CENTRAL | 645740 | S3740 3 | 345 | 26.193 | 26.2504 | 0.0574
ERAS-2025-013 | 03 CENTRAL | 646206 | S1206 5 | 161 | 43.4538 | 43.4765 | 0.0227
ERAS-2025-013 | 03 CENTRAL | 650189 | 103&ROKEBY3 | 345 | 20.9854 | 21.0061 | 0.0207
ERAS-2025-013 | 03 CENTRAL | 762691 | GEN-2018-033 | 345 | 24.8856 | 24.9374 | 0.0518
ERAS-2025-013 | 03 CENTRAL | 764795 | GEN-2020-094 | 345 | 11.5936 | 11.6078 | 0.0142
ERAS-2025-013 | 03 CENTRAL | 764805 | G20-094-TAP | 345 | 16.5215 | 16.5503 | 0.0288
ERAS-2025-013 | 03 CENTRAL | 788727 | ERAS-07 | 345 | 8.745 | 9.5988 | 0.8538
ERAS-2025-013 | 03 CENTRAL | 788990 | ERAS-13 | 345 | 8.7422 | 9.5988 | 0.8566
ERAS-2025-015 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 12.3763 | 12.3886 | 0.0123
ERAS-2025-015 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 10.6377 | 10.6466 | 0.0089
ERAS-2025-015 | 03 CENTRAL | 515634 | PALDR1W7 | 345 | 9.2689 | 9.2756 | 0.0067
ERAS-2025-015 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 12.148 | 12.1573 | 0.0093
ERAS-2025-015 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 11.0294 | 11.037 | 0.0076
ERAS-2025-015 | 03 CENTRAL | 516074 | PONDRSA7 | 345 | 9.6604 | 9.6662 | 0.0058
ERAS-2025-015 | 03 CENTRAL | 523019 | OSLO-SYLVIE7 | 345 | 9.2195 | 9.2288 | 0.0093
ERAS-2025-015 | 03 CENTRAL | 523020 | SYLVIE 7 | 345 | 9.2195 | 9.2288 | 0.0093
ERAS-2025-015 | 03 CENTRAL | 523030 | OLSO 7 | 345 | 9.2195 | 9.2288 | 0.0093
ERAS-2025-015 | 03 CENTRAL | 523040 | OLYMPIA7 | 345 | 12.7523 | 12.7707 | 0.0184
ERAS-2025-015 | 03 CENTRAL | 523041 | FRWLN7 | 345 | 10.5246 | 10.5371 | 0.0125
ERAS-2025-015 | 03 CENTRAL | 523093 | HITCHLAND 3 | 115 | 16.1831 | 16.1899 | 0.0068
ERAS-2025-015 | 03 CENTRAL | 523095 | HITCHLAND 6 | 230 | 13.5349 | 13.5463 | 0.0114
ERAS-2025-015 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 12.9784 | 12.9975 | 0.0191
ERAS-2025-015 | 03 CENTRAL | 523103 | NOBLE_WND 3 | 115 | 9.8953 | 9.8988 | 0.0035
ERAS-2025-015 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 8.5122 | 8.8107 | 0.2985
ERAS-2025-015 | 03 CENTRAL | 523130 | GRPLNS-HV4-3 | 115 | 6.8684 | 6.87 | 0.0016
ERAS-2025-015 | 03 CENTRAL | 523131 | GRPLNS-HV2-3 | 115 | 9.0962 | 9.0991 | 0.0029
ERAS-2025-015 | 03 CENTRAL | 523155 | OCHILTREE 6 | 230 | 4.2393 | 4.2403 | 0.001
ERAS-2025-015 | 03 CENTRAL | 523174 | GOODWELLWND3 | 115 | 6.1308 | 6.1316 | 0.0008
ERAS-2025-015 | 03 CENTRAL | 523309 | MOORE_CNTY 6 | 230 | 8.1385 | 8.1394 | 0.0009
ERAS-2025-015 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 7.6843 | 7.74 | 0.0557
ERAS-2025-015 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 16.8194 | 18.1052 | 1.2858
ERAS-2025-015 | 03 CENTRAL | 523959 | POTTER_CO 6 | 230 | 26.5748 | 26.5769 | 0.0021
ERAS-2025-015 | 03 CENTRAL | 523961 | POTTER_CO 7 | 345 | 16.9008 | 16.9026 | 0.0018
ERAS-2025-015 | 03 CENTRAL | 523966 | POTTER_CO 9 | 765 | 7.4629 | 7.4637 | 0.0008
ERAS-2025-015 | 03 CENTRAL | 524296 | SPNSPUR_WND7 | 345 | 6.2546 | 6.2548 | 0.0002
ERAS-2025-015 | 03 CENTRAL | 524299 | SPNSPUR_COL7 | 345 | 6.2546 | 6.2548 | 0.0002
ERAS-2025-015 | 03 CENTRAL | 525549 | TOLK 7 | 345 | 13.803 | 13.8032 | 0.0002
ERAS-2025-015 | 03 CENTRAL | 530554 | ATWOOD 3 | 115 | 3.1722 | 3.1747 | 0.0025
ERAS-2025-015 | 03 CENTRAL | 530555 | COLBY 3 | 115 | 6.1243 | 6.1355 | 0.0112
ERAS-2025-015 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.9867 | 10.9961 | 0.0094
ERAS-2025-015 | 03 CENTRAL | 530559 | PH RUN 3 | 115 | 4.7172 | 4.7234 | 0.0062
ERAS-2025-015 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.7506 | 8.7561 | 0.0055
ERAS-2025-015 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.0475 | 8.0574 | 0.0099
ERAS-2025-015 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.0739 | 11.0835 | 0.0096
ERAS-2025-015 | 03 CENTRAL | 530610 | CEDARBLF_230 | 230 | 3.5012 | 3.5019 | 0.0007
ERAS-2025-015 | 03 CENTRAL | 530644 | COLBY 2 | 69 | 3.6398 | 3.6417 | 0.0019
ERAS-2025-015 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.1252 | 8.1302 | 0.005
ERAS-2025-015 | 03 CENTRAL | 530713 | GEM_SW 3 | 115 | 5.0271 | 5.0343 | 0.0072
ERAS-2025-015 | 03 CENTRAL | 530716 | COLBY_PUMP3 | 115 | 3.7399 | 3.7438 | 0.0039
ERAS-2025-015 | 03 CENTRAL | 530717 | ANGELUS | 115 | 4.2208 | 4.2254 | 0.0046
ERAS-2025-015 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.9867 | 10.9961 | 0.0094
ERAS-2025-015 | 03 CENTRAL | 531203 | PNTPR-GOAB3 | 115 | 6.5142 | 6.5226 | 0.0084
ERAS-2025-015 | 03 CENTRAL | 531204 | PLSNTPR3 | 115 | 4.8131 | 4.8177 | 0.0046
ERAS-2025-015 | 03 CENTRAL | 531210 | BLUEJAY3 | 115 | 2.2391 | 2.241 | 0.0019
ERAS-2025-015 | 03 CENTRAL | 531211 | CHRLSTN3 | 115 | 2.1678 | 2.1695 | 0.0017
ERAS-2025-015 | 03 CENTRAL | 531212 | TWNSPRG3 | 115 | 1.6829 | 1.6839 | 0.001
ERAS-2025-015 | 03 CENTRAL | 531213 | SANTAFE3 | 115 | 2.8544 | 2.8574 | 0.003
ERAS-2025-015 | 03 CENTRAL | 531219 | SHELLEY3 | 115 | 8.1136 | 8.1379 | 0.0243
ERAS-2025-015 | 03 CENTRAL | 531264 | HMLTTAP3 | 115 | 3.0174 | 3.0207 | 0.0033
ERAS-2025-015 | 03 CENTRAL | 531265 | HMLTON 3 | 115 | 2.1391 | 2.1407 | 0.0016
ERAS-2025-015 | 03 CENTRAL | 531351 | BREWSTR3 | 115 | 3.2489 | 3.2526 | 0.0037
ERAS-2025-015 | 03 CENTRAL | 531353 | GOODLND3 | 115 | 2.8027 | 2.8055 | 0.0028
ERAS-2025-015 | 03 CENTRAL | 531360 | JAGGER 3 | 115 | 3.9078 | 3.9143 | 0.0065
ERAS-2025-015 | 03 CENTRAL | 531361 | DIGHTON3 | 115 | 3.709 | 3.7149 | 0.0059
ERAS-2025-015 | 03 CENTRAL | 531362 | MANNGT 3 | 115 | 5.7033 | 5.7205 | 0.0172
ERAS-2025-015 | 03 CENTRAL | 531363 | MANNING3 | 115 | 4.4753 | 4.4859 | 0.0106
ERAS-2025-015 | 03 CENTRAL | 531374 | HASKELL3 | 115 | 5.2859 | 5.2914 | 0.0055
ERAS-2025-015 | 03 CENTRAL | 531375 | PUCKETT3 | 115 | 5.1471 | 5.1557 | 0.0086
ERAS-2025-015 | 03 CENTRAL | 531377 | HICKOCK2 | 69 | 2.9015 | 2.9025 | 0.001
ERAS-2025-015 | 03 CENTRAL | 531378 | HICKOCK3 | 115 | 5.7647 | 5.7715 | 0.0068
ERAS-2025-015 | 03 CENTRAL | 531379 | JONES3 | 115 | 11.7326 | 11.7935 | 0.0609
ERAS-2025-015 | 03 CENTRAL | 531384 | MOSCOW 2 | 69 | 2.2584 | 2.2592 | 0.0008
ERAS-2025-015 | 03 CENTRAL | 531385 | MOSCOWT2 | 69 | 2.3767 | 2.3775 | 0.0008
ERAS-2025-015 | 03 CENTRAL | 531388 | NORTH6 2 | 69 | 2.6765 | 2.6776 | 0.0011
ERAS-2025-015 | 03 CENTRAL | 531389 | NORTH6T2 | 69 | 3.1366 | 3.1382 | 0.0016
ERAS-2025-015 | 03 CENTRAL | 531390 | PIONEER2 | 69 | 4.1072 | 4.11 | 0.0028
ERAS-2025-015 | 03 CENTRAL | 531391 | PIONEER3 | 115 | 6.2373 | 6.248 | 0.0107
ERAS-2025-015 | 03 CENTRAL | 531392 | PIONTAP3 | 115 | 7.1247 | 7.1367 | 0.012
ERAS-2025-015 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 8.274 | 8.2993 | 0.0253
ERAS-2025-015 | 03 CENTRAL | 531394 | PRAXAIR2 | 69 | 2.5786 | 2.5794 | 0.0008
ERAS-2025-015 | 03 CENTRAL | 531396 | SATATAP3 | 115 | 6.5312 | 6.5393 | 0.0081
ERAS-2025-015 | 03 CENTRAL | 531397 | SATANTA3 | 115 | 4.0683 | 4.0714 | 0.0031
ERAS-2025-015 | 03 CENTRAL | 531398 | SUBLETE3 | 115 | 6.3404 | 6.3499 | 0.0095
ERAS-2025-015 | 03 CENTRAL | 531400 | PK_GOAB3 | 115 | 5.1616 | 5.1703 | 0.0087
ERAS-2025-015 | 03 CENTRAL | 531401 | ULU E 2 | 69 | 3.8492 | 3.8516 | 0.0024
ERAS-2025-015 | 03 CENTRAL | 531402 | ULU NW 2 | 69 | 3.2394 | 3.2412 | 0.0018
ERAS-2025-015 | 03 CENTRAL | 531403 | ULU PLT2 | 69 | 3.1537 | 3.1553 | 0.0016
ERAS-2025-015 | 03 CENTRAL | 531404 | WALKMYR2 | 69 | 8.9763 | 8.9896 | 0.0133
ERAS-2025-015 | 03 CENTRAL | 531405 | WALKMYR3 | 115 | 10.9157 | 10.9484 | 0.0327
ERAS-2025-015 | 03 CENTRAL | 531406 | WOODS 2 | 69 | 6.4037 | 6.4104 | 0.0067
ERAS-2025-015 | 03 CENTRAL | 531407 | INGALLS3 | 115 | 2.8528 | 2.8558 | 0.003
ERAS-2025-015 | 03 CENTRAL | 531408 | PIERCVL3 | 115 | 4.1122 | 4.1184 | 0.0062
ERAS-2025-015 | 03 CENTRAL | 531412 | GRINNEL3 | 115 | 3.8759 | 3.88 | 0.0041
ERAS-2025-015 | 03 CENTRAL | 531419 | DOBSON 3 | 115 | 12.8005 | 12.8627 | 0.0622
ERAS-2025-015 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 7.2391 | 7.2609 | 0.0218
ERAS-2025-015 | 03 CENTRAL | 531425 | LOWETAP3 | 115 | 11.0336 | 11.0836 | 0.05
ERAS-2025-015 | 03 CENTRAL | 531426 | JAMESON3 | 115 | 11.1343 | 11.1873 | 0.053
ERAS-2025-015 | 03 CENTRAL | 531428 | LEOTI 3 | 115 | 4.3549 | 4.3645 | 0.0096
ERAS-2025-015 | 03 CENTRAL | 531429 | MINGO 3 | 115 | 12.5756 | 12.6334 | 0.0578
ERAS-2025-015 | 03 CENTRAL | 531430 | MORRIS-3 | 115 | 7.4665 | 7.487 | 0.0205
ERAS-2025-015 | 03 CENTRAL | 531432 | PILE 3 | 115 | 6.9972 | 7.0223 | 0.0251
ERAS-2025-015 | 03 CENTRAL | 531433 | SCOTCTY3 | 115 | 9.8958 | 9.9548 | 0.059
ERAS-2025-015 | 03 CENTRAL | 531434 | SELKIRK3 | 115 | 3.9886 | 3.9964 | 0.0078
ERAS-2025-015 | 03 CENTRAL | 531435 | LOWESUB3 | 115 | 9.697 | 9.7355 | 0.0385
ERAS-2025-015 | 03 CENTRAL | 531437 | SYRACUS3 | 115 | 3.7943 | 3.8 | 0.0057
ERAS-2025-015 | 03 CENTRAL | 531439 | TRIBUNE3 | 115 | 3.6173 | 3.6231 | 0.0058
ERAS-2025-015 | 03 CENTRAL | 531440 | WILLIAM3 | 115 | 3.9736 | 3.9799 | 0.0063
ERAS-2025-015 | 03 CENTRAL | 531442 | SAT-TAP3 | 115 | 5.3356 | 5.3413 | 0.0057
ERAS-2025-015 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 15.0101 | 15.0861 | 0.076
ERAS-2025-015 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 24.3698 | 24.6661 | 0.2963
ERAS-2025-015 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 17.2712 | 18.6451 | 1.3739
ERAS-2025-015 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.3728 | 6.4211 | 0.0483
ERAS-2025-015 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 11.4387 | 11.5234 | 0.0847
ERAS-2025-015 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 8.5049 | 8.6981 | 0.1932
ERAS-2025-015 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 14.0976 | 14.1904 | 0.0928
ERAS-2025-015 | 03 CENTRAL | 531472 | AMOCO 3 | 115 | 5.0113 | 5.0164 | 0.0051
ERAS-2025-015 | 03 CENTRAL | 531476 | SWNDTAP3 | 115 | 7.9401 | 7.9619 | 0.0218
ERAS-2025-015 | 03 CENTRAL | 531477 | S. WIND3 | 115 | 7.2831 | 7.3014 | 0.0183
ERAS-2025-015 | 03 CENTRAL | 531478 | IRSKDOL3 | 115 | 6.607 | 6.6227 | 0.0157
ERAS-2025-015 | 03 CENTRAL | 531480 | KSAVWTP3 | 115 | 14.6738 | 14.747 | 0.0732
ERAS-2025-015 | 03 CENTRAL | 531483 | GRANTTP3 | 115 | 5.132 | 5.1392 | 0.0072
ERAS-2025-015 | 03 CENTRAL | 531484 | GRANT 3 | 115 | 4.7595 | 4.7657 | 0.0062
ERAS-2025-015 | 03 CENTRAL | 531485 | CNTRLPL3 | 115 | 6.5028 | 6.5261 | 0.0233
ERAS-2025-015 | 03 CENTRAL | 531490 | ULYSPLT3 | 115 | 4.1216 | 4.1265 | 0.0049
ERAS-2025-015 | 03 CENTRAL | 531493 | GANO 3 | 115 | 7.3016 | 7.3259 | 0.0243
ERAS-2025-015 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 10.6538 | 10.8547 | 0.2009
ERAS-2025-015 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 8.2459 | 8.3657 | 0.1198
ERAS-2025-015 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 8.2459 | 8.3657 | 0.1198
ERAS-2025-015 | 03 CENTRAL | 531510 | HARBNGR3 | 115 | 11.6485 | 11.6866 | 0.0381
ERAS-2025-015 | 03 CENTRAL | 531512 | HARBNGR7 | 345 | 7.6762 | 7.7318 | 0.0556
ERAS-2025-015 | 03 CENTRAL | 531623 | EASTFORK3 | 115 | 9.7978 | 9.8328 | 0.035
ERAS-2025-015 | 03 CENTRAL | 531632 | SLMNFRK7 | 345 | 5.5706 | 5.6066 | 0.036
ERAS-2025-015 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 9.4833 | 9.5007 | 0.0174
ERAS-2025-015 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 8.3959 | 8.4094 | 0.0135
ERAS-2025-015 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 14.1052 | 14.1141 | 0.0089
ERAS-2025-015 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 8.7097 | 8.713 | 0.0033
ERAS-2025-015 | 03 CENTRAL | 539691 | SATMKEC3 | 115 | 5.3356 | 5.3413 | 0.0057
ERAS-2025-015 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2847 | 10.2927 | 0.008
ERAS-2025-015 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 9.6676 | 9.6857 | 0.0181
ERAS-2025-015 | 03 CENTRAL | 539758 | FORD 3 | 115 | 6.1126 | 6.1139 | 0.0013
ERAS-2025-015 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 14.1649 | 14.1886 | 0.0237
ERAS-2025-015 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 14.1779 | 14.187 | 0.0091
ERAS-2025-015 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.1736 | 13.219 | 0.0454
ERAS-2025-015 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 17.5963 | 17.6117 | 0.0154
ERAS-2025-015 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.5274 | 13.6094 | 0.082
ERAS-2025-015 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0441 | 11.0756 | 0.0315
ERAS-2025-015 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.2804 | 12.3471 | 0.0667
ERAS-2025-015 | 03 CENTRAL | 539816 | SADDLE7 | 345 | 11.6842 | 11.728 | 0.0438
ERAS-2025-015 | 03 CENTRAL | 539823 | IRONSTAR7 | 345 | 10.1853 | 10.2181 | 0.0328
ERAS-2025-015 | 03 CENTRAL | 539824 | IRS7 115 KV | 115 | 14.9833 | 15.004 | 0.0207
ERAS-2025-015 | 03 CENTRAL | 539831 | WESTPLN7 | 345 | 11.2193 | 11.2743 | 0.055
ERAS-2025-015 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.9272 | 10.957 | 0.0298
ERAS-2025-015 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.1768 | 9.1976 | 0.0208
ERAS-2025-015 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.1787 | 9.1995 | 0.0208
ERAS-2025-015 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.5518 | 8.5697 | 0.0179
ERAS-2025-015 | 03 CENTRAL | 539871 | PIXLEY-SOLAR | 345 | 16.8033 | 16.8172 | 0.0139
ERAS-2025-015 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.7699 | 2.8027 | 0.0328
ERAS-2025-015 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.5915 | 9.5935 | 0.002
ERAS-2025-015 | 03 CENTRAL | 640082 | BEVERLY7 | 115 | 4.9528 | 4.954 | 0.0012
ERAS-2025-015 | 03 CENTRAL | 640083 | BEVERLY8 | 69 | 4.5407 | 4.5413 | 0.0006
ERAS-2025-015 | 03 CENTRAL | 640183 | GENTLMN3 | 345 | 15.7512 | 15.7581 | 0.0069
ERAS-2025-015 | 03 CENTRAL | 640184 | GENTLMN4 | 230 | 19.4985 | 19.5027 | 0.0042
ERAS-2025-015 | 03 CENTRAL | 640252 | KEYSTON3 | 345 | 9.3151 | 9.3168 | 0.0017
ERAS-2025-015 | 03 CENTRAL | 640269 | MCCOOK 7 | 115 | 8.7679 | 8.7724 | 0.0045
ERAS-2025-015 | 03 CENTRAL | 640270 | MCCOOK 8 | 69 | 4.5962 | 4.597 | 0.0008
ERAS-2025-015 | 03 CENTRAL | 640325 | REDWILO3 | 345 | 6.467 | 6.4809 | 0.0139
ERAS-2025-015 | 03 CENTRAL | 640326 | REDWILO7 | 115 | 11.5288 | 11.5381 | 0.0093
ERAS-2025-015 | 03 CENTRAL | 640365 | STOCKVL7 | 115 | 4.8069 | 4.8078 | 0.0009
ERAS-2025-015 | 03 CENTRAL | 640366 | STOCKVL8 | 69 | 3.6364 | 3.6367 | 0.0003
ERAS-2025-015 | 03 CENTRAL | 640500 | THEDFORD 3 | 345 | 5.4242 | 5.4246 | 0.0004
ERAS-2025-015 | 03 CENTRAL | 640527 | MACON 3 | 345 | 7.1012 | 7.1033 | 0.0021
ERAS-2025-015 | 03 CENTRAL | 640528 | LITTLEBLUEW3 | 345 | 6.0011 | 6.0026 | 0.0015
ERAS-2025-015 | 03 CENTRAL | 640700 | ETNA-NE 3 | 345 | 8.3552 | 8.3567 | 0.0015
ERAS-2025-015 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.3207 | 7.3233 | 0.0026
ERAS-2025-015 | 03 CENTRAL | 763406 | GEN-2018-125 | 345 | 6.6434 | 6.6444 | 0.001
ERAS-2025-015 | 03 CENTRAL | 763410 | G18-125-TAP | 345 | 6.9603 | 6.9614 | 0.0011
ERAS-2025-015 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6279 | 9.6602 | 0.0323
ERAS-2025-015 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.6785 | 11.7271 | 0.0486
ERAS-2025-015 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 8.1605 | 8.1634 | 0.0029
ERAS-2025-015 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.2982 | 6.3036 | 0.0054
ERAS-2025-015 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.3739 | 6.3794 | 0.0055
ERAS-2025-015 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.8968 | 12.9402 | 0.0434
ERAS-2025-015 | 03 CENTRAL | 764980 | GEN-2020-008 | 345 | 7.6843 | 7.74 | 0.0557
ERAS-2025-015 | 03 CENTRAL | 768280 | G22-065-TAP | 230 | 6.2962 | 6.3014 | 0.0052
ERAS-2025-015 | 03 CENTRAL | 770039 | GEN-2023-SR2 | 115 | 10.976 | 10.9814 | 0.0054
ERAS-2025-015 | 03 CENTRAL | 788746 | ERA-015 | 345 | 13.4813 | 14.8856 | 1.4043
ERAS-2025-015 | 03 CENTRAL | 788901 | MPT | 115 | 11.4329 | 11.4385 | 0.0056
ERAS-2025-015 | 03 CENTRAL | 788934 | ERA-017-GSU1 | 345 | 16.9965 | 18.0309 | 1.0344
ERAS-2025-015 | 03 CENTRAL | 788935 | ERA-017-GSU2 | 345 | 16.9965 | 18.0309 | 1.0344
ERAS-2025-015 | 03 CENTRAL | 788936 | ERA-2025-017 | 345 | 16.9965 | 18.0309 | 1.0344
ERAS-2025-015 | 03 CENTRAL | 999980 | DUMMY | 115 | 11.4329 | 11.4385 | 0.0056
ERAS-2025-015 | 03 CENTRAL | 999989 | ZSWSH_999989 | 115 | 6.2373 | 6.248 | 0.0107
ERAS-2025-015 | 03 CENTRAL | 999991 | ZSWSH_999991 | 115 | 5.7647 | 5.7715 | 0.0068
ERAS-2025-015 | 03 CENTRAL | 999992 | ZSWSH_999992 | 115 | 2.8544 | 2.8574 | 0.003
ERAS-2025-017 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 12.2844 | 12.3886 | 0.1042
ERAS-2025-017 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 10.5708 | 10.6466 | 0.0758
ERAS-2025-017 | 03 CENTRAL | 515634 | PALDR1W7 | 345 | 9.2187 | 9.2756 | 0.0569
ERAS-2025-017 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 12.0782 | 12.1573 | 0.0791
ERAS-2025-017 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 10.9718 | 11.037 | 0.0652
ERAS-2025-017 | 03 CENTRAL | 516074 | PONDRSA7 | 345 | 9.6171 | 9.6662 | 0.0491
ERAS-2025-017 | 03 CENTRAL | 523019 | OSLO-SYLVIE7 | 345 | 9.1501 | 9.2288 | 0.0787
ERAS-2025-017 | 03 CENTRAL | 523020 | SYLVIE 7 | 345 | 9.1501 | 9.2288 | 0.0787
ERAS-2025-017 | 03 CENTRAL | 523030 | OLSO 7 | 345 | 9.1501 | 9.2288 | 0.0787
ERAS-2025-017 | 03 CENTRAL | 523040 | OLYMPIA7 | 345 | 12.6151 | 12.7707 | 0.1556
ERAS-2025-017 | 03 CENTRAL | 523041 | FRWLN7 | 345 | 10.431 | 10.5371 | 0.1061
ERAS-2025-017 | 03 CENTRAL | 523093 | HITCHLAND 3 | 115 | 16.1324 | 16.1899 | 0.0575
ERAS-2025-017 | 03 CENTRAL | 523095 | HITCHLAND 6 | 230 | 13.4499 | 13.5463 | 0.0964
ERAS-2025-017 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 12.8362 | 12.9975 | 0.1613
ERAS-2025-017 | 03 CENTRAL | 523103 | NOBLE_WND 3 | 115 | 9.8692 | 9.8988 | 0.0296
ERAS-2025-017 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.7761 | 8.8107 | 2.0346
ERAS-2025-017 | 03 CENTRAL | 523130 | GRPLNS-HV4-3 | 115 | 6.8565 | 6.87 | 0.0135
ERAS-2025-017 | 03 CENTRAL | 523131 | GRPLNS-HV2-3 | 115 | 9.0744 | 9.0991 | 0.0247
ERAS-2025-017 | 03 CENTRAL | 523155 | OCHILTREE 6 | 230 | 4.2319 | 4.2403 | 0.0084
ERAS-2025-017 | 03 CENTRAL | 523174 | GOODWELLWND3 | 115 | 6.1253 | 6.1316 | 0.0063
ERAS-2025-017 | 03 CENTRAL | 523309 | MOORE_CNTY 6 | 230 | 8.1318 | 8.1394 | 0.0076
ERAS-2025-017 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 7.2882 | 7.74 | 0.4518
ERAS-2025-017 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 10.94 | 18.1052 | 7.1652
ERAS-2025-017 | 03 CENTRAL | 523959 | POTTER_CO 6 | 230 | 26.5592 | 26.5769 | 0.0177
ERAS-2025-017 | 03 CENTRAL | 523961 | POTTER_CO 7 | 345 | 16.8871 | 16.9026 | 0.0155
ERAS-2025-017 | 03 CENTRAL | 523966 | POTTER_CO 9 | 765 | 7.4572 | 7.4637 | 0.0065
ERAS-2025-017 | 03 CENTRAL | 524296 | SPNSPUR_WND7 | 345 | 6.253 | 6.2548 | 0.0018
ERAS-2025-017 | 03 CENTRAL | 524299 | SPNSPUR_COL7 | 345 | 6.253 | 6.2548 | 0.0018
ERAS-2025-017 | 03 CENTRAL | 525549 | TOLK 7 | 345 | 13.8014 | 13.8032 | 0.0018
ERAS-2025-017 | 03 CENTRAL | 530554 | ATWOOD 3 | 115 | 3.1534 | 3.1747 | 0.0213
ERAS-2025-017 | 03 CENTRAL | 530555 | COLBY 3 | 115 | 6.0414 | 6.1355 | 0.0941
ERAS-2025-017 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.9156 | 10.9961 | 0.0805
ERAS-2025-017 | 03 CENTRAL | 530559 | PH RUN 3 | 115 | 4.6703 | 4.7234 | 0.0531
ERAS-2025-017 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.7088 | 8.7561 | 0.0473
ERAS-2025-017 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.9735 | 8.0574 | 0.0839
ERAS-2025-017 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.0014 | 11.0835 | 0.0821
ERAS-2025-017 | 03 CENTRAL | 530610 | CEDARBLF_230 | 230 | 3.4958 | 3.5019 | 0.0061
ERAS-2025-017 | 03 CENTRAL | 530644 | COLBY 2 | 69 | 3.6253 | 3.6417 | 0.0164
ERAS-2025-017 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.0878 | 8.1302 | 0.0424
ERAS-2025-017 | 03 CENTRAL | 530713 | GEM_SW 3 | 115 | 4.9738 | 5.0343 | 0.0605
ERAS-2025-017 | 03 CENTRAL | 530716 | COLBY_PUMP3 | 115 | 3.7102 | 3.7438 | 0.0336
ERAS-2025-017 | 03 CENTRAL | 530717 | ANGELUS | 115 | 4.1858 | 4.2254 | 0.0396
ERAS-2025-017 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.9156 | 10.9961 | 0.0805
ERAS-2025-017 | 03 CENTRAL | 531203 | PNTPR-GOAB3 | 115 | 6.4514 | 6.5226 | 0.0712
ERAS-2025-017 | 03 CENTRAL | 531204 | PLSNTPR3 | 115 | 4.7788 | 4.8177 | 0.0389
ERAS-2025-017 | 03 CENTRAL | 531210 | BLUEJAY3 | 115 | 2.2254 | 2.241 | 0.0156
ERAS-2025-017 | 03 CENTRAL | 531211 | CHRLSTN3 | 115 | 2.1549 | 2.1695 | 0.0146
ERAS-2025-017 | 03 CENTRAL | 531212 | TWNSPRG3 | 115 | 1.6751 | 1.6839 | 0.0088
ERAS-2025-017 | 03 CENTRAL | 531213 | SANTAFE3 | 115 | 2.8321 | 2.8574 | 0.0253
ERAS-2025-017 | 03 CENTRAL | 531219 | SHELLEY3 | 115 | 7.9345 | 8.1379 | 0.2034
ERAS-2025-017 | 03 CENTRAL | 531264 | HMLTTAP3 | 115 | 2.993 | 3.0207 | 0.0277
ERAS-2025-017 | 03 CENTRAL | 531265 | HMLTON 3 | 115 | 2.1269 | 2.1407 | 0.0138
ERAS-2025-017 | 03 CENTRAL | 531351 | BREWSTR3 | 115 | 3.2209 | 3.2526 | 0.0317
ERAS-2025-017 | 03 CENTRAL | 531353 | GOODLND3 | 115 | 2.7822 | 2.8055 | 0.0233
ERAS-2025-017 | 03 CENTRAL | 531360 | JAGGER 3 | 115 | 3.859 | 3.9143 | 0.0553
ERAS-2025-017 | 03 CENTRAL | 531361 | DIGHTON3 | 115 | 3.6651 | 3.7149 | 0.0498
ERAS-2025-017 | 03 CENTRAL | 531362 | MANNGT 3 | 115 | 5.5763 | 5.7205 | 0.1442
ERAS-2025-017 | 03 CENTRAL | 531363 | MANNING3 | 115 | 4.3969 | 4.4859 | 0.089
ERAS-2025-017 | 03 CENTRAL | 531374 | HASKELL3 | 115 | 5.2446 | 5.2914 | 0.0468
ERAS-2025-017 | 03 CENTRAL | 531375 | PUCKETT3 | 115 | 5.0828 | 5.1557 | 0.0729
ERAS-2025-017 | 03 CENTRAL | 531377 | HICKOCK2 | 69 | 2.8936 | 2.9025 | 0.0089
ERAS-2025-017 | 03 CENTRAL | 531378 | HICKOCK3 | 115 | 5.7137 | 5.7715 | 0.0578
ERAS-2025-017 | 03 CENTRAL | 531379 | JONES3 | 115 | 11.2923 | 11.7935 | 0.5012
ERAS-2025-017 | 03 CENTRAL | 531384 | MOSCOW 2 | 69 | 2.2526 | 2.2592 | 0.0066
ERAS-2025-017 | 03 CENTRAL | 531385 | MOSCOWT2 | 69 | 2.3702 | 2.3775 | 0.0073
ERAS-2025-017 | 03 CENTRAL | 531388 | NORTH6 2 | 69 | 2.6681 | 2.6776 | 0.0095
ERAS-2025-017 | 03 CENTRAL | 531389 | NORTH6T2 | 69 | 3.1252 | 3.1382 | 0.013
ERAS-2025-017 | 03 CENTRAL | 531390 | PIONEER2 | 69 | 4.0862 | 4.11 | 0.0238
ERAS-2025-017 | 03 CENTRAL | 531391 | PIONEER3 | 115 | 6.1576 | 6.248 | 0.0904
ERAS-2025-017 | 03 CENTRAL | 531392 | PIONTAP3 | 115 | 7.0354 | 7.1367 | 0.1013
ERAS-2025-017 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 8.0881 | 8.2993 | 0.2112
ERAS-2025-017 | 03 CENTRAL | 531394 | PRAXAIR2 | 69 | 2.5724 | 2.5794 | 0.007
ERAS-2025-017 | 03 CENTRAL | 531396 | SATATAP3 | 115 | 6.4711 | 6.5393 | 0.0682
ERAS-2025-017 | 03 CENTRAL | 531397 | SATANTA3 | 115 | 4.0455 | 4.0714 | 0.0259
ERAS-2025-017 | 03 CENTRAL | 531398 | SUBLETE3 | 115 | 6.2696 | 6.3499 | 0.0803
ERAS-2025-017 | 03 CENTRAL | 531400 | PK_GOAB3 | 115 | 5.097 | 5.1703 | 0.0733
ERAS-2025-017 | 03 CENTRAL | 531401 | ULU E 2 | 69 | 3.8307 | 3.8516 | 0.0209
ERAS-2025-017 | 03 CENTRAL | 531402 | ULU NW 2 | 69 | 3.2265 | 3.2412 | 0.0147
ERAS-2025-017 | 03 CENTRAL | 531403 | ULU PLT2 | 69 | 3.1414 | 3.1553 | 0.0139
ERAS-2025-017 | 03 CENTRAL | 531404 | WALKMYR2 | 69 | 8.8773 | 8.9896 | 0.1123
ERAS-2025-017 | 03 CENTRAL | 531405 | WALKMYR3 | 115 | 10.6745 | 10.9484 | 0.2739
ERAS-2025-017 | 03 CENTRAL | 531406 | WOODS 2 | 69 | 6.3537 | 6.4104 | 0.0567
ERAS-2025-017 | 03 CENTRAL | 531407 | INGALLS3 | 115 | 2.8306 | 2.8558 | 0.0252
ERAS-2025-017 | 03 CENTRAL | 531408 | PIERCVL3 | 115 | 4.066 | 4.1184 | 0.0524
ERAS-2025-017 | 03 CENTRAL | 531412 | GRINNEL3 | 115 | 3.845 | 3.88 | 0.035
ERAS-2025-017 | 03 CENTRAL | 531419 | DOBSON 3 | 115 | 12.3493 | 12.8627 | 0.5134
ERAS-2025-017 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 7.0791 | 7.2609 | 0.1818
ERAS-2025-017 | 03 CENTRAL | 531425 | LOWETAP3 | 115 | 10.6702 | 11.0836 | 0.4134
ERAS-2025-017 | 03 CENTRAL | 531426 | JAMESON3 | 115 | 10.7498 | 11.1873 | 0.4375
ERAS-2025-017 | 03 CENTRAL | 531428 | LEOTI 3 | 115 | 4.2834 | 4.3645 | 0.0811
ERAS-2025-017 | 03 CENTRAL | 531429 | MINGO 3 | 115 | 12.1549 | 12.6334 | 0.4785
ERAS-2025-017 | 03 CENTRAL | 531430 | MORRIS-3 | 115 | 7.3157 | 7.487 | 0.1713
ERAS-2025-017 | 03 CENTRAL | 531432 | PILE 3 | 115 | 6.813 | 7.0223 | 0.2093
ERAS-2025-017 | 03 CENTRAL | 531433 | SCOTCTY3 | 115 | 9.4712 | 9.9548 | 0.4836
ERAS-2025-017 | 03 CENTRAL | 531434 | SELKIRK3 | 115 | 3.9305 | 3.9964 | 0.0659
ERAS-2025-017 | 03 CENTRAL | 531435 | LOWESUB3 | 115 | 9.4161 | 9.7355 | 0.3194
ERAS-2025-017 | 03 CENTRAL | 531437 | SYRACUS3 | 115 | 3.7524 | 3.8 | 0.0476
ERAS-2025-017 | 03 CENTRAL | 531439 | TRIBUNE3 | 115 | 3.574 | 3.6231 | 0.0491
ERAS-2025-017 | 03 CENTRAL | 531440 | WILLIAM3 | 115 | 3.9269 | 3.9799 | 0.053
ERAS-2025-017 | 03 CENTRAL | 531442 | SAT-TAP3 | 115 | 5.2929 | 5.3413 | 0.0484
ERAS-2025-017 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 14.4606 | 15.0861 | 0.6255
ERAS-2025-017 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 22.3386 | 24.6661 | 2.3275
ERAS-2025-017 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 11.0878 | 18.6451 | 7.5573
ERAS-2025-017 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.0296 | 6.4211 | 0.3915
ERAS-2025-017 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.8361 | 11.5234 | 0.6873
ERAS-2025-017 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.2815 | 8.6981 | 1.4166
ERAS-2025-017 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.4338 | 14.1904 | 0.7566
ERAS-2025-017 | 03 CENTRAL | 531472 | AMOCO 3 | 115 | 4.9728 | 5.0164 | 0.0436
ERAS-2025-017 | 03 CENTRAL | 531476 | SWNDTAP3 | 115 | 7.7796 | 7.9619 | 0.1823
ERAS-2025-017 | 03 CENTRAL | 531477 | S. WIND3 | 115 | 7.148 | 7.3014 | 0.1534
ERAS-2025-017 | 03 CENTRAL | 531478 | IRSKDOL3 | 115 | 6.4913 | 6.6227 | 0.1314
ERAS-2025-017 | 03 CENTRAL | 531480 | KSAVWTP3 | 115 | 14.1437 | 14.747 | 0.6033
ERAS-2025-017 | 03 CENTRAL | 531483 | GRANTTP3 | 115 | 5.078 | 5.1392 | 0.0612
ERAS-2025-017 | 03 CENTRAL | 531484 | GRANT 3 | 115 | 4.7132 | 4.7657 | 0.0525
ERAS-2025-017 | 03 CENTRAL | 531485 | CNTRLPL3 | 115 | 6.3322 | 6.5261 | 0.1939
ERAS-2025-017 | 03 CENTRAL | 531490 | ULYSPLT3 | 115 | 4.0846 | 4.1265 | 0.0419
ERAS-2025-017 | 03 CENTRAL | 531493 | GANO 3 | 115 | 7.1234 | 7.3259 | 0.2025
ERAS-2025-017 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.3462 | 10.8547 | 1.5085
ERAS-2025-017 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.4402 | 8.3657 | 0.9255
ERAS-2025-017 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4402 | 8.3657 | 0.9255
ERAS-2025-017 | 03 CENTRAL | 531510 | HARBNGR3 | 115 | 11.3683 | 11.6866 | 0.3183
ERAS-2025-017 | 03 CENTRAL | 531512 | HARBNGR7 | 345 | 7.281 | 7.7318 | 0.4508
ERAS-2025-017 | 03 CENTRAL | 531623 | EASTFORK3 | 115 | 9.5405 | 9.8328 | 0.2923
ERAS-2025-017 | 03 CENTRAL | 531632 | SLMNFRK7 | 345 | 5.3124 | 5.6066 | 0.2942
ERAS-2025-017 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 9.3538 | 9.5007 | 0.1469
ERAS-2025-017 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 8.2951 | 8.4094 | 0.1143
ERAS-2025-017 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 14.0387 | 14.1141 | 0.0754
ERAS-2025-017 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 8.6849 | 8.713 | 0.0281
ERAS-2025-017 | 03 CENTRAL | 539691 | SATMKEC3 | 115 | 5.2929 | 5.3413 | 0.0484
ERAS-2025-017 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.2243 | 10.2927 | 0.0684
ERAS-2025-017 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 9.5327 | 9.6857 | 0.153
ERAS-2025-017 | 03 CENTRAL | 539758 | FORD 3 | 115 | 6.1029 | 6.1139 | 0.011
ERAS-2025-017 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.9877 | 14.1886 | 0.2009
ERAS-2025-017 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 14.1097 | 14.187 | 0.0773
ERAS-2025-017 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.841 | 13.219 | 0.378
ERAS-2025-017 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 17.4811 | 17.6117 | 0.1306
ERAS-2025-017 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 12.9386 | 13.6094 | 0.6708
ERAS-2025-017 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.8118 | 11.0756 | 0.2638
ERAS-2025-017 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.7986 | 12.3471 | 0.5485
ERAS-2025-017 | 03 CENTRAL | 539816 | SADDLE7 | 345 | 11.3638 | 11.728 | 0.3642
ERAS-2025-017 | 03 CENTRAL | 539823 | IRONSTAR7 | 345 | 9.9444 | 10.2181 | 0.2737
ERAS-2025-017 | 03 CENTRAL | 539824 | IRS7 115 KV | 115 | 14.8288 | 15.004 | 0.1752
ERAS-2025-017 | 03 CENTRAL | 539831 | WESTPLN7 | 345 | 10.8204 | 11.2743 | 0.4539
ERAS-2025-017 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.7065 | 10.957 | 0.2505
ERAS-2025-017 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.0228 | 9.1976 | 0.1748
ERAS-2025-017 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.0247 | 9.1995 | 0.1748
ERAS-2025-017 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.4188 | 8.5697 | 0.1509
ERAS-2025-017 | 03 CENTRAL | 539871 | PIXLEY-SOLAR | 345 | 16.6984 | 16.8172 | 0.1188
ERAS-2025-017 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.5447 | 2.8027 | 0.258
ERAS-2025-017 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.5757 | 9.5935 | 0.0178
ERAS-2025-017 | 03 CENTRAL | 640082 | BEVERLY7 | 115 | 4.9433 | 4.954 | 0.0107
ERAS-2025-017 | 03 CENTRAL | 640083 | BEVERLY8 | 69 | 4.536 | 4.5413 | 0.0053
ERAS-2025-017 | 03 CENTRAL | 640183 | GENTLMN3 | 345 | 15.6992 | 15.7581 | 0.0589
ERAS-2025-017 | 03 CENTRAL | 640184 | GENTLMN4 | 230 | 19.4668 | 19.5027 | 0.0359
ERAS-2025-017 | 03 CENTRAL | 640252 | KEYSTON3 | 345 | 9.3024 | 9.3168 | 0.0144
ERAS-2025-017 | 03 CENTRAL | 640269 | MCCOOK 7 | 115 | 8.7337 | 8.7724 | 0.0387
ERAS-2025-017 | 03 CENTRAL | 640270 | MCCOOK 8 | 69 | 4.5906 | 4.597 | 0.0064
ERAS-2025-017 | 03 CENTRAL | 640325 | REDWILO3 | 345 | 6.3638 | 6.4809 | 0.1171
ERAS-2025-017 | 03 CENTRAL | 640326 | REDWILO7 | 115 | 11.4589 | 11.5381 | 0.0792
ERAS-2025-017 | 03 CENTRAL | 640365 | STOCKVL7 | 115 | 4.8003 | 4.8078 | 0.0075
ERAS-2025-017 | 03 CENTRAL | 640366 | STOCKVL8 | 69 | 3.6343 | 3.6367 | 0.0024
ERAS-2025-017 | 03 CENTRAL | 640500 | THEDFORD 3 | 345 | 5.4215 | 5.4246 | 0.0031
ERAS-2025-017 | 03 CENTRAL | 640527 | MACON 3 | 345 | 7.085 | 7.1033 | 0.0183
ERAS-2025-017 | 03 CENTRAL | 640528 | LITTLEBLUEW3 | 345 | 5.9899 | 6.0026 | 0.0127
ERAS-2025-017 | 03 CENTRAL | 640700 | ETNA-NE 3 | 345 | 8.3441 | 8.3567 | 0.0126
ERAS-2025-017 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.3015 | 7.3233 | 0.0218
ERAS-2025-017 | 03 CENTRAL | 763406 | GEN-2018-125 | 345 | 6.6359 | 6.6444 | 0.0085
ERAS-2025-017 | 03 CENTRAL | 763410 | G18-125-TAP | 345 | 6.9521 | 6.9614 | 0.0093
ERAS-2025-017 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.3903 | 9.6602 | 0.2699
ERAS-2025-017 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.3237 | 11.7271 | 0.4034
ERAS-2025-017 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 8.1395 | 8.1634 | 0.0239
ERAS-2025-017 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.2579 | 6.3036 | 0.0457
ERAS-2025-017 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.3327 | 6.3794 | 0.0467
ERAS-2025-017 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.5778 | 12.9402 | 0.3624
ERAS-2025-017 | 03 CENTRAL | 764980 | GEN-2020-008 | 345 | 7.2882 | 7.74 | 0.4518
ERAS-2025-017 | 03 CENTRAL | 768280 | G22-065-TAP | 230 | 6.2576 | 6.3014 | 0.0438
ERAS-2025-017 | 03 CENTRAL | 770039 | GEN-2023-SR2 | 115 | 10.9357 | 10.9814 | 0.0457
ERAS-2025-017 | 03 CENTRAL | 788746 | ERA-015 | 345 | 9.7917 | 14.8856 | 5.0939
ERAS-2025-017 | 03 CENTRAL | 788901 | MPT | 115 | 11.3912 | 11.4385 | 0.0473
ERAS-2025-017 | 03 CENTRAL | 788934 | ERA-017-GSU1 | 345 | 9.5344 | 18.0309 | 8.4965
ERAS-2025-017 | 03 CENTRAL | 788935 | ERA-017-GSU2 | 345 | 9.5344 | 18.0309 | 8.4965
ERAS-2025-017 | 03 CENTRAL | 788936 | ERA-2025-017 | 345 | 9.5344 | 18.0309 | 8.4965
ERAS-2025-017 | 03 CENTRAL | 999980 | DUMMY | 115 | 11.3912 | 11.4385 | 0.0473
ERAS-2025-017 | 03 CENTRAL | 999989 | ZSWSH_999989 | 115 | 6.1576 | 6.248 | 0.0904
ERAS-2025-017 | 03 CENTRAL | 999991 | ZSWSH_999991 | 115 | 5.7137 | 5.7715 | 0.0578
ERAS-2025-017 | 03 CENTRAL | 999992 | ZSWSH_999992 | 115 | 2.8321 | 2.8574 | 0.0253
ERAS-2025-019 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.6423 | 2.9777 | 0.3354
ERAS-2025-019 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.4966 | 4.5391 | 0.0425
ERAS-2025-019 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.6271 | 1.9859 | 0.3588
ERAS-2025-019 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.7568 | 1.9317 | 0.1749
ERAS-2025-019 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.4081 | 2.7468 | 0.3387
ERAS-2025-019 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 6.5685 | 6.8887 | 0.3202
ERAS-2025-019 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.6866 | 1.8474 | 0.1608
ERAS-2025-019 | 03 CENTRAL | 530724 | CENTENNIAL3 | 115 | 5.8921 | 5.9184 | 0.0263
ERAS-2025-019 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 6.2751 | 6.3736 | 0.0985
ERAS-2025-019 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 6.5685 | 6.8887 | 0.3202
ERAS-2025-019 | 03 CENTRAL | 788892 | MPT HIGH SID | 115 | 6.3835 | 6.6792 | 0.2957
ERAS-2025-019 | 03 CENTRAL | 789782 | ERAS-19 | 115 | 1.5599 | 1.9232 | 0.3633
ERAS-2025-019 | 03 CENTRAL | 999990 | DUMMY | 115 | 6.3835 | 6.6792 | 0.2957
ERAS-2025-029 | 03 CENTRAL | 532912 | EDWRDVL5 | 161 | 22.5943 | 22.776 | 0.1817
ERAS-2025-029 | 03 CENTRAL | 533238 | EDWARVL3 | 115 | 19.8147 | 19.8713 | 0.0566
ERAS-2025-029 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.4057 | 27.4828 | 0.0771
ERAS-2025-029 | 03 CENTRAL | 543017 | WETHRBY5 | 161 | 16.2678 | 16.3222 | 0.0544
ERAS-2025-029 | 03 CENTRAL | 543026 | TIFFANY5 | 161 | 20.4926 | 20.545 | 0.0524
ERAS-2025-029 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 38.1859 | 38.4158 | 0.2299
ERAS-2025-029 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.5734 | 32.6823 | 0.1089
ERAS-2025-029 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 39.3486 | 39.4966 | 0.148
ERAS-2025-029 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 28.2289 | 28.3855 | 0.1566
ERAS-2025-029 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 29.499 | 29.5697 | 0.0707
ERAS-2025-029 | 03 CENTRAL | 543134 | WALDRON5 | 161 | 15.3236 | 15.414 | 0.0904
ERAS-2025-029 | 03 CENTRAL | 546651 | BARBER 5 | 161 | 29.8887 | 30.1595 | 0.2708
ERAS-2025-029 | 03 CENTRAL | 546652 | QUIND 5 | 161 | 19.1198 | 19.5902 | 0.4704
ERAS-2025-029 | 03 CENTRAL | 546653 | NEARMAN5 | 161 | 21.2448 | 21.9268 | 0.682
ERAS-2025-029 | 03 CENTRAL | 546654 | SUNSET 5 | 161 | 18.5285 | 18.8819 | 0.3534
ERAS-2025-029 | 03 CENTRAL | 546655 | KAW W 5 | 161 | 22.3198 | 22.6148 | 0.295
ERAS-2025-029 | 03 CENTRAL | 546656 | MAYWOOD5 | 161 | 21.839 | 22.1454 | 0.3064
ERAS-2025-029 | 03 CENTRAL | 546658 | GIBBS 5 | 161 | 22.4323 | 22.6477 | 0.2154
ERAS-2025-029 | 03 CENTRAL | 546659 | CTR CTY5 | 161 | 15.2945 | 15.4674 | 0.1729
ERAS-2025-029 | 03 CENTRAL | 546663 | GM PLT 5 | 161 | 15.8554 | 16.1097 | 0.2543
ERAS-2025-029 | 03 CENTRAL | 546665 | TURNER 5 | 161 | 21.6499 | 21.8802 | 0.2303
ERAS-2025-029 | 03 CENTRAL | 546667 | FAIRFX-5 | 161 | 15.2086 | 15.4043 | 0.1957
ERAS-2025-029 | 03 CENTRAL | 546668 | PIPER 5 | 161 | 15.6472 | 15.793 | 0.1458
ERAS-2025-029 | 03 CENTRAL | 546669 | WOLCOTT5 | 161 | 17.7996 | 17.9683 | 0.1687
ERAS-2025-029 | 03 CENTRAL | 546670 | OAK KNOL | 69 | 8.7733 | 8.7941 | 0.0208
ERAS-2025-029 | 03 CENTRAL | 546672 | MORRIS 2 | 69 | 9.6603 | 9.6852 | 0.0249
ERAS-2025-029 | 03 CENTRAL | 546673 | GR WHL 2 | 69 | 11.2341 | 11.2676 | 0.0335
ERAS-2025-029 | 03 CENTRAL | 546674 | SPEAKER2 | 69 | 9.8527 | 9.879 | 0.0263
ERAS-2025-029 | 03 CENTRAL | 546675 | GW TAP 1 | 69 | 11.3415 | 11.3756 | 0.0341
ERAS-2025-029 | 03 CENTRAL | 546676 | GW TAP 2 | 69 | 9.0202 | 9.042 | 0.0218
ERAS-2025-029 | 03 CENTRAL | 546677 | MAYWOOD2 | 69 | 11.2695 | 11.3043 | 0.0348
ERAS-2025-029 | 03 CENTRAL | 546681 | MUNCIE 2 | 69 | 9.0196 | 9.0377 | 0.0181
ERAS-2025-029 | 03 CENTRAL | 546682 | EVERETT2 | 69 | 9.7849 | 9.8111 | 0.0262
ERAS-2025-029 | 03 CENTRAL | 546684 | FIBGLAS5 | 161 | 15.2947 | 15.5031 | 0.2084
ERAS-2025-029 | 03 CENTRAL | 546687 | COL PAL2 | 69 | 8.9911 | 9.008 | 0.0169
ERAS-2025-029 | 03 CENTRAL | 546691 | BARBER 2 | 69 | 9.2886 | 9.3055 | 0.0169
ERAS-2025-029 | 03 CENTRAL | 546692 | QUINDA 2 | 69 | 14.0828 | 14.1387 | 0.0559
ERAS-2025-029 | 03 CENTRAL | 546693 | V WEST2 | 69 | 9.9925 | 10.02 | 0.0275
ERAS-2025-029 | 03 CENTRAL | 546694 | QUINDB 2 | 69 | 13.978 | 14.0329 | 0.0549
ERAS-2025-029 | 03 CENTRAL | 546695 | QUINDC 2 | 69 | 13.7877 | 13.841 | 0.0533
ERAS-2025-029 | 03 CENTRAL | 546722 | MAYSOTH5 | 161 | 21.8533 | 22.1574 | 0.3041
ERAS-2025-029 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.1093 | 27.3919 | 0.2826
ERAS-2025-029 | 03 CENTRAL | 546751 | NM4 BUS | 161 | 20.3943 | 21.0197 | 0.6254
ERAS-2025-029 | 03 CENTRAL | 789000 | ERA-31-1 | 161 | 19.0362 | 19.5023 | 0.4661
ERAS-2025-029 | 03 CENTRAL | 789002 | ERA-31-2 | 161 | 19.0347 | 19.5008 | 0.4661
ERAS-2025-029 | 03 CENTRAL | 789010 | ERA-29 | 161 | 21.1497 | 21.8318 | 0.6821
ERAS-2025-031 | 03 CENTRAL | 532912 | EDWRDVL5 | 161 | 22.5836 | 22.776 | 0.1924
ERAS-2025-031 | 03 CENTRAL | 543017 | WETHRBY5 | 161 | 16.265 | 16.3222 | 0.0572
ERAS-2025-031 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 38.1571 | 38.4158 | 0.2587
ERAS-2025-031 | 03 CENTRAL | 543134 | WALDRON5 | 161 | 15.3207 | 15.414 | 0.0933
ERAS-2025-031 | 03 CENTRAL | 546651 | BARBER 5 | 161 | 29.8266 | 30.1595 | 0.3329
ERAS-2025-031 | 03 CENTRAL | 546652 | QUIND 5 | 161 | 18.8227 | 19.5902 | 0.7675
ERAS-2025-031 | 03 CENTRAL | 546653 | NEARMAN5 | 161 | 21.2624 | 21.9268 | 0.6644
ERAS-2025-031 | 03 CENTRAL | 546654 | SUNSET 5 | 161 | 18.5262 | 18.8819 | 0.3557
ERAS-2025-031 | 03 CENTRAL | 546655 | KAW W 5 | 161 | 22.2996 | 22.6148 | 0.3152
ERAS-2025-031 | 03 CENTRAL | 546656 | MAYWOOD5 | 161 | 21.833 | 22.1454 | 0.3124
ERAS-2025-031 | 03 CENTRAL | 546658 | GIBBS 5 | 161 | 22.4024 | 22.6477 | 0.2453
ERAS-2025-031 | 03 CENTRAL | 546659 | CTR CTY5 | 161 | 15.2054 | 15.4674 | 0.262
ERAS-2025-031 | 03 CENTRAL | 546663 | GM PLT 5 | 161 | 15.7057 | 16.1097 | 0.404
ERAS-2025-031 | 03 CENTRAL | 546665 | TURNER 5 | 161 | 21.6253 | 21.8802 | 0.2549
ERAS-2025-031 | 03 CENTRAL | 546667 | FAIRFX-5 | 161 | 15.1011 | 15.4043 | 0.3032
ERAS-2025-031 | 03 CENTRAL | 546668 | PIPER 5 | 161 | 15.644 | 15.793 | 0.149
ERAS-2025-031 | 03 CENTRAL | 546669 | WOLCOTT5 | 161 | 17.7955 | 17.9683 | 0.1728
ERAS-2025-031 | 03 CENTRAL | 546670 | OAK KNOL | 69 | 8.7695 | 8.7941 | 0.0246
ERAS-2025-031 | 03 CENTRAL | 546672 | MORRIS 2 | 69 | 9.6557 | 9.6852 | 0.0295
ERAS-2025-031 | 03 CENTRAL | 546673 | GR WHL 2 | 69 | 11.228 | 11.2676 | 0.0396
ERAS-2025-031 | 03 CENTRAL | 546674 | SPEAKER2 | 69 | 9.8463 | 9.879 | 0.0327
ERAS-2025-031 | 03 CENTRAL | 546675 | GW TAP 1 | 69 | 11.3352 | 11.3756 | 0.0404
ERAS-2025-031 | 03 CENTRAL | 546676 | GW TAP 2 | 69 | 9.0162 | 9.042 | 0.0258
ERAS-2025-031 | 03 CENTRAL | 546677 | MAYWOOD2 | 69 | 11.2632 | 11.3043 | 0.0411
ERAS-2025-031 | 03 CENTRAL | 546681 | MUNCIE 2 | 69 | 9.0136 | 9.0377 | 0.0241
ERAS-2025-031 | 03 CENTRAL | 546682 | EVERETT2 | 69 | 9.7775 | 9.8111 | 0.0336
ERAS-2025-031 | 03 CENTRAL | 546684 | FIBGLAS5 | 161 | 15.1778 | 15.5031 | 0.3253
ERAS-2025-031 | 03 CENTRAL | 546687 | COL PAL2 | 69 | 8.9856 | 9.008 | 0.0224
ERAS-2025-031 | 03 CENTRAL | 546691 | BARBER 2 | 69 | 9.2834 | 9.3055 | 0.0221
ERAS-2025-031 | 03 CENTRAL | 546692 | QUINDA 2 | 69 | 14.0625 | 14.1387 | 0.0762
ERAS-2025-031 | 03 CENTRAL | 546693 | V WEST2 | 69 | 9.9863 | 10.02 | 0.0337
ERAS-2025-031 | 03 CENTRAL | 546694 | QUINDB 2 | 69 | 13.9581 | 14.0329 | 0.0748
ERAS-2025-031 | 03 CENTRAL | 546695 | QUINDC 2 | 69 | 13.7684 | 13.841 | 0.0726
ERAS-2025-031 | 03 CENTRAL | 546722 | MAYSOTH5 | 161 | 21.8472 | 22.1574 | 0.3102
ERAS-2025-031 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.0929 | 27.3919 | 0.299
ERAS-2025-031 | 03 CENTRAL | 546750 | MUNCIE 5 | 161 | 16.0699 | 16.3013 | 0.2314
ERAS-2025-031 | 03 CENTRAL | 546751 | NM4 BUS | 161 | 20.4105 | 21.0197 | 0.6092
ERAS-2025-031 | 03 CENTRAL | 789000 | ERA-31-1 | 161 | 18.7376 | 19.5023 | 0.7647
ERAS-2025-031 | 03 CENTRAL | 789002 | ERA-31-2 | 161 | 18.7376 | 19.5008 | 0.7632
ERAS-2025-031 | 03 CENTRAL | 789010 | ERA-29 | 161 | 21.1733 | 21.8318 | 0.6585
ERAS-2025-032 | 03 CENTRAL | 530565 | SEWARD 2 | 69 | 5.6045 | 5.7293 | 0.1248
ERAS-2025-032 | 03 CENTRAL | 530569 | GB STH 2 | 69 | 4.5025 | 4.5529 | 0.0504
ERAS-2025-032 | 03 CENTRAL | 530576 | HUDSON 2 | 69 | 3.2727 | 3.3049 | 0.0322
ERAS-2025-032 | 03 CENTRAL | 530577 | ZOOK 2 | 69 | 2.6051 | 2.6255 | 0.0204
ERAS-2025-032 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 13.2647 | 13.4921 | 0.2274
ERAS-2025-032 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 8.3595 | 8.449 | 0.0895
ERAS-2025-032 | 03 CENTRAL | 530617 | EDWARDS3 | 115 | 2.7378 | 2.9777 | 0.2399
ERAS-2025-032 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.3427 | 4.5391 | 0.1964
ERAS-2025-032 | 03 CENTRAL | 530619 | KINSLEY3 | 115 | 1.8913 | 1.9859 | 0.0946
ERAS-2025-032 | 03 CENTRAL | 530621 | PAWNEE 3 | 115 | 1.8299 | 1.9317 | 0.1018
ERAS-2025-032 | 03 CENTRAL | 530622 | PAWN-ED3 | 115 | 2.5458 | 2.7468 | 0.201
ERAS-2025-032 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.6013 | 6.8887 | 1.2874
ERAS-2025-032 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.2504 | 5.5769 | 0.3265
ERAS-2025-032 | 03 CENTRAL | 530685 | LARNED3 | 115 | 1.7541 | 1.8474 | 0.0933
ERAS-2025-032 | 03 CENTRAL | 530724 | CENTENNIAL3 | 115 | 5.7941 | 5.9184 | 0.1243
ERAS-2025-032 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 10.907 | 10.9454 | 0.0384
ERAS-2025-032 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 11.5897 | 11.6888 | 0.0991
ERAS-2025-032 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 11.8515 | 11.9552 | 0.1037
ERAS-2025-032 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 27.4276 | 27.5618 | 0.1342
ERAS-2025-032 | 03 CENTRAL | 533416 | RENO 3 | 115 | 30.2858 | 30.3753 | 0.0895
ERAS-2025-032 | 03 CENTRAL | 533419 | HEC 3 | 115 | 25.022 | 25.1323 | 0.1103
ERAS-2025-032 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 26.6794 | 26.8049 | 0.1255
ERAS-2025-032 | 03 CENTRAL | 533502 | CESSNA 2 | 69 | 4.7765 | 4.7789 | 0.0024
ERAS-2025-032 | 03 CENTRAL | 533503 | CESSNAJ2 | 69 | 4.8456 | 4.848 | 0.0024
ERAS-2025-032 | 03 CENTRAL | 533507 | 18&PLUM2 | 69 | 4.96 | 4.9625 | 0.0025
ERAS-2025-032 | 03 CENTRAL | 533509 | 11HALST2 | 69 | 5.6783 | 5.6817 | 0.0034
ERAS-2025-032 | 03 CENTRAL | 533511 | 14LORAN2 | 69 | 5.3168 | 5.3197 | 0.0029
ERAS-2025-032 | 03 CENTRAL | 533513 | HEC 2 | 69 | 7.5277 | 7.5337 | 0.006
ERAS-2025-032 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.0743 | 6.0782 | 0.0039
ERAS-2025-032 | 03 CENTRAL | 533522 | 17HUXMN2 | 69 | 5.4773 | 5.4804 | 0.0031
ERAS-2025-032 | 03 CENTRAL | 533523 | 17 PLUM2 | 69 | 5.0143 | 5.0169 | 0.0026
ERAS-2025-032 | 03 CENTRAL | 539010 | SADLHRN3 | 115 | 4.898 | 5.515 | 0.617
ERAS-2025-032 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.197 | 4.2052 | 0.0082
ERAS-2025-032 | 03 CENTRAL | 539649 | SAWYER 3 | 115 | 5.0327 | 5.2556 | 0.2229
ERAS-2025-032 | 03 CENTRAL | 539651 | RVROAD 3 | 115 | 4.8765 | 5.1823 | 0.3058
ERAS-2025-032 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 5.8697 | 5.9137 | 0.044
ERAS-2025-032 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.0465 | 8.2777 | 0.2312
ERAS-2025-032 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 13.39 | 13.6254 | 0.2354
ERAS-2025-032 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.5481 | 8.6322 | 0.0841
ERAS-2025-032 | 03 CENTRAL | 539681 | NWGBEND3 | 115 | 8.6925 | 8.79 | 0.0975
ERAS-2025-032 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 3.1212 | 3.1334 | 0.0122
ERAS-2025-032 | 03 CENTRAL | 539687 | PRATT 3 | 115 | 4.8638 | 5.168 | 0.3042
ERAS-2025-032 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 5.2748 | 5.3102 | 0.0354
ERAS-2025-032 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.9289 | 6.3736 | 0.4447
ERAS-2025-032 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.6013 | 6.8887 | 1.2874
ERAS-2025-032 | 03 CENTRAL | 539753 | PRATTENERGY3 | 115 | 3.7762 | 3.9962 | 0.22
ERAS-2025-032 | 03 CENTRAL | 539754 | SEMCRDE3 | 115 | 2.4493 | 2.5408 | 0.0915
ERAS-2025-032 | 03 CENTRAL | 539756 | SKLYVL_GOAB3 | 115 | 2.5147 | 2.6112 | 0.0965
ERAS-2025-032 | 03 CENTRAL | 584710 | ASGI2015-001 | 115 | 2.6134 | 2.7087 | 0.0953
ERAS-2025-032 | 03 CENTRAL | 788892 | MPT HIGH SID | 115 | 5.378 | 6.6792 | 1.3012
ERAS-2025-032 | 03 CENTRAL | 789782 | ERAS-19 | 115 | 1.8361 | 1.9232 | 0.0871
ERAS-2025-032 | 03 CENTRAL | 999985 | ZSWSH_999985 | 115 | 4.8765 | 5.1823 | 0.3058
ERAS-2025-032 | 03 CENTRAL | 999990 | DUMMY | 115 | 5.378 | 6.6792 | 1.3012
ERAS-2025-033 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.0486 | 8.0574 | 0.0088
ERAS-2025-033 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.0747 | 11.0835 | 0.0088
ERAS-2025-033 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.1256 | 8.1302 | 0.0046
ERAS-2025-033 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 18.6322 | 18.6451 | 0.0129
ERAS-2025-033 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 14.1042 | 14.1904 | 0.0862
ERAS-2025-033 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 10.8316 | 10.8547 | 0.0231
ERAS-2025-033 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 8.3519 | 8.3657 | 0.0138
ERAS-2025-033 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 8.3519 | 8.3657 | 0.0138
ERAS-2025-033 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 9.4327 | 9.5007 | 0.068
ERAS-2025-033 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 8.3566 | 8.4094 | 0.0528
ERAS-2025-033 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 6.3507 | 6.588 | 0.2373
ERAS-2025-033 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 6.3507 | 6.588 | 0.2373
ERAS-2025-033 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 9.6132 | 10.2088 | 0.5956
ERAS-2025-033 | 03 CENTRAL | 539646 | KISMET 3 | 115 | 5.4356 | 5.4511 | 0.0155
ERAS-2025-033 | 03 CENTRAL | 539652 | CMRIVTP3 | 115 | 6.1099 | 6.1242 | 0.0143
ERAS-2025-033 | 03 CENTRAL | 539654 | CIM-PLT3 | 115 | 6.9081 | 6.9205 | 0.0124
ERAS-2025-033 | 03 CENTRAL | 539659 | CUDAHY 3 | 115 | 4.1713 | 4.2088 | 0.0375
ERAS-2025-033 | 03 CENTRAL | 539664 | GRNBURG3 | 115 | 4.1061 | 4.1323 | 0.0262
ERAS-2025-033 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.8917 | 2.9267 | 0.035
ERAS-2025-033 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 12.9865 | 14.1141 | 1.1276
ERAS-2025-033 | 03 CENTRAL | 539672 | E-LIBER3 | 115 | 5.1297 | 5.137 | 0.0073
ERAS-2025-033 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 6.9019 | 7.1925 | 0.2906
ERAS-2025-033 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 8.293 | 8.713 | 0.42
ERAS-2025-033 | 03 CENTRAL | 539690 | E-PINE 3 | 115 | 4.3679 | 4.3732 | 0.0053
ERAS-2025-033 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 10.1237 | 10.2927 | 0.169
ERAS-2025-033 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 9.6149 | 9.6857 | 0.0708
ERAS-2025-033 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 6.4907 | 6.7332 | 0.2425
ERAS-2025-033 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 8.6613 | 9.138 | 0.4767
ERAS-2025-033 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.9633 | 6.1139 | 0.1506
ERAS-2025-033 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 14.0117 | 14.1886 | 0.1769
ERAS-2025-033 | 03 CENTRAL | 539761 | SSTARW 3 | 115 | 3.7929 | 3.8202 | 0.0273
ERAS-2025-033 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.4479 | 4.4882 | 0.0403
ERAS-2025-033 | 03 CENTRAL | 539766 | GRB_NIN3 | 115 | 4.1061 | 4.1323 | 0.0262
ERAS-2025-033 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 13.0832 | 14.187 | 1.1038
ERAS-2025-033 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.8917 | 2.9267 | 0.035
ERAS-2025-033 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.8917 | 2.9267 | 0.035
ERAS-2025-033 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.5124 | 4.5757 | 0.0633
ERAS-2025-033 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.0328 | 3.0613 | 0.0285
ERAS-2025-033 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.176 | 13.219 | 0.043
ERAS-2025-033 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.5331 | 13.6094 | 0.0763
ERAS-2025-033 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.0457 | 11.0756 | 0.0299
ERAS-2025-033 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.285 | 12.3471 | 0.0621
ERAS-2025-033 | 03 CENTRAL | 539816 | SADDLE7 | 345 | 11.6869 | 11.728 | 0.0411
ERAS-2025-033 | 03 CENTRAL | 539823 | IRONSTAR7 | 345 | 10.1873 | 10.2181 | 0.0308
ERAS-2025-033 | 03 CENTRAL | 539824 | IRS7 115 KV | 115 | 14.9846 | 15.004 | 0.0194
ERAS-2025-033 | 03 CENTRAL | 539831 | WESTPLN7 | 345 | 11.2231 | 11.2743 | 0.0512
ERAS-2025-033 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.9287 | 10.957 | 0.0283
ERAS-2025-033 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.1779 | 9.1976 | 0.0197
ERAS-2025-033 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.1798 | 9.1995 | 0.0197
ERAS-2025-033 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.5527 | 8.5697 | 0.017
ERAS-2025-033 | 03 CENTRAL | 539944 | LOCHS 3 | 115 | 5.5395 | 5.7192 | 0.1797
ERAS-2025-033 | 03 CENTRAL | 640527 | MACON 3 | 345 | 7.1019 | 7.1033 | 0.0014
ERAS-2025-033 | 03 CENTRAL | 640528 | LITTLEBLUEW3 | 345 | 6.0016 | 6.0026 | 0.001
ERAS-2025-033 | 03 CENTRAL | 762471 | GEN-2018-009 | 115 | 3.2184 | 3.2202 | 0.0018
ERAS-2025-033 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.6299 | 9.6602 | 0.0303
ERAS-2025-033 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.6815 | 11.7271 | 0.0456
ERAS-2025-033 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 7.8059 | 8.1634 | 0.3575
ERAS-2025-033 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.2861 | 6.3036 | 0.0175
ERAS-2025-033 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.3615 | 6.3794 | 0.0179
ERAS-2025-033 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.899 | 12.9402 | 0.0412
ERAS-2025-033 | 03 CENTRAL | 768280 | G22-065-TAP | 230 | 6.285 | 6.3014 | 0.0164
ERAS-2025-033 | 03 CENTRAL | 770039 | GEN-2023-SR2 | 115 | 10.286 | 10.9814 | 0.6954
ERAS-2025-033 | 03 CENTRAL | 788746 | ERA-015 | 345 | 14.8778 | 14.8856 | 0.0078
ERAS-2025-033 | 03 CENTRAL | 788901 | MPT | 115 | 10.2858 | 11.4385 | 1.1527
ERAS-2025-033 | 03 CENTRAL | 788934 | ERA-017-GSU1 | 345 | 18.0215 | 18.0309 | 0.0094
ERAS-2025-033 | 03 CENTRAL | 788935 | ERA-017-GSU2 | 345 | 18.0215 | 18.0309 | 0.0094
ERAS-2025-033 | 03 CENTRAL | 788936 | ERA-2025-017 | 345 | 18.0215 | 18.0309 | 0.0094
ERAS-2025-033 | 03 CENTRAL | 999980 | DUMMY | 115 | 10.2858 | 11.4385 | 1.1527
ERAS-2025-034 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.8477 | 6.8505 | 0.0028
ERAS-2025-034 | 03 CENTRAL | 300763 | 2WASHBRN | 69 | 6.8427 | 6.8455 | 0.0028
ERAS-2025-034 | 03 CENTRAL | 301462 | 2COMMNEO | 69 | 5.9803 | 5.9847 | 0.0044
ERAS-2025-034 | 03 CENTRAL | 505480 | BEAVER 5 | 161 | 10.7211 | 10.728 | 0.0069
ERAS-2025-034 | 03 CENTRAL | 505485 | WASHBURN5 | 161 | 8.1481 | 8.1565 | 0.0084
ERAS-2025-034 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.8911 | 16.0083 | 0.1172
ERAS-2025-034 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.794 | 16.9094 | 0.1154
ERAS-2025-034 | 03 CENTRAL | 505490 | CARTHG 2 | 69 | 14.0137 | 14.0407 | 0.027
ERAS-2025-034 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 26.3408 | 26.3552 | 0.0144
ERAS-2025-034 | 03 CENTRAL | 510417 | VINTAJC4 | 138 | 5.2845 | 5.2874 | 0.0029
ERAS-2025-034 | 03 CENTRAL | 512630 | MIAMI 2 | 69 | 12.771 | 12.791 | 0.02
ERAS-2025-034 | 03 CENTRAL | 512631 | MIAMI 5 | 161 | 9.8997 | 9.931 | 0.0313
ERAS-2025-034 | 03 CENTRAL | 512632 | AFTON 5 | 161 | 8.7619 | 8.7747 | 0.0128
ERAS-2025-034 | 03 CENTRAL | 513020 | MIAMI1 2 | 69 | 10.8977 | 10.9123 | 0.0146
ERAS-2025-034 | 03 CENTRAL | 513022 | MIAMI4 2 | 69 | 9.2464 | 9.2569 | 0.0105
ERAS-2025-034 | 03 CENTRAL | 513026 | COMMTP 2 | 69 | 9.7066 | 9.7182 | 0.0116
ERAS-2025-034 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 17.9163 | 17.9293 | 0.013
ERAS-2025-034 | 03 CENTRAL | 532911 | MUSTNG5 | 161 | 6.7486 | 6.7516 | 0.003
ERAS-2025-034 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.1413 | 8.1459 | 0.0046
ERAS-2025-034 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.2847 | 23.3216 | 0.0369
ERAS-2025-034 | 03 CENTRAL | 532939 | N345 4 5 | 161 | 23.1226 | 23.158 | 0.0354
ERAS-2025-034 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2646 | 7.266 | 0.0014
ERAS-2025-034 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 24.9206 | 24.9498 | 0.0292
ERAS-2025-034 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 24.9628 | 24.992 | 0.0292
ERAS-2025-034 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 24.8484 | 24.8774 | 0.029
ERAS-2025-034 | 03 CENTRAL | 533023 | N345 3 4 | 138 | 24.5584 | 24.5861 | 0.0277
ERAS-2025-034 | 03 CENTRAL | 533482 | MUSTNG2 | 69 | 7.4672 | 7.4685 | 0.0013
ERAS-2025-034 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0019 | 24.0179 | 0.016
ERAS-2025-034 | 03 CENTRAL | 547400 | MON376J2 | 69 | 7.8302 | 7.8345 | 0.0043
ERAS-2025-034 | 03 CENTRAL | 547401 | MON376 2 | 69 | 8.0606 | 8.0652 | 0.0046
ERAS-2025-034 | 03 CENTRAL | 547402 | MON416J2 | 69 | 6.2444 | 6.2471 | 0.0027
ERAS-2025-034 | 03 CENTRAL | 547403 | MON416 2 | 69 | 5.9708 | 5.9733 | 0.0025
ERAS-2025-034 | 03 CENTRAL | 547404 | PUR390 2 | 69 | 2.2443 | 2.2446 | 0.0003
ERAS-2025-034 | 03 CENTRAL | 547405 | MON352J2 | 69 | 8.9108 | 8.9164 | 0.0056
ERAS-2025-034 | 03 CENTRAL | 547406 | MON352 2 | 69 | 8.5198 | 8.525 | 0.0052
ERAS-2025-034 | 03 CENTRAL | 547407 | MON311J2 | 69 | 8.1126 | 8.1172 | 0.0046
ERAS-2025-034 | 03 CENTRAL | 547408 | MON311 2 | 69 | 7.9919 | 7.9965 | 0.0046
ERAS-2025-034 | 03 CENTRAL | 547409 | SCAM66 2 | 69 | 3.195 | 3.1976 | 0.0026
ERAS-2025-034 | 03 CENTRAL | 547411 | COL282 2 | 69 | 7.0067 | 7.0201 | 0.0134
ERAS-2025-034 | 03 CENTRAL | 547412 | SEK225T2 | 69 | 4.1633 | 4.1681 | 0.0048
ERAS-2025-034 | 03 CENTRAL | 547413 | SEK225 2 | 69 | 4.1475 | 4.1522 | 0.0047
ERAS-2025-034 | 03 CENTRAL | 547414 | SMN425 2 | 69 | 2.7613 | 2.7634 | 0.0021
ERAS-2025-034 | 03 CENTRAL | 547415 | SHR444 2 | 69 | 3.2119 | 3.2147 | 0.0028
ERAS-2025-034 | 03 CENTRAL | 547416 | CHE491T2 | 69 | 1.963 | 1.9639 | 0.0009
ERAS-2025-034 | 03 CENTRAL | 547417 | CHE491 2 | 69 | 1.8779 | 1.8787 | 0.0008
ERAS-2025-034 | 03 CENTRAL | 547420 | WEL186 2 | 69 | 1.4435 | 1.4439 | 0.0004
ERAS-2025-034 | 03 CENTRAL | 547426 | SEN375 2 | 69 | 3.2159 | 3.2189 | 0.003
ERAS-2025-034 | 03 CENTRAL | 547431 | WEB105 2 | 69 | 8.3867 | 8.4068 | 0.0201
ERAS-2025-034 | 03 CENTRAL | 547438 | EXP449T2 | 69 | 9.8983 | 9.933 | 0.0347
ERAS-2025-034 | 03 CENTRAL | 547439 | EXP4492 | 69 | 8.1156 | 8.1388 | 0.0232
ERAS-2025-034 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 6.3799 | 6.3838 | 0.0039
ERAS-2025-034 | 03 CENTRAL | 547455 | COL473 2 | 69 | 6.8887 | 6.9016 | 0.0129
ERAS-2025-034 | 03 CENTRAL | 547459 | WWR477 | 161 | 24.0265 | 24.8597 | 0.8332
ERAS-2025-034 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 14.5663 | 14.7745 | 0.2082
ERAS-2025-034 | 03 CENTRAL | 547463 | KOD471 2 | 69 | 15.4262 | 15.4949 | 0.0687
ERAS-2025-034 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 17.153 | 17.3363 | 0.1833
ERAS-2025-034 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 20.8488 | 21.171 | 0.3222
ERAS-2025-034 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 17.3234 | 17.3485 | 0.0251
ERAS-2025-034 | 03 CENTRAL | 547469 | RIV4525 | 161 | 26.4896 | 26.9859 | 0.4963
ERAS-2025-034 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 20.1075 | 20.5532 | 0.4457
ERAS-2025-034 | 03 CENTRAL | 547471 | NEO184 5 | 161 | 14.6539 | 14.7467 | 0.0928
ERAS-2025-034 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 18.0894 | 18.3386 | 0.2492
ERAS-2025-034 | 03 CENTRAL | 547473 | RDS295 5 | 161 | 17.3234 | 17.3485 | 0.0251
ERAS-2025-034 | 03 CENTRAL | 547476 | ASB349 5 | 161 | 11.4675 | 11.5147 | 0.0472
ERAS-2025-034 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.9507 | 13.0508 | 0.1001
ERAS-2025-034 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 14.1287 | 14.1698 | 0.0411
ERAS-2025-034 | 03 CENTRAL | 547480 | MON383 5 | 161 | 14.7863 | 14.8247 | 0.0384
ERAS-2025-034 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.4167 | 20.8691 | 0.4524
ERAS-2025-034 | 03 CENTRAL | 547485 | CAR395 5 | 161 | 12.5161 | 12.5788 | 0.0627
ERAS-2025-034 | 03 CENTRAL | 547486 | HOC404 4 | 138 | 6.856 | 6.8706 | 0.0146
ERAS-2025-034 | 03 CENTRAL | 547487 | HOC404 5 | 161 | 14.0738 | 14.1705 | 0.0967
ERAS-2025-034 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 14.9988 | 15.1464 | 0.1476
ERAS-2025-034 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 19.2752 | 19.5384 | 0.2632
ERAS-2025-034 | 03 CENTRAL | 547496 | NOL435 5 | 161 | 10.1813 | 10.1957 | 0.0144
ERAS-2025-034 | 03 CENTRAL | 547498 | STL439 5 | 161 | 26.4495 | 27.4622 | 1.0127
ERAS-2025-034 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 9.8535 | 9.8589 | 0.0054
ERAS-2025-034 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.755 | 14.9345 | 0.1795
ERAS-2025-034 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 24.9342 | 25.3612 | 0.427
ERAS-2025-034 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 24.5565 | 24.9778 | 0.4213
ERAS-2025-034 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 26.0607 | 26.5369 | 0.4762
ERAS-2025-034 | 03 CENTRAL | 547524 | NEO 56 2 | 69 | 8.0208 | 8.0351 | 0.0143
ERAS-2025-034 | 03 CENTRAL | 547525 | JOP 59 2 | 69 | 20.6144 | 20.7575 | 0.1431
ERAS-2025-034 | 03 CENTRAL | 547526 | JOP 64 2 | 69 | 20.4294 | 20.5708 | 0.1414
ERAS-2025-034 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.3858 | 9.4112 | 0.0254
ERAS-2025-034 | 03 CENTRAL | 547530 | COL 94 2 | 69 | 8.0936 | 8.1115 | 0.0179
ERAS-2025-034 | 03 CENTRAL | 547531 | COL476 2 | 69 | 7.0759 | 7.0896 | 0.0137
ERAS-2025-034 | 03 CENTRAL | 547532 | CAR108 2 | 69 | 7.4552 | 7.4677 | 0.0125
ERAS-2025-034 | 03 CENTRAL | 547533 | ATL109 2 | 69 | 22.9226 | 23.0772 | 0.1546
ERAS-2025-034 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 19.3779 | 19.4947 | 0.1168
ERAS-2025-034 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 14.0869 | 14.0947 | 0.0078
ERAS-2025-034 | 03 CENTRAL | 547539 | JOP145 2 | 69 | 21.6295 | 21.7952 | 0.1657
ERAS-2025-034 | 03 CENTRAL | 547540 | MON152 2 | 69 | 11.6102 | 11.6193 | 0.0091
ERAS-2025-034 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 18.549 | 18.653 | 0.104
ERAS-2025-034 | 03 CENTRAL | 547543 | NEO184 2 | 69 | 11.9032 | 11.9322 | 0.029
ERAS-2025-034 | 03 CENTRAL | 547551 | GAT490 2 | 69 | 15.1253 | 15.1986 | 0.0733
ERAS-2025-034 | 03 CENTRAL | 547554 | BAX492 2 | 69 | 11.2072 | 11.2384 | 0.0312
ERAS-2025-034 | 03 CENTRAL | 547555 | GAL278 2 | 69 | 13.819 | 13.8843 | 0.0653
ERAS-2025-034 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 17.0975 | 17.1868 | 0.0893
ERAS-2025-034 | 03 CENTRAL | 547557 | JOP284 2 | 69 | 17.6099 | 17.7134 | 0.1035
ERAS-2025-034 | 03 CENTRAL | 547559 | TIP292 2 | 69 | 10.3561 | 10.3859 | 0.0298
ERAS-2025-034 | 03 CENTRAL | 547574 | JOP341 2 | 69 | 16.1358 | 16.2225 | 0.0867
ERAS-2025-034 | 03 CENTRAL | 547588 | JOP372 2 | 69 | 16.0877 | 16.1727 | 0.085
ERAS-2025-034 | 03 CENTRAL | 547589 | RAC375 2 | 69 | 6.806 | 6.8204 | 0.0144
ERAS-2025-034 | 03 CENTRAL | 547590 | QUA377 2 | 69 | 8.3447 | 8.3593 | 0.0146
ERAS-2025-034 | 03 CENTRAL | 547591 | MON383 2 | 69 | 13.4379 | 13.4508 | 0.0129
ERAS-2025-034 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.8002 | 15.8942 | 0.094
ERAS-2025-034 | 03 CENTRAL | 547593 | JOP391 5 | 161 | 13.81 | 13.9752 | 0.1652
ERAS-2025-034 | 03 CENTRAL | 547595 | RNM393 2 | 69 | 21.1074 | 21.2422 | 0.1348
ERAS-2025-034 | 03 CENTRAL | 547601 | HOC404 2 | 69 | 11.9923 | 12.025 | 0.0327
ERAS-2025-034 | 03 CENTRAL | 547602 | RIV406 2 | 69 | 16.4506 | 16.5315 | 0.0809
ERAS-2025-034 | 03 CENTRAL | 547607 | JOP422 5 | 161 | 13.5997 | 13.769 | 0.1693
ERAS-2025-034 | 03 CENTRAL | 547608 | JOP430 2 | 69 | 16.449 | 16.5436 | 0.0946
ERAS-2025-034 | 03 CENTRAL | 547685 | PLB447 2 | 69 | 15.1153 | 15.1879 | 0.0726
ERAS-2025-034 | 03 CENTRAL | 547690 | GLF339 2 | 69 | 12.3183 | 12.3666 | 0.0483
ERAS-2025-034 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 15.8566 | 15.9963 | 0.1397
ERAS-2025-034 | 03 CENTRAL | 547730 | NFRKRG WF | 161 | 5.3271 | 5.336 | 0.0089
ERAS-2025-034 | 03 CENTRAL | 547732 | KINGSPT WF | 161 | 7.1102 | 7.1198 | 0.0096
ERAS-2025-034 | 03 CENTRAL | 547736 | NEO184KAMO_2 | 69 | 10.5717 | 10.5874 | 0.0157
ERAS-2025-034 | 03 CENTRAL | 760242 | GEN-2017-188 | 161 | 2.0328 | 2.0336 | 0.0008
ERAS-2025-034 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 16.1077 | 16.23 | 0.1223
ERAS-2025-034 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 19.613 | 19.8022 | 0.1892
ERAS-2025-034 | 03 CENTRAL | 764315 | GEN-2020-088 | 161 | 13.7491 | 13.7879 | 0.0388
ERAS-2025-034 | 03 CENTRAL | 788908 | ERA-2025-034 | 161 | 25.8126 | 26.8262 | 1.0136

## SCRCCT Results
Group | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Analysis Needed
04 SOUTHEAST | ERAS-2025-005 | 5.4287 | FAIL | 20.5805 | PASS | None | PASS | YES
04 SOUTHEAST | ERAS-2025-022 | 6.6277 | PASS | 11.561 | PASS | None | PASS | NO
04 SOUTHEAST | ERAS-2025-025 | 6.824 | PASS | 18.4047 | PASS | None | PASS | NO
03 CENTRAL | ERAS-2025-015 | 7.4207 | PASS | 1.3446 | PASS | None | PASS | NO
03 CENTRAL | ERAS-2025-019 | 2 | FAIL | 16.4077 | PASS | 0.97351 | FAIL | YES
03 CENTRAL | ERAS-2025-029 | 24.8913 | PASS | 0.72263 | PASS | None | PASS | NO
03 CENTRAL | ERAS-2025-032 | 1.7199 | FAIL | 1.6956 | PASS | 0.97351 | FAIL | YES
03 CENTRAL | ERAS-2025-033 | 3.7215 | FAIL | 0.040924 | FAIL | None | PASS | YES
05 SOUTHWEST | ERAS-2025-018 | 3.8662 | FAIL | 21.7138 | PASS | 2.1577 | FAIL | YES
05 SOUTHWEST | ERAS-2025-020 | 4.4926 | FAIL | 44.3234 | PASS | None | PASS | YES
05 SOUTHWEST | ERAS-2025-021 | 1.4743 | FAIL | 16.8616 | PASS | None | PASS | YES
05 SOUTHWEST | ERAS-2025-027 | 5.8567 | FAIL | 1.8635 | PASS | 4.1916 | FAIL | YES
05 SOUTHWEST | ERAS-2025-028 | 5.5485 | FAIL | 3.1349 | PASS | 4.1916 | FAIL | YES
05 SOUTHWEST | ERAS-2025-030 | 1.808 | FAIL | 1.8477 | PASS | 2.1577 | FAIL | YES

## SCRCCT
Study Name | Group | Season | GI Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pgen (MW) | IBR Rating (MVA)
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | base | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | base | 12.407 | PASS | 101.9794 | PASS | 101879.4245 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | base | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | base | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4069 | PASS | 33.7968 | PASS | 33696.8419 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4069 | PASS | 101.7881 | PASS | 101688.0583 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3323 | PASS | 14.6585 | PASS | 14558.5289 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8559 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 12.4071 | PASS | 33.7932 | PASS | 33693.1603 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 12.4071 | PASS | 101.9713 | PASS | 101871.2667 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 7.3313 | PASS | 14.6604 | PASS | 14560.3522 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 10.1535 | PASS | 19.1427 | PASS | 19042.7082 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.407 | PASS | 33.7942 | PASS | 33694.2241 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.407 | PASS | 101.9113 | PASS | 101811.3084 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 7.3324 | PASS | 14.6587 | PASS | 14558.6677 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8682 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 8.9909 | PASS | 45.025 | PASS | 44925.0177 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 8.9909 | PASS | 23.2915 | PASS | 23191.479 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7611 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8511 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 5.4384 | FAIL | 35.0386 | PASS | 34938.6164 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 5.4384 | FAIL | 22.3992 | PASS | 22299.1854 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 7.3329 | PASS | 14.6574 | PASS | 14557.4365 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.9143 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.4047 | PASS | 33.8314 | PASS | 33731.4033 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.4047 | PASS | 100.2099 | PASS | 100109.8926 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 7.3311 | PASS | 14.6591 | PASS | 14559.0799 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 10.1553 | PASS | 19.1427 | PASS | 19042.6987 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 12.4059 | PASS | 33.7934 | PASS | 33693.4175 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 12.4059 | PASS | 101.8965 | PASS | 101796.502 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 7.3321 | PASS | 14.6575 | PASS | 14557.5162 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 10.1552 | PASS | 19.143 | PASS | 19042.954 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4059 | PASS | 33.7969 | PASS | 33696.913 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4059 | PASS | 101.7407 | PASS | 101640.7302 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 7.3326 | PASS | 14.6573 | PASS | 14557.292 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.9211 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.4065 | PASS | 33.793 | PASS | 33693.0418 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.4065 | PASS | 101.9471 | PASS | 101847.0731 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 7.3316 | PASS | 14.6579 | PASS | 14557.9482 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 10.1544 | PASS | 19.143 | PASS | 19042.9923 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.86 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 12.4069 | PASS | 101.9795 | PASS | 101879.491 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8537 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8454 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4055 | PASS | 33.7958 | PASS | 33695.7965 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4055 | PASS | 101.7779 | PASS | 101677.9202 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 7.3327 | PASS | 14.6579 | PASS | 14557.8978 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8953 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 12.4032 | PASS | 33.8373 | PASS | 33737.3216 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 12.4032 | PASS | 99.8991 | PASS | 99799.0692 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 7.3306 | PASS | 14.6605 | PASS | 14560.476 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 10.1552 | PASS | 19.1424 | PASS | 19042.3986 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8874 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 12.407 | PASS | 101.9774 | PASS | 101877.3758 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8416 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8488 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8874 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 12.407 | PASS | 101.9774 | PASS | 101877.3758 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 7.3324 | PASS | 14.6588 | PASS | 14558.8416 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8488 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 12.4048 | PASS | 33.7925 | PASS | 33692.4673 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 12.4048 | PASS | 101.8826 | PASS | 101782.5523 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 7.3308 | PASS | 14.6603 | PASS | 14560.3425 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 10.1539 | PASS | 19.1426 | PASS | 19042.623 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 12.4069 | PASS | 33.7962 | PASS | 33696.2199 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 12.4069 | PASS | 101.8045 | PASS | 101704.5422 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 7.3293 | PASS | 14.663 | PASS | 14563.0262 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 10.1517 | PASS | 19.1418 | PASS | 19041.8468 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.864 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 12.407 | PASS | 101.9792 | PASS | 101879.1664 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.9108 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 10.1553 | PASS | 19.1428 | PASS | 19042.8349 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 12.4066 | PASS | 33.7937 | PASS | 33693.6931 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 12.4066 | PASS | 101.9188 | PASS | 101818.7507 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 7.3322 | PASS | 14.6592 | PASS | 14559.1821 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 10.1548 | PASS | 19.1428 | PASS | 19042.7933 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.4045 | PASS | 33.7923 | PASS | 33692.2918 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.4045 | PASS | 101.8844 | PASS | 101784.38 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 7.332 | PASS | 14.6589 | PASS | 14558.9408 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 10.1552 | PASS | 19.1428 | PASS | 19042.7924 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 580555 [MONETT345 345.00] CKT 1 | 12.4007 | PASS | 33.7906 | PASS | 33690.5858 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 580555 [MONETT345 345.00] CKT 1 | 12.4007 | PASS | 101.7612 | PASS | 101661.2097 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 580555 [MONETT345 345.00] CKT 1 | 7.3308 | PASS | 14.6609 | PASS | 14560.9412 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 580555 [MONETT345 345.00] CKT 1 | 10.155 | PASS | 19.1426 | PASS | 19042.6109 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8359 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4069 | PASS | 101.9791 | PASS | 101879.0543 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 7.3322 | PASS | 14.6591 | PASS | 14559.0691 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 10.1557 | PASS | 19.1348 | PASS | 19034.8362 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8531 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 12.4069 | PASS | 101.9787 | PASS | 101878.7244 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 7.3305 | PASS | 14.6528 | PASS | 14552.7632 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 10.1336 | PASS | 19.1512 | PASS | 19051.1641 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 12.4071 | PASS | 33.793 | PASS | 33692.9874 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 12.4071 | PASS | 101.9773 | PASS | 101877.2658 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 7.3306 | PASS | 14.657 | PASS | 14556.998 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 10.1405 | PASS | 19.1818 | PASS | 19081.819 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9215 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.7659 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 7.3319 | PASS | 14.6565 | PASS | 14556.5493 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 9.9238 | PASS | 19.2158 | PASS | 19115.8193 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8664 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.3589 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.7364 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 9.7688 | PASS | 19.2709 | PASS | 19170.9461 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8659 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.3672 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.7173 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 9.7683 | PASS | 19.2686 | PASS | 19168.6144 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8679 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.3295 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14558.9865 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 10.1548 | PASS | 19.1423 | PASS | 19042.3225 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8637 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.4069 | PASS | 101.9794 | PASS | 101879.4106 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 7.3323 | PASS | 14.6588 | PASS | 14558.8157 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 10.1556 | PASS | 19.1428 | PASS | 19042.8243 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8681 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4069 | PASS | 101.9771 | PASS | 101877.0918 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 7.3315 | PASS | 14.6593 | PASS | 14559.2931 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 9.8944 | PASS | 19.1931 | PASS | 19093.0992 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 12.4068 | PASS | 33.793 | PASS | 33692.977 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 12.4068 | PASS | 101.9678 | PASS | 101867.8225 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 7.3296 | PASS | 14.6489 | PASS | 14548.8576 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 10.0201 | PASS | 19.1762 | PASS | 19076.1992 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8586 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.4069 | PASS | 101.9793 | PASS | 101879.2545 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 7.3323 | PASS | 14.6589 | PASS | 14558.8523 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 10.1558 | PASS | 19.1429 | PASS | 19042.8839 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8888 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.407 | PASS | 101.9789 | PASS | 101878.9298 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 7.3326 | PASS | 14.6584 | PASS | 14558.4457 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 9.8296 | PASS | 19.2812 | PASS | 19181.1846 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9277 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.2936 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 7.3322 | PASS | 14.659 | PASS | 14559.0176 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 10.1459 | PASS | 19.1449 | PASS | 19044.9054 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 12.4073 | PASS | 33.7935 | PASS | 33693.4788 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 12.4073 | PASS | 101.9757 | PASS | 101875.747 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 7.3146 | PASS | 14.6044 | PASS | 14504.3739 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 10.0077 | PASS | 19.1747 | PASS | 19074.6699 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 12.4081 | PASS | 33.7938 | PASS | 33693.8481 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 12.4081 | PASS | 101.9896 | PASS | 101889.5755 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 7.3348 | PASS | 14.6532 | PASS | 14553.2468 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 10.1578 | PASS | 19.1558 | PASS | 19055.8035 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8665 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.3551 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.7168 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 10.1557 | PASS | 19.1429 | PASS | 19042.9151 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9148 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 12.407 | PASS | 101.9782 | PASS | 101878.2015 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 7.3319 | PASS | 14.6566 | PASS | 14556.5783 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 9.9042 | PASS | 19.1839 | PASS | 19083.9313 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8652 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.3812 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 7.3325 | PASS | 14.6588 | PASS | 14558.8124 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 9.7232 | PASS | 19.2712 | PASS | 19171.1802 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8861 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.7452 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 7.3325 | PASS | 14.6585 | PASS | 14558.5356 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 9.7738 | PASS | 19.2744 | PASS | 19174.3869 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.864 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.7125 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 7.3322 | PASS | 14.6591 | PASS | 14559.1332 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 9.6333 | PASS | 19.3393 | PASS | 19239.3306 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8686 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.316 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.7278 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 9.7233 | PASS | 19.2887 | PASS | 19188.7212 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9021 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 12.407 | PASS | 101.9784 | PASS | 101878.4327 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8175 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 10.1245 | PASS | 19.1531 | PASS | 19053.0801 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.931 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 12.407 | PASS | 101.9786 | PASS | 101878.574 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 7.3308 | PASS | 14.6547 | PASS | 14554.7049 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 10.1285 | PASS | 19.1454 | PASS | 19045.4284 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8468 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 12.4069 | PASS | 101.9797 | PASS | 101879.7311 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8413 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8482 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4065 | PASS | 33.7928 | PASS | 33692.7507 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4065 | PASS | 101.9654 | PASS | 101865.3964 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8478 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8473 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8492 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4069 | PASS | 101.9779 | PASS | 101877.9054 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.852 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.847 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4069 | PASS | 33.7928 | PASS | 33692.8491 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4069 | PASS | 101.9779 | PASS | 101877.9082 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.8521 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.847 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.8565 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4068 | PASS | 101.976 | PASS | 101875.9694 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3323 | PASS | 14.6589 | PASS | 14558.8501 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8523 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4068 | PASS | 33.7929 | PASS | 33692.8565 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4068 | PASS | 101.976 | PASS | 101875.9694 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 7.3323 | PASS | 14.6589 | PASS | 14558.8501 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 10.1554 | PASS | 19.1429 | PASS | 19042.8523 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 12.4036 | PASS | 33.8106 | PASS | 33710.5954 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 12.4036 | PASS | 101.056 | PASS | 100956.0186 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 7.3324 | PASS | 14.6569 | PASS | 14556.9172 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.9286 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8546 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.341 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8466 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8475 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 12.4032 | PASS | 33.8274 | PASS | 33727.3742 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 12.4032 | PASS | 100.2351 | PASS | 100135.1179 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 7.3319 | PASS | 14.6572 | PASS | 14557.1714 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8354 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 12.4083 | PASS | 33.7946 | PASS | 33694.5776 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 12.4083 | PASS | 101.9613 | PASS | 101861.2531 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 7.3339 | PASS | 14.6568 | PASS | 14556.7847 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 10.1556 | PASS | 19.143 | PASS | 19043.0399 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 12.3982 | PASS | 33.7944 | PASS | 33694.3811 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 12.3982 | PASS | 101.4299 | PASS | 101329.8504 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 7.3309 | PASS | 14.661 | PASS | 14560.9654 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 10.1552 | PASS | 19.1425 | PASS | 19042.4758 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 12.4051 | PASS | 33.794 | PASS | 33693.9624 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 12.4051 | PASS | 101.8283 | PASS | 101728.2737 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 7.3312 | PASS | 14.6605 | PASS | 14560.4901 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 10.155 | PASS | 19.1425 | PASS | 19042.5487 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4069 | PASS | 33.7931 | PASS | 33693.0928 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4069 | PASS | 101.966 | PASS | 101866.0479 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8936 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8448 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.856 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.326 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8438 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8482 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8557 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.3316 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8501 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8482 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4072 | PASS | 33.7933 | PASS | 33693.2505 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4072 | PASS | 101.9662 | PASS | 101866.1852 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 7.3326 | PASS | 14.6586 | PASS | 14558.612 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8716 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8636 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 12.407 | PASS | 101.9799 | PASS | 101879.8588 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 7.3324 | PASS | 14.6583 | PASS | 14558.2594 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 10.1553 | PASS | 19.143 | PASS | 19043.0214 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.889 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 12.4069 | PASS | 101.9758 | PASS | 101875.7942 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 7.3316 | PASS | 14.6601 | PASS | 14560.1202 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 10.1542 | PASS | 19.1425 | PASS | 19042.5393 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9158 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 12.407 | PASS | 101.9775 | PASS | 101877.5166 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 7.3318 | PASS | 14.6599 | PASS | 14559.854 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 10.1543 | PASS | 19.1423 | PASS | 19042.325 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8687 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 12.407 | PASS | 101.9798 | PASS | 101879.7782 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 7.3323 | PASS | 14.6576 | PASS | 14557.6321 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 10.1327 | PASS | 19.1482 | PASS | 19048.2056 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 12.4067 | PASS | 33.7928 | PASS | 33692.7849 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 12.4067 | PASS | 101.9652 | PASS | 101865.2157 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 7.3322 | PASS | 14.6593 | PASS | 14559.2606 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 10.143 | PASS | 19.144 | PASS | 19043.9836 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9087 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.407 | PASS | 101.9783 | PASS | 101878.306 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 7.3328 | PASS | 14.6581 | PASS | 14558.1142 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.1537 | PASS | 19.1447 | PASS | 19044.6986 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8889 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.407 | PASS | 101.9776 | PASS | 101877.5984 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 7.3318 | PASS | 14.6598 | PASS | 14559.7697 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 10.154 | PASS | 19.1429 | PASS | 19042.8961 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9064 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.8115 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 7.3316 | PASS | 14.6577 | PASS | 14557.7448 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.1413 | PASS | 19.1448 | PASS | 19044.8212 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.9061 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.407 | PASS | 101.9788 | PASS | 101878.818 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 7.3316 | PASS | 14.6578 | PASS | 14557.7502 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 10.1414 | PASS | 19.1448 | PASS | 19044.8088 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9016 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 12.407 | PASS | 101.978 | PASS | 101878.0006 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 7.3324 | PASS | 14.658 | PASS | 14557.9697 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 10.1558 | PASS | 19.1433 | PASS | 19043.2693 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 12.4073 | PASS | 33.7937 | PASS | 33693.7389 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 12.4073 | PASS | 101.9546 | PASS | 101854.6447 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 7.3266 | PASS | 14.642 | PASS | 14542.0047 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 10.1537 | PASS | 19.1402 | PASS | 19040.1804 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.9144 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 12.4069 | PASS | 101.9753 | PASS | 101875.307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 7.3312 | PASS | 14.6607 | PASS | 14560.6798 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 10.155 | PASS | 19.1404 | PASS | 19040.3713 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 12.4069 | PASS | 33.7929 | PASS | 33692.9144 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 12.4069 | PASS | 101.9753 | PASS | 101875.307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 7.3312 | PASS | 14.6607 | PASS | 14560.6798 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 10.155 | PASS | 19.1404 | PASS | 19040.3713 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 12.4069 | PASS | 33.7929 | PASS | 33692.9144 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 12.4069 | PASS | 101.9753 | PASS | 101875.307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 7.3312 | PASS | 14.6607 | PASS | 14560.6798 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 10.155 | PASS | 19.1404 | PASS | 19040.3713 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.9216 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 12.4069 | PASS | 101.9783 | PASS | 101878.3043 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 7.3313 | PASS | 14.6568 | PASS | 14556.8254 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 10.1547 | PASS | 19.1425 | PASS | 19042.451 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8957 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 12.407 | PASS | 101.9781 | PASS | 101878.1088 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 7.3319 | PASS | 14.6594 | PASS | 14559.3835 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 10.1537 | PASS | 19.1427 | PASS | 19042.7289 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8681 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.407 | PASS | 101.9773 | PASS | 101877.282 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 7.3321 | PASS | 14.6591 | PASS | 14559.1152 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 10.1554 | PASS | 19.1427 | PASS | 19042.6946 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8636 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 12.4069 | PASS | 101.9787 | PASS | 101878.7288 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 7.3321 | PASS | 14.6582 | PASS | 14558.2472 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 10.1542 | PASS | 19.1428 | PASS | 19042.8465 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8613 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.7605 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7809 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8424 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 12.4072 | PASS | 33.7933 | PASS | 33693.343 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 12.4072 | PASS | 101.9644 | PASS | 101864.4137 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 7.331 | PASS | 14.6477 | PASS | 14547.6581 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 10.1545 | PASS | 19.1423 | PASS | 19042.3208 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8768 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 12.407 | PASS | 101.9792 | PASS | 101879.158 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 7.3324 | PASS | 14.6583 | PASS | 14558.2643 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 10.1541 | PASS | 19.1433 | PASS | 19043.3193 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 12.4072 | PASS | 33.7942 | PASS | 33694.1835 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 12.4072 | PASS | 101.9264 | PASS | 101826.4268 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 7.33 | PASS | 14.6565 | PASS | 14556.4845 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 10.1542 | PASS | 19.1411 | PASS | 19041.1048 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 12.4065 | PASS | 33.7927 | PASS | 33692.6875 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 12.4065 | PASS | 101.9774 | PASS | 101877.3814 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 7.332 | PASS | 14.6594 | PASS | 14559.3807 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 10.1553 | PASS | 19.1428 | PASS | 19042.7664 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.944 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4069 | PASS | 101.9734 | PASS | 101873.4005 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 7.3321 | PASS | 14.6577 | PASS | 14557.7233 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.1552 | PASS | 19.1429 | PASS | 19042.9136 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.4069 | PASS | 33.7929 | PASS | 33692.9436 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.4069 | PASS | 101.9734 | PASS | 101873.4014 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 7.3321 | PASS | 14.6577 | PASS | 14557.713 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 10.1552 | PASS | 19.1429 | PASS | 19042.9219 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 12.4065 | PASS | 33.7928 | PASS | 33692.77 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 12.4065 | PASS | 101.961 | PASS | 101860.9968 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 7.3302 | PASS | 14.6558 | PASS | 14555.798 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 10.1318 | PASS | 19.1506 | PASS | 19050.6257 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 12.4107 | PASS | 33.7964 | PASS | 33696.3901 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 12.4107 | PASS | 101.9902 | PASS | 101890.2069 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 7.3374 | PASS | 14.6486 | PASS | 14548.592 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 10.1547 | PASS | 19.1447 | PASS | 19044.7202 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8566 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.2982 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 7.3325 | PASS | 14.6584 | PASS | 14558.45 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 10.0431 | PASS | 19.1306 | PASS | 19030.6413 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8656 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 12.407 | PASS | 101.9794 | PASS | 101879.378 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 7.3324 | PASS | 14.6587 | PASS | 14558.7401 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 10.1012 | PASS | 19.1351 | PASS | 19035.0789 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 12.407 | PASS | 33.7929 | PASS | 33692.8656 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 12.407 | PASS | 101.9794 | PASS | 101879.378 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 7.3324 | PASS | 14.6587 | PASS | 14558.7401 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 10.1012 | PASS | 19.1351 | PASS | 19035.0789 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4094 | PASS | 33.7949 | PASS | 33694.895 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4094 | PASS | 102.0004 | PASS | 101900.3566 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 7.3376 | PASS | 14.6496 | PASS | 14549.6174 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 10.1907 | PASS | 19.3958 | PASS | 19295.821 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4072 | PASS | 33.7931 | PASS | 33693.1013 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4072 | PASS | 101.9814 | PASS | 101881.3676 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 7.3331 | PASS | 14.657 | PASS | 14557.0247 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 10.162 | PASS | 19.2431 | PASS | 19143.1303 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.8647 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 12.4068 | PASS | 101.9781 | PASS | 101878.0545 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 7.3312 | PASS | 14.6595 | PASS | 14559.4645 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 9.7992 | PASS | 19.1428 | PASS | 19042.7886 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.864 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4026 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8846 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 10.0578 | PASS | 19.1789 | PASS | 19078.8644 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8731 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4069 | PASS | 101.9783 | PASS | 101878.3328 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 7.3323 | PASS | 14.6587 | PASS | 14558.743 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 10.1066 | PASS | 19.1499 | PASS | 19049.902 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 12.408 | PASS | 33.795 | PASS | 33695.0414 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 12.408 | PASS | 101.9251 | PASS | 101825.0524 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 7.3338 | PASS | 14.6569 | PASS | 14556.8665 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 10.1556 | PASS | 19.143 | PASS | 19043.0376 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 12.4083 | PASS | 33.7952 | PASS | 33695.2284 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 12.4083 | PASS | 101.926 | PASS | 101825.9656 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 7.334 | PASS | 14.6565 | PASS | 14556.5324 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 10.1556 | PASS | 19.1431 | PASS | 19043.0686 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 12.4082 | PASS | 33.7952 | PASS | 33695.1964 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 12.4082 | PASS | 101.9273 | PASS | 101827.2704 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 7.334 | PASS | 14.6566 | PASS | 14556.5644 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 10.1556 | PASS | 19.1431 | PASS | 19043.0647 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 12.4068 | PASS | 33.7929 | PASS | 33692.9345 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 12.4068 | PASS | 101.9673 | PASS | 101867.2777 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8149 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8505 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 12.4071 | PASS | 33.7931 | PASS | 33693.1181 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 12.4071 | PASS | 101.9728 | PASS | 101872.7644 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 7.3315 | PASS | 14.6601 | PASS | 14560.1458 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 10.1536 | PASS | 19.1428 | PASS | 19042.7809 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 12.4066 | PASS | 33.7927 | PASS | 33692.7046 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 12.4066 | PASS | 101.9773 | PASS | 101877.2644 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 7.332 | PASS | 14.6593 | PASS | 14559.2735 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 10.1553 | PASS | 19.1428 | PASS | 19042.7745 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.4036 | PASS | 33.7906 | PASS | 33690.5515 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.4036 | PASS | 101.9242 | PASS | 101824.1988 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.6803 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8012 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.9097 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.4068 | PASS | 101.9669 | PASS | 101866.8689 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.808 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8592 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.4068 | PASS | 33.7929 | PASS | 33692.9097 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.4068 | PASS | 101.9669 | PASS | 101866.8679 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 7.3324 | PASS | 14.6588 | PASS | 14558.8079 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 10.1555 | PASS | 19.1429 | PASS | 19042.859 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 11.5873 | PASS | 37.5406 | PASS | 37440.6488 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 11.5873 | PASS | 52.9932 | PASS | 52893.2231 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 7.332 | PASS | 14.6593 | PASS | 14559.2694 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8147 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 11.5856 | PASS | 37.5477 | PASS | 37447.6578 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 11.5856 | PASS | 52.9653 | PASS | 52865.3227 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 7.3319 | PASS | 14.6593 | PASS | 14559.2772 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8146 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.3957 | PASS | 31.0528 | PASS | 30952.8382 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.3957 | PASS | 20.8054 | PASS | 20705.37 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.3317 | PASS | 14.6595 | PASS | 14559.5103 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.7938 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 9.0415 | PASS | 37.242 | PASS | 37142.0092 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 9.0415 | PASS | 22.0414 | PASS | 21941.3998 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 7.3323 | PASS | 14.6588 | PASS | 14558.7631 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8492 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 12.4066 | PASS | 33.7949 | PASS | 33694.9224 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 12.4066 | PASS | 101.8771 | PASS | 101777.0685 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 7.0363 | PASS | 13.6301 | PASS | 13530.0836 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 10.1537 | PASS | 19.143 | PASS | 19042.9544 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4069 | PASS | 33.7945 | PASS | 33694.5005 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4069 | PASS | 101.9028 | PASS | 101802.7596 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 6.9776 | PASS | 13.5233 | PASS | 13423.2943 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 10.1527 | PASS | 19.1429 | PASS | 19042.9385 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 12.4067 | PASS | 33.7931 | PASS | 33693.1176 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 12.4067 | PASS | 101.9618 | PASS | 101861.7752 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 7.3049 | PASS | 14.5472 | PASS | 14447.227 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 10.1547 | PASS | 19.1429 | PASS | 19042.8941 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 12.4068 | PASS | 33.7927 | PASS | 33692.7404 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 12.4068 | PASS | 101.9802 | PASS | 101880.1921 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 7.3334 | PASS | 14.683 | PASS | 14583.0315 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.9022 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4068 | PASS | 33.793 | PASS | 33692.9785 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4068 | PASS | 101.9685 | PASS | 101868.4917 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 6.953 | PASS | 13.4972 | PASS | 13397.2376 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 10.1555 | PASS | 19.1427 | PASS | 19042.6742 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8548 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 12.4069 | PASS | 101.9789 | PASS | 101878.8987 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 7.3315 | PASS | 14.6621 | PASS | 14562.0661 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 10.1554 | PASS | 19.1427 | PASS | 19042.7267 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8805 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 12.407 | PASS | 101.9791 | PASS | 101879.1068 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 7.3239 | PASS | 14.6227 | PASS | 14522.6883 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 10.1552 | PASS | 19.1429 | PASS | 19042.868 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8861 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 12.4069 | PASS | 101.9783 | PASS | 101878.3001 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 7.3299 | PASS | 14.6647 | PASS | 14564.6821 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 10.1551 | PASS | 19.1426 | PASS | 19042.5947 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8887 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 12.4069 | PASS | 101.9785 | PASS | 101878.4944 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 7.3292 | PASS | 14.667 | PASS | 14566.9896 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 10.155 | PASS | 19.1425 | PASS | 19042.5016 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.9318 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 12.4068 | PASS | 101.9743 | PASS | 101874.2705 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 7.283 | PASS | 14.3651 | PASS | 14265.1027 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 10.1541 | PASS | 19.1423 | PASS | 19042.3302 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.8215 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 12.4068 | PASS | 101.9757 | PASS | 101875.7232 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 7.304 | PASS | 14.5358 | PASS | 14435.7769 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 10.1525 | PASS | 19.1435 | PASS | 19043.4942 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 12.4078 | PASS | 33.7943 | PASS | 33694.2607 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 12.4078 | PASS | 101.9505 | PASS | 101850.4814 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 7.1392 | PASS | 13.5105 | PASS | 13410.4969 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 10.1522 | PASS | 19.1435 | PASS | 19043.5032 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 12.4077 | PASS | 33.7935 | PASS | 33693.5397 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 12.4077 | PASS | 101.9665 | PASS | 101866.507 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 7.2403 | PASS | 14.0903 | PASS | 13990.2693 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 10.1538 | PASS | 19.1432 | PASS | 19043.1834 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 12.4077 | PASS | 33.7935 | PASS | 33693.5266 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 12.4077 | PASS | 101.9665 | PASS | 101866.5018 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 7.2428 | PASS | 14.1079 | PASS | 14007.8876 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 10.1539 | PASS | 19.1432 | PASS | 19043.1625 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 12.4064 | PASS | 33.7926 | PASS | 33692.5653 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 12.4064 | PASS | 101.979 | PASS | 101879.037 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 7.3217 | PASS | 15.4893 | PASS | 15389.278 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 10.1555 | PASS | 19.143 | PASS | 19042.9857 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 10.58 | PASS | 40.4817 | PASS | 40381.7355 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 10.58 | PASS | 45.0963 | PASS | 44996.2683 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 7.3325 | PASS | 14.6584 | PASS | 14558.4092 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8654 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 9.2967 | PASS | 79.8939 | PASS | 79793.9001 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 9.2967 | PASS | 29.3946 | PASS | 29294.5579 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 7.3326 | PASS | 14.6586 | PASS | 14558.5939 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8582 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 5.4287 | FAIL | 40.0069 | PASS | 39906.8518 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 5.4287 | FAIL | 23.5238 | PASS | 23423.7918 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.333 | PASS | 14.6574 | PASS | 14557.391 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.9155 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 12.3929 | PASS | 33.786 | PASS | 33686.0358 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 12.3929 | PASS | 101.6019 | PASS | 101501.9147 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 7.3325 | PASS | 14.6571 | PASS | 14557.0757 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 10.1549 | PASS | 19.143 | PASS | 19043.011 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.3955 | PASS | 33.8323 | PASS | 33732.3039 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.3955 | PASS | 99.8247 | PASS | 99724.7174 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 7.3335 | PASS | 14.6528 | PASS | 14552.8263 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 10.1551 | PASS | 19.1434 | PASS | 19043.3787 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 12.4069 | PASS | 33.7953 | PASS | 33695.2833 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 12.4069 | PASS | 101.8379 | PASS | 101737.9479 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 7.3325 | PASS | 14.6585 | PASS | 14558.4657 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8046 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.4073 | PASS | 33.7959 | PASS | 33695.9009 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.4073 | PASS | 101.8465 | PASS | 101746.54 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 7.3309 | PASS | 14.6604 | PASS | 14560.427 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 10.1535 | PASS | 19.1423 | PASS | 19042.2607 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 12.4071 | PASS | 33.7929 | PASS | 33692.8969 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 12.4071 | PASS | 101.983 | PASS | 101883.0254 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 7.3319 | PASS | 14.659 | PASS | 14558.9662 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 10.1554 | PASS | 19.1427 | PASS | 19042.7409 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4069 | PASS | 33.7927 | PASS | 33692.732 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4069 | PASS | 101.9873 | PASS | 101887.3236 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 7.3323 | PASS | 14.658 | PASS | 14557.9533 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8379 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 12.4069 | PASS | 33.7927 | PASS | 33692.734 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 12.4069 | PASS | 101.9873 | PASS | 101887.2938 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 7.3323 | PASS | 14.658 | PASS | 14557.952 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8381 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 12.4175 | PASS | 33.8103 | PASS | 33710.2728 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 12.4175 | PASS | 101.6535 | PASS | 101553.526 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 7.3427 | PASS | 14.6417 | PASS | 14541.6776 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 10.1554 | PASS | 19.1446 | PASS | 19044.6039 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.4075 | PASS | 33.7992 | PASS | 33699.1823 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.4075 | PASS | 101.7048 | PASS | 101604.7767 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 7.327 | PASS | 14.6662 | PASS | 14566.1824 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 10.1447 | PASS | 19.1433 | PASS | 19043.2798 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 12.4069 | PASS | 33.7927 | PASS | 33692.7216 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 12.4069 | PASS | 101.9884 | PASS | 101888.4178 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 7.3323 | PASS | 14.6579 | PASS | 14557.9092 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.84 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8512 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 12.407 | PASS | 101.9803 | PASS | 101880.3033 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 7.3324 | PASS | 14.6583 | PASS | 14558.3099 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8705 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.7997 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 12.4069 | PASS | 101.9824 | PASS | 101882.4287 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 7.3324 | PASS | 14.6587 | PASS | 14558.6524 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8523 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 12.4063 | PASS | 33.793 | PASS | 33693.0473 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 12.4063 | PASS | 101.9423 | PASS | 101842.2736 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 7.3325 | PASS | 14.6585 | PASS | 14558.5488 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.881 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.7878 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 12.4069 | PASS | 101.9824 | PASS | 101882.4233 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 7.3324 | PASS | 14.6587 | PASS | 14558.6765 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8507 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.7864 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 12.4069 | PASS | 101.9824 | PASS | 101882.4394 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 7.3324 | PASS | 14.6586 | PASS | 14558.6455 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.852 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.7583 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 12.4069 | PASS | 101.9819 | PASS | 101881.8789 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.7496 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8498 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 12.4069 | PASS | 33.7928 | PASS | 33692.7604 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 12.4069 | PASS | 101.9818 | PASS | 101881.8393 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 7.3325 | PASS | 14.6588 | PASS | 14558.7518 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8498 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 12.4069 | PASS | 33.7928 | PASS | 33692.7675 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 12.4069 | PASS | 101.9813 | PASS | 101881.2549 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 7.3325 | PASS | 14.6588 | PASS | 14558.7549 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 10.1555 | PASS | 19.1428 | PASS | 19042.8497 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4049 | PASS | 33.7946 | PASS | 33694.6056 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4049 | PASS | 101.8003 | PASS | 101700.2663 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 7.3327 | PASS | 14.6576 | PASS | 14557.6478 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.9448 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.425 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.425 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.425 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 12.4093 | PASS | 33.7991 | PASS | 33699.0699 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 12.4093 | PASS | 101.8016 | PASS | 101701.6431 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 7.3347 | PASS | 14.6544 | PASS | 14554.3588 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 10.1553 | PASS | 19.1433 | PASS | 19043.3077 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 12.4086 | PASS | 33.7973 | PASS | 33697.2802 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 12.4086 | PASS | 101.8513 | PASS | 101751.3307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 7.334 | PASS | 14.6557 | PASS | 14555.714 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 10.1553 | PASS | 19.1432 | PASS | 19043.1716 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 12.4084 | PASS | 33.7971 | PASS | 33697.0956 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 12.4084 | PASS | 101.8513 | PASS | 101751.2693 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 7.3339 | PASS | 14.6559 | PASS | 14555.9303 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 10.1553 | PASS | 19.1432 | PASS | 19043.1515 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 12.4093 | PASS | 33.7991 | PASS | 33699.0699 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 12.4093 | PASS | 101.8016 | PASS | 101701.6431 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 7.3347 | PASS | 14.6544 | PASS | 14554.3588 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 10.1553 | PASS | 19.1433 | PASS | 19043.3077 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 12.4086 | PASS | 33.7973 | PASS | 33697.2802 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 12.4086 | PASS | 101.8513 | PASS | 101751.3307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 7.334 | PASS | 14.6557 | PASS | 14555.714 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 10.1553 | PASS | 19.1432 | PASS | 19043.1716 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 12.4084 | PASS | 33.7971 | PASS | 33697.0956 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 12.4084 | PASS | 101.8513 | PASS | 101751.2693 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 7.3339 | PASS | 14.6559 | PASS | 14555.9303 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 10.1553 | PASS | 19.1432 | PASS | 19043.1515 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4067 | PASS | 33.7928 | PASS | 33692.8135 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4067 | PASS | 101.9665 | PASS | 101866.4521 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 7.332 | PASS | 14.6593 | PASS | 14559.2578 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 10.155 | PASS | 19.1428 | PASS | 19042.7839 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8633 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 12.407 | PASS | 101.9792 | PASS | 101879.185 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.9062 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 10.1553 | PASS | 19.1428 | PASS | 19042.836 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.851 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 12.4069 | PASS | 101.9788 | PASS | 101878.7581 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 7.3323 | PASS | 14.6587 | PASS | 14558.7134 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.7858 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4069 | PASS | 33.7927 | PASS | 33692.7202 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4069 | PASS | 101.9884 | PASS | 101888.449 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 7.3323 | PASS | 14.6579 | PASS | 14557.9103 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8399 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9102 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 12.407 | PASS | 101.9781 | PASS | 101878.0798 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 7.3323 | PASS | 14.6591 | PASS | 14559.0554 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 10.1553 | PASS | 19.1428 | PASS | 19042.7884 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 12.4099 | PASS | 33.796 | PASS | 33695.9834 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 12.4099 | PASS | 101.9685 | PASS | 101868.5425 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 7.3358 | PASS | 14.6541 | PASS | 14554.1403 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 10.1558 | PASS | 19.1434 | PASS | 19043.355 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4058 | PASS | 33.7927 | PASS | 33692.6569 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4058 | PASS | 101.9257 | PASS | 101825.7269 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 7.3314 | PASS | 14.6594 | PASS | 14559.3763 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 10.1542 | PASS | 19.1428 | PASS | 19042.8328 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 12.407 | PASS | 33.7931 | PASS | 33693.0882 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 12.407 | PASS | 101.9697 | PASS | 101869.7482 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7711 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8665 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 12.407 | PASS | 33.7931 | PASS | 33693.0891 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 12.407 | PASS | 101.9697 | PASS | 101869.731 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7707 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8666 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.3963 | PASS | 33.7875 | PASS | 33687.487 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.3963 | PASS | 101.6948 | PASS | 101594.8413 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 7.3315 | PASS | 14.6588 | PASS | 14558.807 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 10.1549 | PASS | 19.1423 | PASS | 19042.3107 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.7979 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4068 | PASS | 101.9777 | PASS | 101877.7387 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 7.233 | PASS | 14.3679 | PASS | 14267.9398 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 10.1548 | PASS | 19.1428 | PASS | 19042.8066 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.8183 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 12.4068 | PASS | 101.9774 | PASS | 101877.3501 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 7.2334 | PASS | 14.3076 | PASS | 14207.5681 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 10.1548 | PASS | 19.1428 | PASS | 19042.7763 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 12.4067 | PASS | 33.7927 | PASS | 33692.7063 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 12.4067 | PASS | 101.9797 | PASS | 101879.733 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 7.3337 | PASS | 14.7449 | PASS | 14644.9345 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 10.1556 | PASS | 19.143 | PASS | 19042.9701 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 12.4088 | PASS | 33.7944 | PASS | 33694.447 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 12.4088 | PASS | 101.995 | PASS | 101894.9873 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 7.3377 | PASS | 14.6478 | PASS | 14547.7578 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 10.166 | PASS | 19.1814 | PASS | 19081.3765 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 12.4083 | PASS | 33.794 | PASS | 33694.0224 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 12.4083 | PASS | 101.9925 | PASS | 101892.5408 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 7.335 | PASS | 14.6548 | PASS | 14554.8392 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 10.1588 | PASS | 19.146 | PASS | 19046.026 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9162 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 12.407 | PASS | 101.9782 | PASS | 101878.174 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 7.3319 | PASS | 14.6565 | PASS | 14556.5157 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 9.9245 | PASS | 19.2212 | PASS | 19121.1535 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8356 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 12.4069 | PASS | 101.9795 | PASS | 101879.5077 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.9018 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 10.1553 | PASS | 19.1427 | PASS | 19042.6983 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8615 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.7656 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8515 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.921 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 12.4064 | PASS | 33.7927 | PASS | 33692.6568 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 12.4064 | PASS | 101.9762 | PASS | 101876.178 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 7.3318 | PASS | 14.6596 | PASS | 14559.6252 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 10.1539 | PASS | 19.1398 | PASS | 19039.799 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8618 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.446 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8086 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 10.1556 | PASS | 19.143 | PASS | 19043.021 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.857 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 12.4069 | PASS | 101.9778 | PASS | 101877.7595 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 7.3315 | PASS | 14.6592 | PASS | 14559.1761 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 9.8938 | PASS | 19.2031 | PASS | 19103.1468 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4255 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8513 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8434 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8765 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 12.4069 | PASS | 101.9733 | PASS | 101873.3237 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 7.3313 | PASS | 14.6569 | PASS | 14556.8505 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 10.1137 | PASS | 19.1477 | PASS | 19047.7 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 12.4099 | PASS | 33.7953 | PASS | 33695.314 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 12.4099 | PASS | 102.0038 | PASS | 101903.7998 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 7.3378 | PASS | 14.651 | PASS | 14551.0131 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 10.1588 | PASS | 19.1478 | PASS | 19047.7942 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.872 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 12.4068 | PASS | 101.9734 | PASS | 101873.4099 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 7.3312 | PASS | 14.6569 | PASS | 14556.8796 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 10.1129 | PASS | 19.1476 | PASS | 19047.6028 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.425 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8876 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 12.4069 | PASS | 101.9794 | PASS | 101879.4 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 7.332 | PASS | 14.6589 | PASS | 14558.9441 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 10.1353 | PASS | 19.1555 | PASS | 19055.473 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 12.406 | PASS | 33.7925 | PASS | 33692.5106 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 12.406 | PASS | 101.9736 | PASS | 101873.5727 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 7.3313 | PASS | 14.6603 | PASS | 14560.2966 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 10.1528 | PASS | 19.1372 | PASS | 19037.2309 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8623 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4357 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 7.3326 | PASS | 14.6587 | PASS | 14558.6996 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 10.1558 | PASS | 19.1431 | PASS | 19043.0712 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8621 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.407 | PASS | 101.9794 | PASS | 101879.4408 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 7.3326 | PASS | 14.6587 | PASS | 14558.6864 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 10.1558 | PASS | 19.1431 | PASS | 19043.0669 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4071 | PASS | 33.7929 | PASS | 33692.9498 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4071 | PASS | 101.9793 | PASS | 101879.3203 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.332 | PASS | 14.6581 | PASS | 14558.1252 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 10.1316 | PASS | 19.1468 | PASS | 19046.7846 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8748 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 12.407 | PASS | 101.9799 | PASS | 101879.853 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 7.3325 | PASS | 14.6583 | PASS | 14558.2746 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 10.1286 | PASS | 19.1451 | PASS | 19045.0678 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8996 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 12.407 | PASS | 101.981 | PASS | 101880.9812 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 7.3328 | PASS | 14.6573 | PASS | 14557.31 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 10.1009 | PASS | 19.1567 | PASS | 19056.6957 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4068 | PASS | 33.793 | PASS | 33692.9804 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4068 | PASS | 101.9671 | PASS | 101867.0914 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 7.3285 | PASS | 14.651 | PASS | 14551.0266 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 10.0255 | PASS | 19.1683 | PASS | 19068.298 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 12.4067 | PASS | 33.7927 | PASS | 33692.6788 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 12.4067 | PASS | 101.976 | PASS | 101875.9698 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 7.3319 | PASS | 14.6597 | PASS | 14559.695 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 10.1547 | PASS | 19.1385 | PASS | 19038.4847 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4259 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7568 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 10.1555 | PASS | 19.143 | PASS | 19043.0405 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8631 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4189 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8509 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 10.1557 | PASS | 19.143 | PASS | 19043.0458 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.8107 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 12.4068 | PASS | 101.9786 | PASS | 101878.6367 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14558.9732 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 10.154 | PASS | 19.141 | PASS | 19041.0359 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.8132 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 12.4068 | PASS | 101.9786 | PASS | 101878.5887 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14558.9785 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 10.154 | PASS | 19.1408 | PASS | 19040.8032 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 12.4067 | PASS | 33.7926 | PASS | 33692.634 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 12.4067 | PASS | 101.9762 | PASS | 101876.1589 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 7.3319 | PASS | 14.6595 | PASS | 14559.5487 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 10.1454 | PASS | 19.1311 | PASS | 19031.1284 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9063 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.811 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.3324 | PASS | 14.657 | PASS | 14557.0382 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.0865 | PASS | 20.2748 | PASS | 20174.7782 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8608 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 12.4069 | PASS | 101.979 | PASS | 101879.0159 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8718 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 10.1552 | PASS | 19.1427 | PASS | 19042.6711 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8939 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 12.407 | PASS | 101.9786 | PASS | 101878.5994 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 7.332 | PASS | 14.6566 | PASS | 14556.5917 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 9.9066 | PASS | 19.2078 | PASS | 19107.8323 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8802 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 12.4069 | PASS | 101.9791 | PASS | 101879.0793 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 7.3323 | PASS | 14.6586 | PASS | 14558.6183 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 10.1426 | PASS | 19.1366 | PASS | 19036.5743 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9108 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.7276 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.3322 | PASS | 14.659 | PASS | 14558.9756 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 10.1474 | PASS | 19.1435 | PASS | 19043.4713 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4071 | PASS | 33.793 | PASS | 33692.9556 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4071 | PASS | 101.9792 | PASS | 101879.208 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.3319 | PASS | 14.6578 | PASS | 14557.8253 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 10.1278 | PASS | 19.1469 | PASS | 19046.9204 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.8094 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 12.4068 | PASS | 101.9784 | PASS | 101878.4158 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14559.0129 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 10.1552 | PASS | 19.1423 | PASS | 19042.301 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9087 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 12.407 | PASS | 101.9785 | PASS | 101878.5492 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8056 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 10.1243 | PASS | 19.1532 | PASS | 19053.2003 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 12.4084 | PASS | 33.7934 | PASS | 33693.4334 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 12.4084 | PASS | 101.9867 | PASS | 101886.7211 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 7.3341 | PASS | 14.6566 | PASS | 14556.6219 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 10.1585 | PASS | 19.1468 | PASS | 19046.7554 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4068 | PASS | 33.793 | PASS | 33692.9665 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4068 | PASS | 101.9671 | PASS | 101867.1123 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 7.3286 | PASS | 14.6509 | PASS | 14550.9094 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 10.025 | PASS | 19.1687 | PASS | 19068.7397 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8629 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.425 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8466 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 12.4069 | PASS | 101.9797 | PASS | 101879.7353 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8414 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8482 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.8441 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 12.4068 | PASS | 101.9795 | PASS | 101879.532 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8256 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8517 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 12.4065 | PASS | 33.7925 | PASS | 33692.5085 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 12.4065 | PASS | 101.9819 | PASS | 101881.9127 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 7.3321 | PASS | 14.6593 | PASS | 14559.2772 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8094 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8452 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 12.4069 | PASS | 101.9795 | PASS | 101879.5228 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8495 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8477 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 12.4069 | PASS | 33.7928 | PASS | 33692.8455 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 12.4069 | PASS | 101.9795 | PASS | 101879.5172 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 7.3324 | PASS | 14.6588 | PASS | 14558.8433 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8476 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4066 | PASS | 33.7927 | PASS | 33692.6707 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4066 | PASS | 101.9694 | PASS | 101869.4124 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8619 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8457 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 12.4071 | PASS | 33.7931 | PASS | 33693.1357 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 12.4071 | PASS | 101.9697 | PASS | 101869.7289 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 7.3325 | PASS | 14.6587 | PASS | 14558.6832 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 12.4059 | PASS | 33.7937 | PASS | 33693.6951 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 12.4059 | PASS | 101.8809 | PASS | 101780.8867 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 7.3322 | PASS | 14.6591 | PASS | 14559.1206 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.806 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4067 | PASS | 33.7928 | PASS | 33692.7707 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4067 | PASS | 101.9747 | PASS | 101874.6711 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8657 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 12.407 | PASS | 33.7929 | PASS | 33692.8675 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 12.407 | PASS | 101.9786 | PASS | 101878.6456 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 7.3324 | PASS | 14.6589 | PASS | 14558.8535 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 10.1555 | PASS | 19.1428 | PASS | 19042.8481 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 12.407 | PASS | 33.7929 | PASS | 33692.8804 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 12.407 | PASS | 101.9779 | PASS | 101877.9489 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 7.3324 | PASS | 14.6589 | PASS | 14558.8534 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 10.1555 | PASS | 19.1428 | PASS | 19042.8478 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.9282 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 12.4069 | PASS | 101.9755 | PASS | 101875.4828 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8453 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8491 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 12.4069 | PASS | 33.7929 | PASS | 33692.9283 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 12.4069 | PASS | 101.9755 | PASS | 101875.481 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 7.3324 | PASS | 14.6588 | PASS | 14558.8452 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8491 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 12.4069 | PASS | 33.793 | PASS | 33692.9637 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 12.4069 | PASS | 101.973 | PASS | 101873.0167 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7945 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8526 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8576 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 12.4069 | PASS | 101.9791 | PASS | 101879.0884 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8495 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8492 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 12.4069 | PASS | 33.7929 | PASS | 33692.8574 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 12.4069 | PASS | 101.9791 | PASS | 101879.0935 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 7.3324 | PASS | 14.6588 | PASS | 14558.8497 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8492 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 12.4069 | PASS | 33.7929 | PASS | 33692.8563 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 12.4069 | PASS | 101.9791 | PASS | 101879.1131 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 7.3324 | PASS | 14.6588 | PASS | 14558.8431 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 10.1555 | PASS | 19.1428 | PASS | 19042.8475 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 12.4028 | PASS | 33.806 | PASS | 33705.9779 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 12.4028 | PASS | 101.2377 | PASS | 101137.6641 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 7.3323 | PASS | 14.6575 | PASS | 14557.4886 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.9407 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 12.4062 | PASS | 33.7947 | PASS | 33694.6503 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 12.4062 | PASS | 101.8815 | PASS | 101781.5006 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 7.332 | PASS | 14.6589 | PASS | 14558.9267 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8194 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.407 | PASS | 33.7928 | PASS | 33692.8495 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4381 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8567 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8468 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 12.407 | PASS | 33.7928 | PASS | 33692.8495 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 12.407 | PASS | 101.9794 | PASS | 101879.4381 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.8567 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8468 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 12.4101 | PASS | 33.8007 | PASS | 33700.7345 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 12.4101 | PASS | 101.7392 | PASS | 101639.2414 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 7.3372 | PASS | 14.6518 | PASS | 14551.8087 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 10.1557 | PASS | 19.1435 | PASS | 19043.5074 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 12.4066 | PASS | 33.7937 | PASS | 33693.7317 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 12.4066 | PASS | 101.9191 | PASS | 101819.1364 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 7.3322 | PASS | 14.6591 | PASS | 14559.0682 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8159 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 12.4067 | PASS | 33.7939 | PASS | 33693.9183 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 12.4067 | PASS | 101.9183 | PASS | 101818.2812 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 7.3324 | PASS | 14.6587 | PASS | 14558.7418 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8498 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8554 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 12.4069 | PASS | 101.978 | PASS | 101877.9938 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7857 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8645 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8399 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 12.4069 | PASS | 101.9787 | PASS | 101878.7435 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8699 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8449 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 12.4069 | PASS | 33.7928 | PASS | 33692.8399 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 12.4069 | PASS | 101.9787 | PASS | 101878.7435 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.8699 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8449 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 12.4069 | PASS | 33.7935 | PASS | 33693.5118 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 12.4069 | PASS | 101.9439 | PASS | 101843.9356 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 7.3323 | PASS | 14.6589 | PASS | 14558.8994 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8243 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.407 | PASS | 33.7935 | PASS | 33693.4544 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.407 | PASS | 101.9511 | PASS | 101851.0625 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 7.3317 | PASS | 14.6598 | PASS | 14559.7664 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 10.1542 | PASS | 19.1426 | PASS | 19042.6357 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 12.407 | PASS | 33.7935 | PASS | 33693.5004 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 12.407 | PASS | 101.9493 | PASS | 101849.2983 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 7.3317 | PASS | 14.6598 | PASS | 14559.8317 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 10.1542 | PASS | 19.1426 | PASS | 19042.6017 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 12.4071 | PASS | 33.793 | PASS | 33692.9963 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 12.4071 | PASS | 101.9796 | PASS | 101879.5718 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14559.0133 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 10.1545 | PASS | 19.1428 | PASS | 19042.8429 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 12.4065 | PASS | 33.7915 | PASS | 33691.4992 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 12.4065 | PASS | 102.0295 | PASS | 101929.5421 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 7.3322 | PASS | 14.6592 | PASS | 14559.2218 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.827 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 12.4068 | PASS | 33.7933 | PASS | 33693.3286 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 12.4068 | PASS | 101.9542 | PASS | 101854.1556 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.7924 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8491 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 12.4067 | PASS | 33.7921 | PASS | 33692.1001 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 12.4067 | PASS | 102.0077 | PASS | 101907.7306 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14559.0431 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8381 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 12.4065 | PASS | 33.7945 | PASS | 33694.4831 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 12.4065 | PASS | 101.8954 | PASS | 101795.3997 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 7.3322 | PASS | 14.6588 | PASS | 14558.8393 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8311 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4023 | PASS | 33.824 | PASS | 33724.0056 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4023 | PASS | 100.3999 | PASS | 100299.8523 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.332 | PASS | 14.6559 | PASS | 14555.9305 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 10.1553 | PASS | 19.1429 | PASS | 19042.9175 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8471 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 12.4069 | PASS | 101.9797 | PASS | 101879.7283 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.841 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8484 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8663 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4069 | PASS | 101.978 | PASS | 101878.0226 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8522 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8465 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.4013 | PASS | 33.7921 | PASS | 33692.0506 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.4013 | PASS | 101.715 | PASS | 101615.0297 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 7.3315 | PASS | 14.6601 | PASS | 14560.0523 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 10.1553 | PASS | 19.1426 | PASS | 19042.6424 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 12.4069 | PASS | 33.7934 | PASS | 33693.4083 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 12.4069 | PASS | 101.9504 | PASS | 101850.3928 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8384 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8478 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 12.4072 | PASS | 33.7933 | PASS | 33693.2505 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 12.4072 | PASS | 101.9662 | PASS | 101866.1852 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 7.3326 | PASS | 14.6586 | PASS | 14558.612 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8716 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 12.4101 | PASS | 33.7988 | PASS | 33698.7959 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 12.4101 | PASS | 101.8369 | PASS | 101736.938 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 7.3368 | PASS | 14.6525 | PASS | 14552.5276 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 10.1557 | PASS | 19.1434 | PASS | 19043.4456 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 12.409 | PASS | 33.7967 | PASS | 33696.7334 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 12.409 | PASS | 101.889 | PASS | 101788.9849 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 7.3352 | PASS | 14.6549 | PASS | 14554.865 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 10.1556 | PASS | 19.1432 | PASS | 19043.2318 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4075 | PASS | 33.793 | PASS | 33693.0097 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4075 | PASS | 101.9998 | PASS | 101899.7571 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 7.3326 | PASS | 14.6576 | PASS | 14557.5524 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 10.1548 | PASS | 19.1432 | PASS | 19043.2022 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 12.4031 | PASS | 33.8271 | PASS | 33727.0953 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 12.4031 | PASS | 100.2477 | PASS | 100147.7264 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 7.3319 | PASS | 14.6572 | PASS | 14557.1795 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8373 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4069 | PASS | 33.7933 | PASS | 33693.258 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4069 | PASS | 101.9569 | PASS | 101856.8635 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.3323 | PASS | 14.6589 | PASS | 14558.9242 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8388 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8916 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4069 | PASS | 101.975 | PASS | 101875.0498 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3314 | PASS | 14.6598 | PASS | 14559.7999 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.1551 | PASS | 19.1428 | PASS | 19042.8234 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8651 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.407 | PASS | 101.9798 | PASS | 101879.83 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 7.3324 | PASS | 14.6583 | PASS | 14558.2681 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 10.1552 | PASS | 19.143 | PASS | 19042.9986 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8774 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.6972 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 7.3322 | PASS | 14.6586 | PASS | 14558.5698 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.8212 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8792 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 12.4069 | PASS | 101.9791 | PASS | 101879.0747 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 7.3319 | PASS | 14.6591 | PASS | 14559.1329 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 10.1545 | PASS | 19.1424 | PASS | 19042.4351 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8666 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.6594 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 7.3324 | PASS | 14.6586 | PASS | 14558.5671 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8973 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 12.4073 | PASS | 33.7929 | PASS | 33692.9446 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 12.4073 | PASS | 101.9911 | PASS | 101891.1168 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 7.3329 | PASS | 14.6493 | PASS | 14549.2552 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 10.1162 | PASS | 19.158 | PASS | 19057.9603 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 12.4071 | PASS | 33.7929 | PASS | 33692.8908 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 12.4071 | PASS | 101.98 | PASS | 101880.0029 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 7.3327 | PASS | 14.6581 | PASS | 14558.087 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 10.1558 | PASS | 19.1437 | PASS | 19043.6693 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 12.4071 | PASS | 33.7929 | PASS | 33692.8908 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 12.4071 | PASS | 101.9807 | PASS | 101880.6964 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 7.3327 | PASS | 14.6581 | PASS | 14558.0955 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 10.1558 | PASS | 19.1436 | PASS | 19043.6408 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 514885 [NORTWS41 13.800] CKT 4 | 12.407 | PASS | 33.7929 | PASS | 33692.8886 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 514885 [NORTWS41 13.800] CKT 4 | 12.407 | PASS | 101.9796 | PASS | 101879.6027 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 514885 [NORTWS41 13.800] CKT 4 | 7.3323 | PASS | 14.6587 | PASS | 14558.723 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 514885 [NORTWS41 13.800] CKT 4 | 10.1552 | PASS | 19.1423 | PASS | 19042.2965 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8823 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 101.9775 | PASS | 101877.4758 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3317 | PASS | 14.6599 | PASS | 14559.8776 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.154 | PASS | 19.1428 | PASS | 19042.8099 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8959 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 12.4069 | PASS | 101.9766 | PASS | 101876.5598 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 7.331 | PASS | 14.658 | PASS | 14558.0357 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 9.9702 | PASS | 19.1828 | PASS | 19082.7849 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 12.4093 | PASS | 33.7952 | PASS | 33695.2035 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 12.4093 | PASS | 101.979 | PASS | 101878.9543 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 7.3365 | PASS | 14.6466 | PASS | 14546.6235 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 10.1574 | PASS | 19.1559 | PASS | 19055.9092 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 12.4072 | PASS | 33.7935 | PASS | 33693.4787 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 12.4072 | PASS | 101.9605 | PASS | 101860.4757 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 7.3284 | PASS | 14.6439 | PASS | 14543.9023 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 10.1528 | PASS | 19.142 | PASS | 19042.0478 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515714 [CIMARO11 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.89 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515714 [CIMARO11 13.800] CKT 1 | 12.407 | PASS | 101.9807 | PASS | 101880.7164 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515714 [CIMARO11 13.800] CKT 1 | 7.3329 | PASS | 14.6574 | PASS | 14557.3686 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515714 [CIMARO11 13.800] CKT 1 | 10.1521 | PASS | 19.15 | PASS | 19049.9878 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515715 [CIMARO21 13.800] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.9057 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515715 [CIMARO21 13.800] CKT 2 | 12.407 | PASS | 101.9806 | PASS | 101880.6085 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515715 [CIMARO21 13.800] CKT 2 | 7.3319 | PASS | 14.6591 | PASS | 14559.1315 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515715 [CIMARO21 13.800] CKT 2 | 10.1483 | PASS | 19.1385 | PASS | 19038.5245 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8533 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.3597 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3319 | PASS | 14.6585 | PASS | 14558.5488 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.1554 | PASS | 19.1432 | PASS | 19043.2141 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8466 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 12.4069 | PASS | 101.9764 | PASS | 101876.3532 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 7.3322 | PASS | 14.659 | PASS | 14558.9935 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 10.1551 | PASS | 19.1422 | PASS | 19042.2201 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8746 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 12.407 | PASS | 101.9792 | PASS | 101879.1953 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14558.9573 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 10.1543 | PASS | 19.1425 | PASS | 19042.5261 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8556 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.407 | PASS | 101.9798 | PASS | 101879.7684 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 7.3324 | PASS | 14.6582 | PASS | 14558.2268 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 10.1553 | PASS | 19.143 | PASS | 19042.9939 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515703 [ARCADI21 13.800] CKT 2 | 12.4069 | PASS | 33.7929 | PASS | 33692.8605 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515703 [ARCADI21 13.800] CKT 2 | 12.4069 | PASS | 101.979 | PASS | 101879.0394 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515703 [ARCADI21 13.800] CKT 2 | 7.3324 | PASS | 14.6588 | PASS | 14558.794 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515703 [ARCADI21 13.800] CKT 2 | 10.1553 | PASS | 19.1428 | PASS | 19042.7522 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515704 [ARCADI31 13.800] CKT 3 | 12.4069 | PASS | 33.7928 | PASS | 33692.8379 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515704 [ARCADI31 13.800] CKT 3 | 12.4069 | PASS | 101.9797 | PASS | 101879.6556 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515704 [ARCADI31 13.800] CKT 3 | 7.3326 | PASS | 14.6582 | PASS | 14558.2066 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515704 [ARCADI31 13.800] CKT 3 | 10.1553 | PASS | 19.1433 | PASS | 19043.2833 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515700 [ARCADI41 13.800] CKT 4 | 12.4069 | PASS | 33.7928 | PASS | 33692.8348 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515700 [ARCADI41 13.800] CKT 4 | 12.4069 | PASS | 101.9797 | PASS | 101879.7077 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515700 [ARCADI41 13.800] CKT 4 | 7.3326 | PASS | 14.6581 | PASS | 14558.1188 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] TO BUS 515700 [ARCADI41 13.800] CKT 4 | 10.1552 | PASS | 19.1433 | PASS | 19043.2847 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8586 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.822 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 7.3323 | PASS | 14.6586 | PASS | 14558.5744 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 10.1549 | PASS | 19.1429 | PASS | 19042.8933 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8574 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 12.407 | PASS | 101.9795 | PASS | 101879.5304 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 7.3323 | PASS | 14.6585 | PASS | 14558.545 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 10.1549 | PASS | 19.1429 | PASS | 19042.9008 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 12.407 | PASS | 33.7929 | PASS | 33692.8691 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 12.407 | PASS | 101.9789 | PASS | 101878.868 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 7.3323 | PASS | 14.6586 | PASS | 14558.5575 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 10.1548 | PASS | 19.1429 | PASS | 19042.8572 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514985 [TXSTELA2 69.000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8807 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514985 [TXSTELA2 69.000] CKT 1 | 12.4069 | PASS | 101.9791 | PASS | 101879.0915 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514985 [TXSTELA2 69.000] CKT 1 | 7.3311 | PASS | 14.657 | PASS | 14557.0202 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514985 [TXSTELA2 69.000] CKT 1 | 10.1547 | PASS | 19.1425 | PASS | 19042.5275 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 515504 [MCLOUDT2 69.000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.9076 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 515504 [MCLOUDT2 69.000] CKT 1 | 12.4069 | PASS | 101.9781 | PASS | 101878.1099 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 515504 [MCLOUDT2 69.000] CKT 1 | 7.3322 | PASS | 14.6585 | PASS | 14558.4986 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 515504 [MCLOUDT2 69.000] CKT 1 | 10.1552 | PASS | 19.1427 | PASS | 19042.6963 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514937 [HSLWEST2 69.000] TO BUS 514941 [HSL 4 138.00] TO BUS 515731 [HSL 1 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.9247 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514937 [HSLWEST2 69.000] TO BUS 514941 [HSL 4 138.00] TO BUS 515731 [HSL 1 13.800] CKT 1 | 12.4069 | PASS | 101.9783 | PASS | 101878.2561 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514937 [HSLWEST2 69.000] TO BUS 514941 [HSL 4 138.00] TO BUS 515731 [HSL 1 13.800] CKT 1 | 7.3312 | PASS | 14.6569 | PASS | 14556.9453 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514937 [HSLWEST2 69.000] TO BUS 514941 [HSL 4 138.00] TO BUS 515731 [HSL 1 13.800] CKT 1 | 10.1546 | PASS | 19.1424 | PASS | 19042.3887 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8632 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4069 | PASS | 101.9787 | PASS | 101878.7125 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3322 | PASS | 14.659 | PASS | 14558.9686 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.1551 | PASS | 19.1428 | PASS | 19042.8229 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 2 | 12.4069 | PASS | 33.7929 | PASS | 33692.8766 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 2 | 12.4069 | PASS | 101.9791 | PASS | 101879.1366 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 2 | 7.3321 | PASS | 14.659 | PASS | 14559.0338 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 2 | 10.1548 | PASS | 19.1427 | PASS | 19042.7032 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514971 [GRNPAST4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9214 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514971 [GRNPAST4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 101.9774 | PASS | 101877.4104 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514971 [GRNPAST4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3317 | PASS | 14.66 | PASS | 14559.991 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514971 [GRNPAST4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.1543 | PASS | 19.1422 | PASS | 19042.1847 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514963 [TROSPER4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8789 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514963 [TROSPER4 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.666 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514963 [TROSPER4 138.00] CKT 1 | 7.332 | PASS | 14.6591 | PASS | 14559.1415 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514963 [TROSPER4 138.00] CKT 1 | 10.1533 | PASS | 19.1428 | PASS | 19042.8014 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8627 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.7372 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 7.3323 | PASS | 14.6586 | PASS | 14558.6248 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 10.1554 | PASS | 19.1429 | PASS | 19042.8622 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 515156 [WASHPRK4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8684 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 515156 [WASHPRK4 138.00] CKT 1 | 12.4069 | PASS | 101.9789 | PASS | 101878.863 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 515156 [WASHPRK4 138.00] CKT 1 | 7.3322 | PASS | 14.6589 | PASS | 14558.93 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 515156 [WASHPRK4 138.00] CKT 1 | 10.1552 | PASS | 19.1427 | PASS | 19042.6987 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514972 [RENO 2 69.000] TO BUS 515753 [RENO 1 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8705 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514972 [RENO 2 69.000] TO BUS 515753 [RENO 1 13.800] CKT 1 | 12.4069 | PASS | 101.9792 | PASS | 101879.2415 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514972 [RENO 2 69.000] TO BUS 515753 [RENO 1 13.800] CKT 1 | 7.3319 | PASS | 14.6592 | PASS | 14559.21 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514973 [RENO 4 138.00] TO BUS 514972 [RENO 2 69.000] TO BUS 515753 [RENO 1 13.800] CKT 1 | 10.1548 | PASS | 19.1424 | PASS | 19042.4458 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 515959 [TINKER74 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8638 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 515959 [TINKER74 138.00] CKT 1 | 12.4069 | PASS | 101.9787 | PASS | 101878.713 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 515959 [TINKER74 138.00] CKT 1 | 7.3323 | PASS | 14.6588 | PASS | 14558.8315 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 515959 [TINKER74 138.00] CKT 1 | 10.155 | PASS | 19.1427 | PASS | 19042.7457 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4072 | PASS | 33.7934 | PASS | 33693.3579 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4072 | PASS | 101.9648 | PASS | 101864.8088 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3308 | PASS | 14.6476 | PASS | 14547.6186 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.1544 | PASS | 19.1422 | PASS | 19042.1887 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8916 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.407 | PASS | 101.9786 | PASS | 101878.6279 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3319 | PASS | 14.659 | PASS | 14558.9555 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.1534 | PASS | 19.1429 | PASS | 19042.9147 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514933 [DRAPER 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8606 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514933 [DRAPER 4 138.00] CKT 1 | 12.407 | PASS | 101.981 | PASS | 101881.035 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514933 [DRAPER 4 138.00] CKT 1 | 7.3332 | PASS | 14.6553 | PASS | 14555.2657 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514933 [DRAPER 4 138.00] CKT 1 | 10.1495 | PASS | 19.1452 | PASS | 19045.2041 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514994 [TINKER54 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8684 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514994 [TINKER54 138.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.3178 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514994 [TINKER54 138.00] CKT 1 | 7.3325 | PASS | 14.6586 | PASS | 14558.5579 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514994 [TINKER54 138.00] CKT 1 | 10.1553 | PASS | 19.1431 | PASS | 19043.1151 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 510907 [PITTSB-7 345.00] CKT 1 | 12.4065 | PASS | 33.795 | PASS | 33695.0405 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 510907 [PITTSB-7 345.00] CKT 1 | 12.4065 | PASS | 101.8632 | PASS | 101763.1652 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 510907 [PITTSB-7 345.00] CKT 1 | 7.3186 | PASS | 14.6544 | PASS | 14554.3646 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 510907 [PITTSB-7 345.00] CKT 1 | 10.1547 | PASS | 19.1411 | PASS | 19041.0976 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 | 12.4068 | PASS | 33.7932 | PASS | 33693.181 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 | 12.4068 | PASS | 101.9592 | PASS | 101859.2287 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 | 7.3308 | PASS | 14.6583 | PASS | 14558.2567 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 | 10.1412 | PASS | 19.1446 | PASS | 19044.5748 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 12.4068 | PASS | 33.7932 | PASS | 33693.181 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 12.4068 | PASS | 101.9592 | PASS | 101859.2287 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 7.3308 | PASS | 14.6583 | PASS | 14558.2567 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 10.1412 | PASS | 19.1446 | PASS | 19044.5748 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 3 | 12.4069 | PASS | 33.793 | PASS | 33693.0278 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 3 | 12.4069 | PASS | 101.9655 | PASS | 101865.5115 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 3 | 7.33 | PASS | 14.6613 | PASS | 14561.3161 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 3 | 10.1471 | PASS | 19.1417 | PASS | 19041.7382 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515041 [SEMINL2G 17.100] CKT 1 | 12.412 | PASS | 33.7991 | PASS | 33699.0821 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515041 [SEMINL2G 17.100] CKT 1 | 12.412 | PASS | 101.933 | PASS | 101832.9519 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515041 [SEMINL2G 17.100] CKT 1 | 7.3358 | PASS | 14.6151 | PASS | 14515.1158 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515041 [SEMINL2G 17.100] CKT 1 | 10.1369 | PASS | 19.1511 | PASS | 19051.0627 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515042 [SEMINL3G 20.900] CKT 1 | 12.4116 | PASS | 33.7993 | PASS | 33699.3312 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515042 [SEMINL3G 20.900] CKT 1 | 12.4116 | PASS | 101.9051 | PASS | 101805.0958 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515042 [SEMINL3G 20.900] CKT 1 | 7.334 | PASS | 14.6069 | PASS | 14506.8885 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515042 [SEMINL3G 20.900] CKT 1 | 10.1314 | PASS | 19.1529 | PASS | 19052.9165 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 12.4054 | PASS | 33.8153 | PASS | 33715.2964 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 12.4054 | PASS | 100.912 | PASS | 100812.0354 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 7.3243 | PASS | 14.6654 | PASS | 14565.4429 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 10.1438 | PASS | 19.144 | PASS | 19043.9924 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515756 [SEMINO11 14.400] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8751 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515756 [SEMINO11 14.400] CKT 1 | 12.4069 | PASS | 101.9796 | PASS | 101879.6264 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515756 [SEMINO11 14.400] CKT 1 | 7.326 | PASS | 14.6389 | PASS | 14538.8907 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515756 [SEMINO11 14.400] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.7636 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515757 [SEMINO21 14.400] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8581 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515757 [SEMINO21 14.400] CKT 2 | 12.407 | PASS | 101.9797 | PASS | 101879.734 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515757 [SEMINO21 14.400] CKT 2 | 7.3265 | PASS | 14.6381 | PASS | 14538.1358 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 515757 [SEMINO21 14.400] CKT 2 | 10.1554 | PASS | 19.1428 | PASS | 19042.8044 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 516211 [SEMINO31 14.400] CKT 3 | 12.4069 | PASS | 33.7929 | PASS | 33692.8751 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 516211 [SEMINO31 14.400] CKT 3 | 12.4069 | PASS | 101.9796 | PASS | 101879.6219 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 516211 [SEMINO31 14.400] CKT 3 | 7.326 | PASS | 14.6389 | PASS | 14538.8907 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515044 [SEMINOL4 138.00] TO BUS 516211 [SEMINO31 14.400] CKT 3 | 10.1554 | PASS | 19.1428 | PASS | 19042.7634 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4072 | PASS | 33.7942 | PASS | 33694.2365 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4072 | PASS | 101.925 | PASS | 101824.955 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3298 | PASS | 14.6566 | PASS | 14556.6275 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.154 | PASS | 19.1409 | PASS | 19040.8746 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515060 [INGLEWD4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9351 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515060 [INGLEWD4 138.00] CKT 1 | 12.407 | PASS | 101.9772 | PASS | 101877.1565 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515060 [INGLEWD4 138.00] CKT 1 | 7.3318 | PASS | 14.6608 | PASS | 14560.7552 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515060 [INGLEWD4 138.00] CKT 1 | 10.1551 | PASS | 19.1425 | PASS | 19042.5483 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515286 [STRLGTP4 138.00] CKT 1 | 12.407 | PASS | 33.793 | PASS | 33693.0181 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515286 [STRLGTP4 138.00] CKT 1 | 12.407 | PASS | 101.9765 | PASS | 101876.4588 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515286 [STRLGTP4 138.00] CKT 1 | 7.3325 | PASS | 14.6483 | PASS | 14548.2678 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515059 [SQUIRCK4 138.00] TO BUS 515286 [STRLGTP4 138.00] CKT 1 | 10.155 | PASS | 19.1439 | PASS | 19043.8712 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.4067 | PASS | 33.793 | PASS | 33693.0443 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.4067 | PASS | 101.9702 | PASS | 101870.1765 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 7.3326 | PASS | 14.6586 | PASS | 14558.6445 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8536 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 12.4064 | PASS | 33.7992 | PASS | 33699.2278 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 12.4064 | PASS | 101.6524 | PASS | 101552.4352 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 7.3317 | PASS | 14.6594 | PASS | 14559.4443 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 10.1552 | PASS | 19.1427 | PASS | 19042.748 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 762823 [GEN-2018-048345.00] CKT 1 | 12.4074 | PASS | 33.7999 | PASS | 33699.8689 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 762823 [GEN-2018-048345.00] CKT 1 | 12.4074 | PASS | 101.6317 | PASS | 101531.7097 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 762823 [GEN-2018-048345.00] CKT 1 | 7.3326 | PASS | 14.6576 | PASS | 14557.5524 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 762823 [GEN-2018-048345.00] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.928 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515749 [PECANC11 13.800] CKT 1 | 12.4069 | PASS | 33.7953 | PASS | 33695.29 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515749 [PECANC11 13.800] CKT 1 | 12.4069 | PASS | 101.8671 | PASS | 101767.1451 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515749 [PECANC11 13.800] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.8295 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515749 [PECANC11 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8299 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515759 [PECANC21 13.800] CKT 2 | 12.4068 | PASS | 33.7968 | PASS | 33696.8159 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515759 [PECANC21 13.800] CKT 2 | 12.4068 | PASS | 101.7942 | PASS | 101694.1843 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515759 [PECANC21 13.800] CKT 2 | 7.3323 | PASS | 14.6588 | PASS | 14558.8453 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515234 [PECANCK5 161.00] TO BUS 515759 [PECANC21 13.800] CKT 2 | 10.1554 | PASS | 19.1428 | PASS | 19042.8167 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515233 [PECANCK4 138.00] TO BUS 515750 [PECANC31 13.800] CKT 4 | 12.4069 | PASS | 33.7949 | PASS | 33694.858 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515233 [PECANCK4 138.00] TO BUS 515750 [PECANC31 13.800] CKT 4 | 12.4069 | PASS | 101.8874 | PASS | 101787.4337 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515233 [PECANCK4 138.00] TO BUS 515750 [PECANC31 13.800] CKT 4 | 7.3323 | PASS | 14.659 | PASS | 14558.9817 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515233 [PECANCK4 138.00] TO BUS 515750 [PECANC31 13.800] CKT 4 | 10.1553 | PASS | 19.1429 | PASS | 19042.8641 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 12.4067 | PASS | 33.7928 | PASS | 33692.7814 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 12.4067 | PASS | 101.9707 | PASS | 101870.6573 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 7.332 | PASS | 14.6585 | PASS | 14558.5228 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 10.1545 | PASS | 19.142 | PASS | 19042.0355 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 2 | 12.4067 | PASS | 33.7928 | PASS | 33692.7738 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 2 | 12.4067 | PASS | 101.9708 | PASS | 101870.8017 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 2 | 7.332 | PASS | 14.6585 | PASS | 14558.5102 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 2 | 10.1545 | PASS | 19.142 | PASS | 19042.0361 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 12.408 | PASS | 33.7937 | PASS | 33693.7461 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 12.408 | PASS | 101.9866 | PASS | 101886.5904 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 7.3342 | PASS | 14.6561 | PASS | 14556.1356 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 10.1559 | PASS | 19.1441 | PASS | 19044.0913 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 12.4091 | PASS | 33.7947 | PASS | 33694.6902 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 12.4091 | PASS | 101.9944 | PASS | 101894.3733 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 7.336 | PASS | 14.6536 | PASS | 14553.5939 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 10.1564 | PASS | 19.1443 | PASS | 19044.2658 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 12.4084 | PASS | 33.7942 | PASS | 33694.1607 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 12.4084 | PASS | 101.9894 | PASS | 101889.446 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 7.3351 | PASS | 14.6547 | PASS | 14554.747 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 10.1562 | PASS | 19.145 | PASS | 19045.0323 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515051 [JACKTWN4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.871 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515051 [JACKTWN4 138.00] CKT 1 | 12.4069 | PASS | 101.979 | PASS | 101879.0173 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515051 [JACKTWN4 138.00] CKT 1 | 7.3319 | PASS | 14.6578 | PASS | 14557.7818 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515051 [JACKTWN4 138.00] CKT 1 | 10.155 | PASS | 19.1428 | PASS | 19042.7666 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515366 [WFROSST4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.9378 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515366 [WFROSST4 138.00] CKT 1 | 12.4069 | PASS | 101.9751 | PASS | 101875.055 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515366 [WFROSST4 138.00] CKT 1 | 7.331 | PASS | 14.6546 | PASS | 14554.6473 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 515366 [WFROSST4 138.00] CKT 1 | 10.1513 | PASS | 19.1447 | PASS | 19044.7196 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 520464 [MEEKER 4 138.00] CKT 1 | 12.4067 | PASS | 33.7944 | PASS | 33694.3941 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 520464 [MEEKER 4 138.00] CKT 1 | 12.4067 | PASS | 101.9146 | PASS | 101814.5829 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 520464 [MEEKER 4 138.00] CKT 1 | 7.3271 | PASS | 14.6425 | PASS | 14542.5279 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515442 [LINCOLN4 138.00] TO BUS 520464 [MEEKER 4 138.00] CKT 1 | 10.1513 | PASS | 19.1421 | PASS | 19042.0662 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515459 [ACORN 4 138.00] TO BUS 514839 [BRYANT 4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8745 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515459 [ACORN 4 138.00] TO BUS 514839 [BRYANT 4 138.00] CKT 1 | 12.4069 | PASS | 101.9765 | PASS | 101876.5197 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515459 [ACORN 4 138.00] TO BUS 514839 [BRYANT 4 138.00] CKT 1 | 7.3317 | PASS | 14.66 | PASS | 14559.9901 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515459 [ACORN 4 138.00] TO BUS 514839 [BRYANT 4 138.00] CKT 1 | 10.1542 | PASS | 19.1427 | PASS | 19042.7 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.4066 | PASS | 33.7928 | PASS | 33692.7771 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.4066 | PASS | 101.9649 | PASS | 101864.8988 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 7.3318 | PASS | 14.6598 | PASS | 14559.7822 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 10.1401 | PASS | 19.1433 | PASS | 19043.3051 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.9413 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 12.4068 | PASS | 101.9654 | PASS | 101865.3604 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 7.3288 | PASS | 14.6548 | PASS | 14554.7986 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 9.9791 | PASS | 19.1768 | PASS | 19076.8374 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 12.407 | PASS | 33.7931 | PASS | 33693.1025 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 12.407 | PASS | 101.9704 | PASS | 101870.3662 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 7.3314 | PASS | 14.6598 | PASS | 14559.8156 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 9.4984 | PASS | 19.388 | PASS | 19287.973 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] TO BUS 515801 [GRCMNT11 13.800] CKT 3 | 12.407 | PASS | 33.7929 | PASS | 33692.8805 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] TO BUS 515801 [GRCMNT11 13.800] CKT 3 | 12.407 | PASS | 101.9791 | PASS | 101879.0932 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] TO BUS 515801 [GRCMNT11 13.800] CKT 3 | 7.3317 | PASS | 14.6575 | PASS | 14557.5084 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] TO BUS 515801 [GRCMNT11 13.800] CKT 3 | 8.1176 | PASS | 20.2491 | PASS | 20149.1202 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8704 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.407 | PASS | 101.9793 | PASS | 101879.2885 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.9316 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 8.9658 | PASS | 19.6159 | PASS | 19515.889 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8684 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 2 | 12.407 | PASS | 101.9793 | PASS | 101879.3197 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.8979 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 2 | 9.2484 | PASS | 19.4947 | PASS | 19394.7129 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 514715 [WOODRNG7 345.00] CKT 1 | 12.4064 | PASS | 33.7927 | PASS | 33692.6658 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 514715 [WOODRNG7 345.00] CKT 1 | 12.4064 | PASS | 101.9574 | PASS | 101857.3925 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 514715 [WOODRNG7 345.00] CKT 1 | 7.3296 | PASS | 14.6583 | PASS | 14558.3169 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 514715 [WOODRNG7 345.00] CKT 1 | 10.1311 | PASS | 19.1474 | PASS | 19047.4108 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 12.4081 | PASS | 33.7939 | PASS | 33693.9481 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 12.4081 | PASS | 101.9827 | PASS | 101882.7289 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 7.3343 | PASS | 14.6553 | PASS | 14555.2628 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 10.1561 | PASS | 19.1451 | PASS | 19045.0559 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 12.4101 | PASS | 33.7958 | PASS | 33695.7936 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 12.4101 | PASS | 101.9931 | PASS | 101893.068 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 7.337 | PASS | 14.6502 | PASS | 14550.203 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 10.1551 | PASS | 19.1449 | PASS | 19044.9084 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 12.4076 | PASS | 33.7934 | PASS | 33693.4426 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 12.4076 | PASS | 101.9832 | PASS | 101883.1814 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 7.3334 | PASS | 14.657 | PASS | 14556.9915 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 10.1555 | PASS | 19.1436 | PASS | 19043.6181 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4067 | PASS | 33.7961 | PASS | 33696.1264 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4067 | PASS | 101.8141 | PASS | 101714.1469 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 7.0496 | PASS | 13.5002 | PASS | 13400.2272 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 10.1532 | PASS | 19.1432 | PASS | 19043.2476 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 520539 [TCPECTP4 138.00] CKT 1 | 12.4068 | PASS | 33.796 | PASS | 33696.0425 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 520539 [TCPECTP4 138.00] CKT 1 | 12.4068 | PASS | 101.8193 | PASS | 101719.3147 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 520539 [TCPECTP4 138.00] CKT 1 | 7.0491 | PASS | 13.4699 | PASS | 13369.897 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520406 [TUPELO 4 138.00] TO BUS 520539 [TCPECTP4 138.00] CKT 1 | 10.1532 | PASS | 19.1432 | PASS | 19043.1982 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521133 [BCI CL1 34.500] TO BUS 521153 [BCI TERT 4.9800] CKT 1 | 12.4073 | PASS | 33.793 | PASS | 33693.0075 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521133 [BCI CL1 34.500] TO BUS 521153 [BCI TERT 4.9800] CKT 1 | 12.4073 | PASS | 101.9803 | PASS | 101880.2683 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521133 [BCI CL1 34.500] TO BUS 521153 [BCI TERT 4.9800] CKT 1 | 7.333 | PASS | 14.6578 | PASS | 14557.7504 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521133 [BCI CL1 34.500] TO BUS 521153 [BCI TERT 4.9800] CKT 1 | 10.1619 | PASS | 19.2051 | PASS | 19105.0661 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521134 [BCII CL1 34.500] TO BUS 521154 [BCII TERT 4.9800] CKT 1 | 12.4092 | PASS | 33.7947 | PASS | 33694.7411 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521134 [BCII CL1 34.500] TO BUS 521154 [BCII TERT 4.9800] CKT 1 | 12.4092 | PASS | 102.0006 | PASS | 101900.5986 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521134 [BCII CL1 34.500] TO BUS 521154 [BCII TERT 4.9800] CKT 1 | 7.3372 | PASS | 14.6511 | PASS | 14551.1268 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521134 [BCII CL1 34.500] TO BUS 521154 [BCII TERT 4.9800] CKT 1 | 10.1859 | PASS | 19.2815 | PASS | 19181.4598 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521136 [BCVI CL1 34.500] TO BUS 521156 [BCVI TERT 9.9500] CKT 1 | 12.4072 | PASS | 33.7931 | PASS | 33693.1013 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521136 [BCVI CL1 34.500] TO BUS 521156 [BCVI TERT 9.9500] CKT 1 | 12.4072 | PASS | 101.9814 | PASS | 101881.3676 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521136 [BCVI CL1 34.500] TO BUS 521156 [BCVI TERT 9.9500] CKT 1 | 7.3331 | PASS | 14.657 | PASS | 14557.0246 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521136 [BCVI CL1 34.500] TO BUS 521156 [BCVI TERT 9.9500] CKT 1 | 10.162 | PASS | 19.2431 | PASS | 19143.1389 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520422 [SEQUOYAHJ4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9339 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520422 [SEQUOYAHJ4 138.00] CKT 1 | 12.407 | PASS | 101.9776 | PASS | 101877.6294 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520422 [SEQUOYAHJ4 138.00] CKT 1 | 7.331 | PASS | 14.6538 | PASS | 14553.7699 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520422 [SEQUOYAHJ4 138.00] CKT 1 | 10.1121 | PASS | 19.1085 | PASS | 19008.4681 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520508 [CLVLDSW4 138.00] CKT 1 | 12.407 | PASS | 33.793 | PASS | 33692.9656 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520508 [CLVLDSW4 138.00] CKT 1 | 12.407 | PASS | 101.9761 | PASS | 101876.1211 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520508 [CLVLDSW4 138.00] CKT 1 | 7.3309 | PASS | 14.6586 | PASS | 14558.5514 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520508 [CLVLDSW4 138.00] CKT 1 | 9.7904 | PASS | 19.1868 | PASS | 19086.7554 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.800] CKT 1 | 12.4079 | PASS | 33.7937 | PASS | 33693.6826 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.800] CKT 1 | 12.4079 | PASS | 101.9864 | PASS | 101886.4427 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.800] CKT 1 | 7.3329 | PASS | 14.654 | PASS | 14553.9837 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.800] CKT 1 | 9.8851 | PASS | 19.2253 | PASS | 19125.3236 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.800] CKT 1 | 12.4079 | PASS | 33.7937 | PASS | 33693.7057 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.800] CKT 1 | 12.4079 | PASS | 101.9865 | PASS | 101886.4623 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.800] CKT 1 | 7.333 | PASS | 14.6538 | PASS | 14553.8094 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.800] CKT 1 | 9.8869 | PASS | 19.2278 | PASS | 19127.8447 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.800] CKT 1 | 12.4079 | PASS | 33.7937 | PASS | 33693.6893 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.800] CKT 1 | 12.4079 | PASS | 101.9859 | PASS | 101885.8659 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.800] CKT 1 | 7.3329 | PASS | 14.654 | PASS | 14553.9608 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.800] CKT 1 | 9.8856 | PASS | 19.2261 | PASS | 19126.0645 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 12.407 | PASS | 33.793 | PASS | 33692.9704 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 12.407 | PASS | 101.9769 | PASS | 101876.9344 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 7.3267 | PASS | 14.6387 | PASS | 14538.665 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 10.0936 | PASS | 19.1088 | PASS | 19008.7848 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 12.407 | PASS | 33.793 | PASS | 33692.9855 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 12.407 | PASS | 101.9762 | PASS | 101876.1835 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 7.3313 | PASS | 14.6598 | PASS | 14559.8062 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 9.9524 | PASS | 19.1499 | PASS | 19049.9102 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8619 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.800] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4441 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8559 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.800] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8607 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.800] CKT 1 | 12.4077 | PASS | 33.7932 | PASS | 33693.1963 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.800] CKT 1 | 12.4077 | PASS | 101.9818 | PASS | 101881.8124 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.800] CKT 1 | 7.3327 | PASS | 14.6563 | PASS | 14556.2613 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.800] CKT 1 | 10.0082 | PASS | 19.1929 | PASS | 19092.8624 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8624 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.800] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4343 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8576 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8311 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8573 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.800] CKT 1 | 12.407 | PASS | 101.9788 | PASS | 101878.8402 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8603 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.800] CKT 1 | 10.1555 | PASS | 19.1427 | PASS | 19042.6573 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8543 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.800] CKT 1 | 12.4069 | PASS | 101.9789 | PASS | 101878.897 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8619 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.800] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.7819 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8687 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 12.407 | PASS | 101.9789 | PASS | 101878.8654 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 7.3324 | PASS | 14.6584 | PASS | 14558.3714 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 10.1184 | PASS | 19.1496 | PASS | 19049.5847 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520810 [ANADARK2 69.000] TO BUS 521181 [ADRKTERT 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8634 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520810 [ANADARK2 69.000] TO BUS 521181 [ADRKTERT 13.800] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.7228 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520810 [ANADARK2 69.000] TO BUS 521181 [ADRKTERT 13.800] CKT 1 | 7.3324 | PASS | 14.6588 | PASS | 14558.825 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520810 [ANADARK2 69.000] TO BUS 521181 [ADRKTERT 13.800] CKT 1 | 10.1431 | PASS | 19.1498 | PASS | 19049.8298 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521010 [NIJECT 4 138.00] CKT 1 | 12.4067 | PASS | 33.7928 | PASS | 33692.7746 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521010 [NIJECT 4 138.00] CKT 1 | 12.4067 | PASS | 101.9777 | PASS | 101877.7242 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521010 [NIJECT 4 138.00] CKT 1 | 7.3321 | PASS | 14.6592 | PASS | 14559.1899 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521010 [NIJECT 4 138.00] CKT 1 | 10.154 | PASS | 19.1303 | PASS | 19030.2521 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.8635 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 12.4068 | PASS | 101.9774 | PASS | 101877.3853 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 7.3314 | PASS | 14.6593 | PASS | 14559.3196 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521050 [SICKLES4 138.00] CKT 1 | 9.8003 | PASS | 19.163 | PASS | 19063.0027 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 520810 [ANADARK2 69.000] CKT 1 | 12.407 | PASS | 33.7928 | PASS | 33692.849 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 520810 [ANADARK2 69.000] CKT 1 | 12.407 | PASS | 101.9794 | PASS | 101879.4488 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 520810 [ANADARK2 69.000] CKT 1 | 7.3323 | PASS | 14.6589 | PASS | 14558.9182 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 520810 [ANADARK2 69.000] CKT 1 | 10.0586 | PASS | 19.1842 | PASS | 19084.1837 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.8661 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.4068 | PASS | 101.978 | PASS | 101878.0289 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.3311 | PASS | 14.6596 | PASS | 14559.561 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 9.7987 | PASS | 19.13 | PASS | 19029.9909 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 520543 [PINERDG2 69.000] CKT 1 | 12.4068 | PASS | 33.7928 | PASS | 33692.7939 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 520543 [PINERDG2 69.000] CKT 1 | 12.4068 | PASS | 101.9785 | PASS | 101878.4923 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 520543 [PINERDG2 69.000] CKT 1 | 7.3323 | PASS | 14.6591 | PASS | 14559.0882 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 520543 [PINERDG2 69.000] CKT 1 | 10.1548 | PASS | 19.1392 | PASS | 19039.2115 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521003 [MTNVWTP2 69.000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8614 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521003 [MTNVWTP2 69.000] CKT 1 | 12.4069 | PASS | 101.979 | PASS | 101879.0056 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521003 [MTNVWTP2 69.000] CKT 1 | 7.3323 | PASS | 14.6587 | PASS | 14558.6812 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521003 [MTNVWTP2 69.000] CKT 1 | 10.1071 | PASS | 19.1566 | PASS | 19056.5733 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.407 | PASS | 33.7931 | PASS | 33693.1175 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.407 | PASS | 101.9665 | PASS | 101866.4759 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 6.9371 | PASS | 13.5614 | PASS | 13461.3512 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 10.1526 | PASS | 19.1431 | PASS | 19043.0631 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 515192 [LULA 4 138.00] CKT 1 | 12.4068 | PASS | 33.7935 | PASS | 33693.5024 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 515192 [LULA 4 138.00] CKT 1 | 12.4068 | PASS | 101.9455 | PASS | 101845.4628 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 515192 [LULA 4 138.00] CKT 1 | 6.6407 | PASS | 11.8657 | PASS | 11765.7127 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 515192 [LULA 4 138.00] CKT 1 | 10.155 | PASS | 19.1426 | PASS | 19042.6341 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 521075 [STNWLTP4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8563 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 521075 [STNWLTP4 138.00] CKT 1 | 12.4069 | PASS | 101.9789 | PASS | 101878.8681 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 521075 [STNWLTP4 138.00] CKT 1 | 7.2988 | PASS | 14.7265 | PASS | 14626.4679 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521071 [STNWLSW4 138.00] TO BUS 521075 [STNWLTP4 138.00] CKT 1 | 10.1509 | PASS | 19.1431 | PASS | 19043.1125 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8715 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4069 | PASS | 101.9784 | PASS | 101878.3719 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 7.2996 | PASS | 14.4867 | PASS | 14386.6912 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 10.1553 | PASS | 19.1428 | PASS | 19042.8226 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 510949 [WAPANUCKA 4138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.8757 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 510949 [WAPANUCKA 4138.00] CKT 1 | 12.407 | PASS | 101.9787 | PASS | 101878.7437 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 510949 [WAPANUCKA 4138.00] CKT 1 | 7.326 | PASS | 14.6363 | PASS | 14536.2558 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 510949 [WAPANUCKA 4138.00] CKT 1 | 10.1549 | PASS | 19.143 | PASS | 19042.9664 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 520448 [BOGYDPT4 138.00] CKT 1 | 12.4068 | PASS | 33.7929 | PASS | 33692.8503 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 520448 [BOGYDPT4 138.00] CKT 1 | 12.4068 | PASS | 101.9779 | PASS | 101877.8815 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 520448 [BOGYDPT4 138.00] CKT 1 | 7.2887 | PASS | 14.4335 | PASS | 14333.5132 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521074 [BOGGY4 138.00] TO BUS 520448 [BOGYDPT4 138.00] CKT 1 | 10.155 | PASS | 19.1428 | PASS | 19042.8104 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521088 [WASHITA2 69.000] TO BUS 521089 [WASHITA4 138.00] TO BUS 521179 [WASHTERT 7.2000] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.86 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521088 [WASHITA2 69.000] TO BUS 521089 [WASHITA4 138.00] TO BUS 521179 [WASHTERT 7.2000] CKT 1 | 12.4069 | PASS | 101.9788 | PASS | 101878.7838 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521088 [WASHITA2 69.000] TO BUS 521089 [WASHITA4 138.00] TO BUS 521179 [WASHTERT 7.2000] CKT 1 | 7.3321 | PASS | 14.659 | PASS | 14558.9817 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521088 [WASHITA2 69.000] TO BUS 521089 [WASHITA4 138.00] TO BUS 521179 [WASHTERT 7.2000] CKT 1 | 9.9746 | PASS | 19.1732 | PASS | 19073.1704 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.4096 | PASS | 33.7951 | PASS | 33695.1386 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.4096 | PASS | 102.0015 | PASS | 101901.5476 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.3381 | PASS | 14.6467 | PASS | 14546.6904 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 10.2006 | PASS | 19.6385 | PASS | 19538.5228 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 529304 [OMDUNCN4 138.00] TO BUS 511453 [DUNCAN-4 138.00] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9311 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 529304 [OMDUNCN4 138.00] TO BUS 511453 [DUNCAN-4 138.00] CKT 1 | 12.407 | PASS | 101.9786 | PASS | 101878.5708 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 529304 [OMDUNCN4 138.00] TO BUS 511453 [DUNCAN-4 138.00] CKT 1 | 7.3308 | PASS | 14.6547 | PASS | 14554.7182 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 529304 [OMDUNCN4 138.00] TO BUS 511453 [DUNCAN-4 138.00] CKT 1 | 10.1284 | PASS | 19.1456 | PASS | 19045.5632 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 12.4104 | PASS | 33.7967 | PASS | 33696.698 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 12.4104 | PASS | 101.9596 | PASS | 101859.5853 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 7.339 | PASS | 14.6497 | PASS | 14549.7056 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 10.1561 | PASS | 19.1437 | PASS | 19043.726 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8202 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.4069 | PASS | 101.976 | PASS | 101875.9686 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 7.3323 | PASS | 14.659 | PASS | 14558.9759 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 10.1553 | PASS | 19.1429 | PASS | 19042.9404 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 12.4069 | PASS | 33.7928 | PASS | 33692.8202 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 12.4069 | PASS | 101.976 | PASS | 101875.9686 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 7.3323 | PASS | 14.659 | PASS | 14558.9759 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 10.1553 | PASS | 19.1429 | PASS | 19042.9404 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 12.4069 | PASS | 33.7928 | PASS | 33692.8396 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 12.4069 | PASS | 101.9783 | PASS | 101878.2948 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8877 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8056 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 12.4066 | PASS | 33.7928 | PASS | 33692.8008 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 12.4066 | PASS | 101.9636 | PASS | 101863.554 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 7.3317 | PASS | 14.6598 | PASS | 14559.8198 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 10.1538 | PASS | 19.1432 | PASS | 19043.1839 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 12.4066 | PASS | 33.7928 | PASS | 33692.8008 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 12.4066 | PASS | 101.9636 | PASS | 101863.554 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 7.3317 | PASS | 14.6598 | PASS | 14559.8198 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 10.1538 | PASS | 19.1432 | PASS | 19043.1839 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 12.407 | PASS | 33.7928 | PASS | 33692.8484 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 12.407 | PASS | 101.9795 | PASS | 101879.4609 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8515 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 10.1555 | PASS | 19.1428 | PASS | 19042.8466 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 12.4069 | PASS | 33.7929 | PASS | 33692.8653 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 12.4069 | PASS | 101.9782 | PASS | 101878.2454 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.886 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.858 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.4064 | PASS | 33.7927 | PASS | 33692.7452 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.4064 | PASS | 101.9561 | PASS | 101856.0837 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 7.3321 | PASS | 14.6592 | PASS | 14559.2374 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 10.1553 | PASS | 19.1428 | PASS | 19042.8153 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [NRSS7 345.00] CKT 1 | 12.4057 | PASS | 33.7929 | PASS | 33692.9452 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [NRSS7 345.00] CKT 1 | 12.4057 | PASS | 101.9084 | PASS | 101808.3624 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [NRSS7 345.00] CKT 1 | 7.3312 | PASS | 14.6605 | PASS | 14560.4589 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [NRSS7 345.00] CKT 1 | 10.1546 | PASS | 19.1426 | PASS | 19042.6469 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.4061 | PASS | 33.7933 | PASS | 33693.3022 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.4061 | PASS | 101.9175 | PASS | 101817.4768 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 7.3323 | PASS | 14.6587 | PASS | 14558.7315 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 10.1552 | PASS | 19.1428 | PASS | 19042.8166 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533023 [N345 3 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.407 | PASS | 33.7929 | PASS | 33692.9264 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533023 [N345 3 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.407 | PASS | 101.9791 | PASS | 101879.1091 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533023 [N345 3 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 7.3324 | PASS | 14.6589 | PASS | 14558.8857 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533023 [N345 3 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 10.1555 | PASS | 19.1429 | PASS | 19042.8501 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532939 [N345 4 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 2 | 12.4065 | PASS | 33.7927 | PASS | 33692.725 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532939 [N345 4 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 2 | 12.4065 | PASS | 101.9592 | PASS | 101859.1632 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532939 [N345 4 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 2 | 7.3323 | PASS | 14.6589 | PASS | 14558.9452 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532939 [N345 4 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 2 | 10.1554 | PASS | 19.1429 | PASS | 19042.8511 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.4021 | PASS | 33.7889 | PASS | 33688.8721 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.4021 | PASS | 101.9269 | PASS | 101826.8661 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 7.3322 | PASS | 14.6591 | PASS | 14559.1206 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.7973 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 549984 [BROOKLINE 7345.00] CKT 1 | 12.4026 | PASS | 33.7903 | PASS | 33690.3485 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 549984 [BROOKLINE 7345.00] CKT 1 | 12.4026 | PASS | 101.8834 | PASS | 101783.3726 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 549984 [BROOKLINE 7345.00] CKT 1 | 7.3316 | PASS | 14.6598 | PASS | 14559.7825 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 549984 [BROOKLINE 7345.00] CKT 1 | 10.1553 | PASS | 19.1427 | PASS | 19042.7242 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 800102 [NBRAN345 345.00] CKT 1 | 12.4012 | PASS | 33.7914 | PASS | 33691.4196 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 800102 [NBRAN345 345.00] CKT 1 | 12.4012 | PASS | 101.755 | PASS | 101655.004 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 800102 [NBRAN345 345.00] CKT 1 | 7.3319 | PASS | 14.6595 | PASS | 14559.5468 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 580555 [MONETT345 345.00] TO BUS 800102 [NBRAN345 345.00] CKT 1 | 10.1554 | PASS | 19.1428 | PASS | 19042.7756 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760053 [G17-133-XFM134.500] CKT 1 | 12.4084 | PASS | 33.7941 | PASS | 33694.0674 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760053 [G17-133-XFM134.500] CKT 1 | 12.4084 | PASS | 101.9944 | PASS | 101894.3793 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760053 [G17-133-XFM134.500] CKT 1 | 7.3354 | PASS | 14.6543 | PASS | 14554.3363 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760053 [G17-133-XFM134.500] CKT 1 | 10.1568 | PASS | 19.1451 | PASS | 19045.1388 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760074 [G17-134-XFM134.500] CKT 1 | 12.4088 | PASS | 33.7944 | PASS | 33694.3686 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760074 [G17-134-XFM134.500] CKT 1 | 12.4088 | PASS | 101.9976 | PASS | 101897.6161 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760074 [G17-134-XFM134.500] CKT 1 | 7.3362 | PASS | 14.6532 | PASS | 14553.2266 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760074 [G17-134-XFM134.500] CKT 1 | 10.1569 | PASS | 19.1454 | PASS | 19045.3545 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760095 [G17-137-XFM134.500] CKT 1 | 12.4091 | PASS | 33.7946 | PASS | 33694.6331 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760095 [G17-137-XFM134.500] CKT 1 | 12.4091 | PASS | 102 | PASS | 101899.9645 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760095 [G17-137-XFM134.500] CKT 1 | 7.3368 | PASS | 14.6522 | PASS | 14552.24 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 760032 [GEN-2017-133345.00] TO BUS 760095 [G17-137-XFM134.500] CKT 1 | 10.157 | PASS | 19.1456 | PASS | 19045.5512 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760152 [TNOXF2 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8637 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760152 [TNOXF2 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 2 | 12.407 | PASS | 101.9792 | PASS | 101879.1673 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 760152 [TNOXF2 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.9107 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 760152 [TNOXF2 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 2 | 10.1553 | PASS | 19.1428 | PASS | 19042.8349 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 12.4073 | PASS | 33.7937 | PASS | 33693.7361 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 12.4073 | PASS | 101.9581 | PASS | 101858.0528 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 7.3083 | PASS | 14.5978 | PASS | 14497.8315 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.0008 | PASS | 19.1625 | PASS | 19062.4763 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.4073 | PASS | 33.7932 | PASS | 33693.2485 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.4073 | PASS | 101.9797 | PASS | 101879.7093 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 7.3323 | PASS | 14.6555 | PASS | 14555.4733 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 10.158 | PASS | 19.1491 | PASS | 19049.091 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4086 | PASS | 33.7942 | PASS | 33694.2291 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4086 | PASS | 101.994 | PASS | 101893.9974 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3353 | PASS | 14.6543 | PASS | 14554.2816 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 10.156 | PASS | 19.1438 | PASS | 19043.8094 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 762648 [G18-029XFM1 34.500] CKT 1 | 12.4086 | PASS | 33.7942 | PASS | 33694.2218 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 762648 [G18-029XFM1 34.500] CKT 1 | 12.4086 | PASS | 101.9939 | PASS | 101893.8843 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 762648 [G18-029XFM1 34.500] CKT 1 | 7.3355 | PASS | 14.6539 | PASS | 14553.8542 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 762647 [GEN-2018-029138.00] TO BUS 762648 [G18-029XFM1 34.500] CKT 1 | 10.156 | PASS | 19.1442 | PASS | 19044.2223 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.4082 | PASS | 33.7933 | PASS | 33693.3458 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.4082 | PASS | 101.9852 | PASS | 101885.2476 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 7.3341 | PASS | 14.656 | PASS | 14556.0309 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 10.1574 | PASS | 19.1495 | PASS | 19049.5336 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.4082 | PASS | 33.7933 | PASS | 33693.3494 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.4082 | PASS | 101.9847 | PASS | 101884.7297 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 7.3341 | PASS | 14.6561 | PASS | 14556.0672 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 10.1574 | PASS | 19.1494 | PASS | 19049.4131 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 763472 [GEN-2019-002161.00] TO BUS 763473 [G19-002-XFM134.500] CKT 1 | 12.4083 | PASS | 33.7946 | PASS | 33694.5783 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 763472 [GEN-2019-002161.00] TO BUS 763473 [G19-002-XFM134.500] CKT 1 | 12.4083 | PASS | 101.9613 | PASS | 101861.2517 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 763472 [GEN-2019-002161.00] TO BUS 763473 [G19-002-XFM134.500] CKT 1 | 7.3339 | PASS | 14.6568 | PASS | 14556.7846 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 763472 [GEN-2019-002161.00] TO BUS 763473 [G19-002-XFM134.500] CKT 1 | 10.1556 | PASS | 19.143 | PASS | 19043.0399 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 & 2 | 12.4057 | PASS | 33.793 | PASS | 33692.9878 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 & 2 | 12.4057 | PASS | 101.9076 | PASS | 101807.5598 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 & 2 | 7.3324 | PASS | 14.6587 | PASS | 14558.6636 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 & 2 | 10.1554 | PASS | 19.1429 | PASS | 19042.8956 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 & 2 | 12.4088 | PASS | 33.7963 | PASS | 33696.3118 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 & 2 | 12.4088 | PASS | 101.8988 | PASS | 101798.8283 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 & 2 | 7.3347 | PASS | 14.6556 | PASS | 14555.6059 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 & 2 | 10.1556 | PASS | 19.1431 | PASS | 19043.1474 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 & 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8622 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 & 2 | 12.407 | PASS | 101.9787 | PASS | 101878.7456 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 & 2 | 7.3324 | PASS | 14.6589 | PASS | 14558.8541 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 & 2 | 10.1555 | PASS | 19.1428 | PASS | 19042.8471 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8593 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 2 | 12.407 | PASS | 101.9791 | PASS | 101879.0525 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 2 | 7.3322 | PASS | 14.6577 | PASS | 14557.7244 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 2 | 10.1534 | PASS | 19.1431 | PASS | 19043.1305 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 3 | 12.407 | PASS | 33.7929 | PASS | 33692.8597 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 3 | 12.407 | PASS | 101.979 | PASS | 101879.0451 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 3 | 7.3321 | PASS | 14.6576 | PASS | 14557.6449 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 & 3 | 10.1532 | PASS | 19.1431 | PASS | 19043.1124 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 & 3 | 12.407 | PASS | 33.7929 | PASS | 33692.8569 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 & 3 | 12.407 | PASS | 101.9784 | PASS | 101878.4062 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 & 3 | 7.3321 | PASS | 14.6575 | PASS | 14557.5314 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 & 3 | 10.153 | PASS | 19.1432 | PASS | 19043.1507 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 & 2 | 12.407 | PASS | 33.7929 | PASS | 33692.9212 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 & 2 | 12.407 | PASS | 101.9781 | PASS | 101878.0689 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 & 2 | 7.3315 | PASS | 14.6598 | PASS | 14559.8451 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514966 [MIDWAY 4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 & 2 | 10.1536 | PASS | 19.1422 | PASS | 19042.184 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 2 | 12.4066 | PASS | 33.7938 | PASS | 33693.8024 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 2 | 12.4066 | PASS | 101.9225 | PASS | 101822.5134 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 2 | 7.329 | PASS | 14.6544 | PASS | 14554.4488 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 2 | 10.1132 | PASS | 19.15 | PASS | 19049.9621 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 3 | 12.4067 | PASS | 33.7935 | PASS | 33693.5091 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 3 | 12.4067 | PASS | 101.9373 | PASS | 101837.2946 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 3 | 7.3283 | PASS | 14.6591 | PASS | 14559.0561 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 & 3 | 10.1261 | PASS | 19.1452 | PASS | 19045.1925 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 & 3 | 12.4067 | PASS | 33.7935 | PASS | 33693.5091 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 & 3 | 12.4067 | PASS | 101.9373 | PASS | 101837.2946 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 & 3 | 7.3283 | PASS | 14.6591 | PASS | 14559.0561 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 & 3 | 10.1261 | PASS | 19.1452 | PASS | 19045.1925 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 & 2 | 12.4056 | PASS | 33.7924 | PASS | 33692.3987 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 & 2 | 12.4056 | PASS | 101.9349 | PASS | 101834.9156 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 & 2 | 7.3302 | PASS | 14.6576 | PASS | 14557.6004 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 & 2 | 10.1494 | PASS | 19.1395 | PASS | 19039.4843 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 & 2 | 12.407 | PASS | 33.7929 | PASS | 33692.8714 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 & 2 | 12.407 | PASS | 101.979 | PASS | 101879.0201 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 & 2 | 7.3321 | PASS | 14.6593 | PASS | 14559.3177 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 & 2 | 6.824 | PASS | 20.7606 | PASS | 20660.6269 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 & 2 | 12.4059 | PASS | 33.7924 | PASS | 33692.3869 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 & 2 | 12.4059 | PASS | 101.945 | PASS | 101844.9708 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 & 2 | 7.3313 | PASS | 14.6602 | PASS | 14560.2072 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 & 2 | 10.1532 | PASS | 19.1436 | PASS | 19043.6211 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 12.4056 | PASS | 33.7926 | PASS | 33692.6346 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 12.4056 | PASS | 101.9149 | PASS | 101814.9368 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 7.3294 | PASS | 14.6628 | PASS | 14562.8442 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29WP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 10.1487 | PASS | 19.1439 | PASS | 19043.9184 | 175 | 226.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | base | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | base | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | base | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | base | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | base | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | base | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | base | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | base | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | base | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | base | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | base | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | base | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | base | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1667 | PASS | 1.378 | PASS | 1277.9994 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1667 | PASS | 1.3776 | PASS | 1277.6363 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1667 | PASS | 1.3755 | PASS | 1275.5177 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1667 | PASS | 1.3466 | PASS | 1246.5705 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1667 | PASS | 1.3466 | PASS | 1246.6139 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1667 | PASS | 1.3466 | PASS | 1246.6139 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 3.5921 | FAIL | 24.4619 | PASS | 24361.9167 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 31.9192 | PASS | 0.72356 | PASS | 623.564 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 31.9192 | PASS | 0.72356 | PASS | 623.564 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.4202 | PASS | 6.1485 | PASS | 6048.4551 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.4202 | PASS | 1.7194 | PASS | 1619.4355 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.5079 | PASS | 0.041037 | FAIL | -58.9633 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.5079 | PASS | 0.059585 | FAIL | -40.4148 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.2029 | PASS | 1.3776 | PASS | 1277.6243 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.2029 | PASS | 1.3772 | PASS | 1277.2442 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.2029 | PASS | 1.3751 | PASS | 1275.1039 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.2029 | PASS | 1.3463 | PASS | 1246.323 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.2029 | PASS | 1.3464 | PASS | 1246.365 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.2029 | PASS | 1.3464 | PASS | 1246.365 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 3.597 | FAIL | 24.4737 | PASS | 24373.7377 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.4412 | PASS | 6.148 | PASS | 6048.002 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.4412 | PASS | 1.7197 | PASS | 1619.7318 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.5193 | PASS | 0.041056 | FAIL | -58.9438 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.5193 | PASS | 0.059571 | FAIL | -40.4285 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.3075 | PASS | 1.3787 | PASS | 1278.6964 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.3075 | PASS | 1.3783 | PASS | 1278.322 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.3075 | PASS | 1.3762 | PASS | 1276.18 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.3075 | PASS | 1.3474 | PASS | 1247.4182 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.3075 | PASS | 1.3475 | PASS | 1247.4603 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.3075 | PASS | 1.3475 | PASS | 1247.4603 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 3.5884 | FAIL | 24.4546 | PASS | 24354.6464 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 31.9259 | PASS | 0.72357 | PASS | 623.5654 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 31.9259 | PASS | 0.72357 | PASS | 623.5654 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.4107 | PASS | 6.1587 | PASS | 6058.6994 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.4107 | PASS | 1.719 | PASS | 1619.0166 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.5019 | PASS | 0.041011 | FAIL | -58.9887 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 6.5019 | PASS | 0.059609 | FAIL | -40.3907 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.2055 | PASS | 1.3783 | PASS | 1278.2986 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.2055 | PASS | 1.3779 | PASS | 1277.9406 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.2055 | PASS | 1.3758 | PASS | 1275.8269 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.2055 | PASS | 1.3468 | PASS | 1246.8418 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.2055 | PASS | 1.3469 | PASS | 1246.8855 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.2055 | PASS | 1.3469 | PASS | 1246.8855 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 3.5961 | FAIL | 24.4717 | PASS | 24371.7344 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 6.4379 | PASS | 6.1493 | PASS | 6049.2738 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.6412 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 6.5168 | PASS | 0.041046 | FAIL | -58.9544 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 6.5168 | PASS | 0.059576 | FAIL | -40.4242 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 9.1748 | PASS | 1.3774 | PASS | 1277.416 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 9.1748 | PASS | 1.377 | PASS | 1277.0445 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 9.1748 | PASS | 1.3749 | PASS | 1274.918 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 9.1748 | PASS | 1.346 | PASS | 1246.0323 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 9.1748 | PASS | 1.3461 | PASS | 1246.075 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 9.1748 | PASS | 1.3461 | PASS | 1246.075 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 3.2678 | FAIL | 23.6091 | PASS | 23509.0789 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 4.8157 | FAIL | 5.5466 | PASS | 5446.6082 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 4.8157 | FAIL | 1.7783 | PASS | 1678.2579 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 6.5092 | PASS | 0.041043 | FAIL | -58.9575 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530724 [CENTENNIAL3 115.00] CKT 1 | 6.5092 | PASS | 0.05958 | FAIL | -40.4198 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1763 | PASS | 1.3774 | PASS | 1277.3592 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1763 | PASS | 1.377 | PASS | 1276.9869 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1763 | PASS | 1.3749 | PASS | 1274.8594 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1763 | PASS | 1.346 | PASS | 1245.9805 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1763 | PASS | 1.346 | PASS | 1246.0232 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1763 | PASS | 1.346 | PASS | 1246.0232 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9271 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1539 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6504 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1395 | PASS | 1.3779 | PASS | 1277.9422 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1395 | PASS | 1.3776 | PASS | 1277.5775 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1395 | PASS | 1.3755 | PASS | 1275.4567 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1395 | PASS | 1.3465 | PASS | 1246.5268 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1395 | PASS | 1.3466 | PASS | 1246.57 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1395 | PASS | 1.3466 | PASS | 1246.57 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 3.596 | FAIL | 24.4715 | PASS | 24371.5262 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4375 | PASS | 6.1494 | PASS | 6049.4031 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.6348 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5083 | PASS | 0.041061 | FAIL | -58.9391 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5083 | PASS | 0.059575 | FAIL | -40.4245 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1682 | PASS | 1.3778 | PASS | 1277.8138 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1682 | PASS | 1.3774 | PASS | 1277.4478 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1682 | PASS | 1.3753 | PASS | 1275.3261 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1682 | PASS | 1.3464 | PASS | 1246.4027 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1682 | PASS | 1.3464 | PASS | 1246.4458 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1682 | PASS | 1.3464 | PASS | 1246.4458 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 3.596 | FAIL | 24.4717 | PASS | 24371.6668 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4377 | PASS | 6.1493 | PASS | 6049.2799 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4377 | PASS | 1.7196 | PASS | 1619.6398 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5161 | PASS | 0.041048 | FAIL | -58.9523 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5161 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1628 | PASS | 1.3774 | PASS | 1277.3615 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1628 | PASS | 1.377 | PASS | 1276.989 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1628 | PASS | 1.3749 | PASS | 1274.8612 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1628 | PASS | 1.346 | PASS | 1245.9849 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1628 | PASS | 1.346 | PASS | 1246.0276 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 9.1628 | PASS | 1.346 | PASS | 1246.0276 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9412 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.1485 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6508 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5163 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531448 [HOLCOMB3 115.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 8.599 | PASS | 1.3805 | PASS | 1280.4905 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 8.599 | PASS | 1.3801 | PASS | 1280.1489 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 8.599 | PASS | 1.378 | PASS | 1278.0429 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 8.599 | PASS | 1.349 | PASS | 1248.9975 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 8.599 | PASS | 1.349 | PASS | 1249.0422 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 8.599 | PASS | 1.349 | PASS | 1249.0422 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 3.5957 | FAIL | 24.4705 | PASS | 24370.5298 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.4364 | PASS | 6.1496 | PASS | 6049.6033 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.4364 | PASS | 1.7196 | PASS | 1619.5949 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.5097 | PASS | 0.041038 | FAIL | -58.9617 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.5097 | PASS | 0.059585 | FAIL | -40.4149 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 7.6897 | PASS | 1.3832 | PASS | 1283.2289 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 7.6897 | PASS | 1.3829 | PASS | 1282.9071 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 7.6897 | PASS | 1.3808 | PASS | 1280.8108 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 7.6897 | PASS | 1.3517 | PASS | 1251.6879 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 7.6897 | PASS | 1.3517 | PASS | 1251.7339 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 7.6897 | PASS | 1.3517 | PASS | 1251.7339 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 3.5911 | FAIL | 24.4662 | PASS | 24366.2482 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5667 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5667 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 6.4046 | PASS | 6.1403 | PASS | 6040.3082 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 6.4046 | PASS | 1.72 | PASS | 1619.9927 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 6.2248 | PASS | 0.041187 | FAIL | -58.8126 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 6.2248 | PASS | 0.05969 | FAIL | -40.3101 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 9.1779 | PASS | 1.3774 | PASS | 1277.4272 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 9.1779 | PASS | 1.3771 | PASS | 1277.056 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 9.1779 | PASS | 1.3749 | PASS | 1274.9296 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0425 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 9.1779 | PASS | 1.3461 | PASS | 1246.0852 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 9.1779 | PASS | 1.3461 | PASS | 1246.0852 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 3.5966 | FAIL | 24.4729 | PASS | 24372.9484 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 31.9293 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 31.9293 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 6.4397 | PASS | 6.1486 | PASS | 6048.6291 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 6.4397 | PASS | 1.7197 | PASS | 1619.6867 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 6.517 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531502 [CIMRRN 7 345.00] CKT 1 | 6.517 | PASS | 0.059575 | FAIL | -40.4254 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 9.178 | PASS | 1.3776 | PASS | 1277.6128 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 9.178 | PASS | 1.3772 | PASS | 1277.2411 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 9.178 | PASS | 1.3751 | PASS | 1275.1129 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 9.178 | PASS | 1.3462 | PASS | 1246.2393 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 9.178 | PASS | 1.3463 | PASS | 1246.282 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 9.178 | PASS | 1.3463 | PASS | 1246.282 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 3.5966 | FAIL | 24.4722 | PASS | 24372.1959 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 6.4395 | PASS | 6.1482 | PASS | 6048.1565 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 6.4395 | PASS | 1.7197 | PASS | 1619.705 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 6.5171 | PASS | 0.041058 | FAIL | -58.9425 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531504 [CIMWD2 7 345.00] CKT 1 | 6.5171 | PASS | 0.059582 | FAIL | -40.4183 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 9.1778 | PASS | 1.3773 | PASS | 1277.3121 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 9.1778 | PASS | 1.3769 | PASS | 1276.9391 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 9.1778 | PASS | 1.3748 | PASS | 1274.8112 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 9.1778 | PASS | 1.3459 | PASS | 1245.9363 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.979 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.979 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 3.5939 | FAIL | 24.4679 | PASS | 24367.9378 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 6.4269 | PASS | 6.1486 | PASS | 6048.6156 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 6.4269 | PASS | 1.7198 | PASS | 1619.7655 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 6.5157 | PASS | 0.041047 | FAIL | -58.9533 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532998 [G16-111-TAP 345.00] CKT 1 | 6.5157 | PASS | 0.059575 | FAIL | -40.4246 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1735 | PASS | 1.3773 | PASS | 1277.3472 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1735 | PASS | 1.377 | PASS | 1276.9747 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1735 | PASS | 1.3748 | PASS | 1274.8472 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1735 | PASS | 1.346 | PASS | 1245.9689 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1735 | PASS | 1.346 | PASS | 1246.0116 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1735 | PASS | 1.346 | PASS | 1246.0116 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9057 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.4378 | PASS | 6.1489 | PASS | 6048.8706 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.4378 | PASS | 1.7197 | PASS | 1619.6522 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.5136 | PASS | 0.041048 | FAIL | -58.9518 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.5136 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.1735 | PASS | 1.3773 | PASS | 1277.3472 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.1735 | PASS | 1.377 | PASS | 1276.9747 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.1735 | PASS | 1.3748 | PASS | 1274.8472 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.1735 | PASS | 1.346 | PASS | 1245.9689 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.1735 | PASS | 1.346 | PASS | 1246.0116 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.1735 | PASS | 1.346 | PASS | 1246.0116 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9057 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.4378 | PASS | 6.1489 | PASS | 6048.8706 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.4378 | PASS | 1.7197 | PASS | 1619.6522 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.5136 | PASS | 0.041048 | FAIL | -58.9518 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.5136 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1651 | PASS | 1.3774 | PASS | 1277.4394 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1651 | PASS | 1.3771 | PASS | 1277.0683 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1651 | PASS | 1.3749 | PASS | 1274.9419 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1651 | PASS | 1.3461 | PASS | 1246.0543 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1651 | PASS | 1.3461 | PASS | 1246.097 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1651 | PASS | 1.3461 | PASS | 1246.097 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 3.5939 | FAIL | 24.4681 | PASS | 24368.097 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 31.9255 | PASS | 0.72357 | PASS | 623.5653 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 31.9255 | PASS | 0.72357 | PASS | 623.5653 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.4247 | PASS | 6.1463 | PASS | 6046.3445 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.4247 | PASS | 1.7197 | PASS | 1619.7471 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.5072 | PASS | 0.041048 | FAIL | -58.9519 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.5072 | PASS | 0.059577 | FAIL | -40.423 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 9.1784 | PASS | 1.3773 | PASS | 1277.3346 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 9.1784 | PASS | 1.377 | PASS | 1276.962 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 9.1784 | PASS | 1.3748 | PASS | 1274.8344 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.9572 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.9999 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.9999 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 3.596 | FAIL | 24.4709 | PASS | 24370.8951 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 31.935 | PASS | 0.72357 | PASS | 623.5682 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 31.935 | PASS | 0.72357 | PASS | 623.5682 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 6.4378 | PASS | 6.1491 | PASS | 6049.0553 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 6.4378 | PASS | 1.7196 | PASS | 1619.638 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 6.5174 | PASS | 0.041048 | FAIL | -58.9522 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 6.5174 | PASS | 0.059575 | FAIL | -40.4255 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 9.1717 | PASS | 1.3774 | PASS | 1277.373 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 9.1717 | PASS | 1.377 | PASS | 1277.0009 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 9.1717 | PASS | 1.3749 | PASS | 1274.8738 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 9.1717 | PASS | 1.346 | PASS | 1245.9927 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 9.1717 | PASS | 1.346 | PASS | 1246.0354 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 9.1717 | PASS | 1.346 | PASS | 1246.0354 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 3.5949 | FAIL | 24.4686 | PASS | 24368.6333 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 31.9045 | PASS | 0.72357 | PASS | 623.566 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 31.9045 | PASS | 0.72357 | PASS | 623.566 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.4313 | PASS | 6.1474 | PASS | 6047.4498 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.4313 | PASS | 1.7196 | PASS | 1619.624 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.5115 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.5115 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3424 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9699 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8424 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9644 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.007 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.007 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9725 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 31.9304 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 31.9304 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 6.4382 | PASS | 6.1492 | PASS | 6049.1752 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.6565 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 6.5169 | PASS | 0.041047 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4254 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3411 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9686 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8411 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0059 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0059 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9861 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 31.9306 | PASS | 0.72357 | PASS | 623.5669 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 31.9306 | PASS | 0.72357 | PASS | 623.5669 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 6.4382 | PASS | 6.1492 | PASS | 6049.1683 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.658 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 6.5169 | PASS | 0.041048 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4255 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1774 | PASS | 1.3774 | PASS | 1277.358 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1774 | PASS | 1.377 | PASS | 1276.9858 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1774 | PASS | 1.3749 | PASS | 1274.8585 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1245.9788 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0215 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0215 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.596 | FAIL | 24.4716 | PASS | 24371.62 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.4374 | PASS | 6.1491 | PASS | 6049.1051 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.4374 | PASS | 1.7197 | PASS | 1619.6515 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.5163 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 9.1783 | PASS | 1.3773 | PASS | 1277.3089 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 9.1783 | PASS | 1.3769 | PASS | 1276.9359 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 9.1783 | PASS | 1.3748 | PASS | 1274.8079 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 9.1783 | PASS | 1.3459 | PASS | 1245.9334 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9761 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9761 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 3.5959 | FAIL | 24.4694 | PASS | 24369.3511 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 31.9308 | PASS | 0.72357 | PASS | 623.5669 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 31.9308 | PASS | 0.72357 | PASS | 623.5669 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 6.4373 | PASS | 6.1478 | PASS | 6047.7985 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 6.4373 | PASS | 1.7197 | PASS | 1619.663 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 6.5169 | PASS | 0.041048 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.3497 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9773 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.8499 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9711 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0138 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0138 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.596 | FAIL | 24.4718 | PASS | 24371.8083 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.4377 | PASS | 6.1492 | PASS | 6049.2475 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.4377 | PASS | 1.7196 | PASS | 1619.6438 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.5164 | PASS | 0.041047 | FAIL | -58.9534 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.5164 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3502 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9778 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8504 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9715 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0142 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0142 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.596 | FAIL | 24.4718 | PASS | 24371.8011 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.4376 | PASS | 6.1493 | PASS | 6049.2556 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.4376 | PASS | 1.7196 | PASS | 1619.6437 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.5164 | PASS | 0.041047 | FAIL | -58.9534 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.5164 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 9.1766 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 9.1766 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 9.1766 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 9.1766 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 9.1766 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 9.1766 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 3.5955 | FAIL | 24.4661 | PASS | 24366.0882 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 6.4343 | PASS | 6.1438 | PASS | 6043.7534 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 6.4343 | PASS | 1.7195 | PASS | 1619.54 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 6.5146 | PASS | 0.041048 | FAIL | -58.9523 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 6.5146 | PASS | 0.059575 | FAIL | -40.4245 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 9.1751 | PASS | 1.3774 | PASS | 1277.3554 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 9.1751 | PASS | 1.377 | PASS | 1276.9831 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 9.1751 | PASS | 1.3749 | PASS | 1274.8558 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1245.9765 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1246.0192 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1246.0192 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 3.5946 | FAIL | 24.4663 | PASS | 24366.2533 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 6.4285 | PASS | 6.1445 | PASS | 6044.5081 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 6.4285 | PASS | 1.7198 | PASS | 1619.7632 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 6.5119 | PASS | 0.041048 | FAIL | -58.9517 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 6.5119 | PASS | 0.059577 | FAIL | -40.4235 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1771 | PASS | 1.3774 | PASS | 1277.3513 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1771 | PASS | 1.377 | PASS | 1276.9789 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1771 | PASS | 1.3749 | PASS | 1274.8515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.5918 | FAIL | 24.4684 | PASS | 24368.3585 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.412 | PASS | 6.1473 | PASS | 6047.2536 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.412 | PASS | 1.7206 | PASS | 1620.5782 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.5159 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.5159 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 9.177 | PASS | 1.3774 | PASS | 1277.3512 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 9.177 | PASS | 1.377 | PASS | 1276.9788 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 9.177 | PASS | 1.3749 | PASS | 1274.8514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 9.177 | PASS | 1.346 | PASS | 1245.9724 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 9.177 | PASS | 1.346 | PASS | 1246.0151 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 9.177 | PASS | 1.346 | PASS | 1246.0151 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 3.5914 | FAIL | 24.4677 | PASS | 24367.7303 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 6.4092 | PASS | 6.1468 | PASS | 6046.7663 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 6.4092 | PASS | 1.7207 | PASS | 1620.6686 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 6.5158 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 6.5158 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3554 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9831 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8558 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9763 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.019 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.019 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.5958 | FAIL | 24.4715 | PASS | 24371.533 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.4374 | PASS | 6.1494 | PASS | 6049.3743 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.4374 | PASS | 1.7196 | PASS | 1619.6319 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 9.1773 | PASS | 1.3774 | PASS | 1277.3692 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 9.1773 | PASS | 1.377 | PASS | 1276.997 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 9.1773 | PASS | 1.3749 | PASS | 1274.8699 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1245.9891 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0318 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0318 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 3.5948 | FAIL | 24.4728 | PASS | 24372.8452 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 6.4309 | PASS | 6.1517 | PASS | 6051.6976 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 6.4309 | PASS | 1.7199 | PASS | 1619.9198 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 6.5163 | PASS | 0.041047 | FAIL | -58.9534 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4246 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3441 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9716 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8441 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9658 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0085 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0085 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 3.5962 | FAIL | 24.4732 | PASS | 24373.2116 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 6.4381 | PASS | 6.1504 | PASS | 6050.4291 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.7247 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1771 | PASS | 1.3774 | PASS | 1277.4033 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1771 | PASS | 1.377 | PASS | 1277.0317 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1771 | PASS | 1.3749 | PASS | 1274.905 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1246.0205 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1771 | PASS | 1.3461 | PASS | 1246.0632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1771 | PASS | 1.3461 | PASS | 1246.0632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 3.1899 | FAIL | 22.0386 | PASS | 21938.5865 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 4.4801 | FAIL | 4.5613 | PASS | 4461.2594 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 4.4801 | FAIL | 1.731 | PASS | 1630.9586 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 6.5119 | PASS | 0.041052 | FAIL | -58.9484 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 6.5119 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3538 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9814 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8541 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9749 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0176 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0176 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.888 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 6.4379 | PASS | 6.1492 | PASS | 6049.2209 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.648 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 6.5219 | PASS | 0.04105 | FAIL | -58.9496 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 6.5219 | PASS | 0.059585 | FAIL | -40.4145 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 9.1728 | PASS | 1.3775 | PASS | 1277.4788 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 9.1728 | PASS | 1.3771 | PASS | 1277.1081 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 9.1728 | PASS | 1.375 | PASS | 1274.9824 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 9.1728 | PASS | 1.3461 | PASS | 1246.0907 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 9.1728 | PASS | 1.3461 | PASS | 1246.1335 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 9.1728 | PASS | 1.3461 | PASS | 1246.1335 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 3.5947 | FAIL | 24.4698 | PASS | 24369.7545 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 6.4315 | PASS | 6.1505 | PASS | 6050.4612 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 6.4315 | PASS | 1.7196 | PASS | 1619.6098 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 5.882 | FAIL | 0.04159 | FAIL | -58.4105 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 5.882 | FAIL | 0.060091 | FAIL | -39.9088 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.178 | PASS | 1.3774 | PASS | 1277.3538 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.178 | PASS | 1.377 | PASS | 1276.9815 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.178 | PASS | 1.3749 | PASS | 1274.8541 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.178 | PASS | 1.346 | PASS | 1245.9749 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.178 | PASS | 1.346 | PASS | 1246.0176 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.178 | PASS | 1.346 | PASS | 1246.0176 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.912 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.2373 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.438 | PASS | 1.7197 | PASS | 1619.6501 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.5262 | PASS | 0.041044 | FAIL | -58.9557 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.5262 | PASS | 0.059585 | FAIL | -40.4149 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1752 | PASS | 1.3773 | PASS | 1277.284 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1752 | PASS | 1.3769 | PASS | 1276.9106 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1752 | PASS | 1.3748 | PASS | 1274.7822 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1752 | PASS | 1.3459 | PASS | 1245.9111 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1752 | PASS | 1.346 | PASS | 1245.9538 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 9.1752 | PASS | 1.346 | PASS | 1245.9538 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.9619 | FAIL | 23.1426 | PASS | 23042.6375 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 3.7436 | FAIL | 5.3495 | PASS | 5249.4657 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 3.7436 | FAIL | 1.8187 | PASS | 1718.6957 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 6.5169 | PASS | 0.041048 | FAIL | -58.9522 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4247 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1688 | PASS | 1.3774 | PASS | 1277.381 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1688 | PASS | 1.377 | PASS | 1277.0089 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1688 | PASS | 1.3749 | PASS | 1274.8818 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1688 | PASS | 1.346 | PASS | 1246.001 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1688 | PASS | 1.346 | PASS | 1246.0438 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1688 | PASS | 1.346 | PASS | 1246.0438 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.5961 | FAIL | 24.4726 | PASS | 24372.6407 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.4368 | PASS | 6.1491 | PASS | 6049.149 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.4368 | PASS | 1.7198 | PASS | 1619.7784 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 5.1345 | FAIL | 0.042594 | FAIL | -57.4055 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 5.1345 | FAIL | 0.06084 | FAIL | -39.1603 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1738 | PASS | 1.3775 | PASS | 1277.4572 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1738 | PASS | 1.3771 | PASS | 1277.0862 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1738 | PASS | 1.375 | PASS | 1274.9601 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1738 | PASS | 1.3461 | PASS | 1246.071 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1738 | PASS | 1.3461 | PASS | 1246.1138 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1738 | PASS | 1.3461 | PASS | 1246.1138 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.5881 | FAIL | 24.4663 | PASS | 24366.2504 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.3882 | PASS | 6.1427 | PASS | 6042.664 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.3882 | PASS | 1.72 | PASS | 1620.0295 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.0638 | PASS | 0.041734 | FAIL | -58.2661 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.0638 | PASS | 0.060191 | FAIL | -39.809 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1541 | PASS | 1.3774 | PASS | 1277.4045 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1541 | PASS | 1.377 | PASS | 1277.0325 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1541 | PASS | 1.3749 | PASS | 1274.9052 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1541 | PASS | 1.346 | PASS | 1246.0255 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1541 | PASS | 1.3461 | PASS | 1246.0683 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.1541 | PASS | 1.3461 | PASS | 1246.0683 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.5951 | FAIL | 24.4694 | PASS | 24369.4429 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.4345 | PASS | 6.1502 | PASS | 6050.2042 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.4345 | PASS | 1.7196 | PASS | 1619.5515 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 4.849 | FAIL | 0.043007 | FAIL | -56.9934 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 4.849 | FAIL | 0.061108 | FAIL | -38.892 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 9.1783 | PASS | 1.3773 | PASS | 1277.3399 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 9.1783 | PASS | 1.377 | PASS | 1276.9674 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 9.1783 | PASS | 1.3748 | PASS | 1274.8398 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9624 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1246.005 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1246.005 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 3.5963 | FAIL | 24.4718 | PASS | 24371.82 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 31.9291 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 31.9291 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 6.4386 | PASS | 6.1488 | PASS | 6048.7749 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 6.4386 | PASS | 1.7197 | PASS | 1619.6664 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 6.5249 | PASS | 0.041226 | FAIL | -58.7741 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 6.5249 | PASS | 0.059742 | FAIL | -40.2579 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 9.1794 | PASS | 1.3773 | PASS | 1277.3055 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 9.1794 | PASS | 1.3769 | PASS | 1276.9325 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 9.1794 | PASS | 1.3748 | PASS | 1274.8045 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 9.1794 | PASS | 1.3459 | PASS | 1245.9302 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 9.1794 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 9.1794 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 3.5966 | FAIL | 24.4729 | PASS | 24372.8742 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 6.4396 | PASS | 6.1487 | PASS | 6048.7327 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 6.4396 | PASS | 1.7197 | PASS | 1619.6837 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 6.5252 | PASS | 0.041019 | FAIL | -58.9813 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 6.5252 | PASS | 0.059581 | FAIL | -40.4192 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 9.1757 | PASS | 1.3775 | PASS | 1277.5415 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 9.1757 | PASS | 1.3772 | PASS | 1277.1718 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 9.1757 | PASS | 1.375 | PASS | 1275.047 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 9.1757 | PASS | 1.3461 | PASS | 1246.148 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 9.1757 | PASS | 1.3462 | PASS | 1246.1909 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 9.1757 | PASS | 1.3462 | PASS | 1246.1909 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 3.5951 | FAIL | 24.4695 | PASS | 24369.4866 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 31.8158 | PASS | 0.72355 | PASS | 623.5544 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 31.8158 | PASS | 0.72355 | PASS | 623.5544 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 6.4342 | PASS | 6.1506 | PASS | 6050.6191 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 6.4342 | PASS | 1.7196 | PASS | 1619.5603 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 6.5157 | PASS | 0.041044 | FAIL | -58.9558 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 6.5157 | PASS | 0.059577 | FAIL | -40.4228 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 9.1785 | PASS | 1.3773 | PASS | 1277.2801 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 9.1785 | PASS | 1.3769 | PASS | 1276.9067 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 9.1785 | PASS | 1.3748 | PASS | 1274.7784 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 9.1785 | PASS | 1.3459 | PASS | 1245.9069 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 9.1785 | PASS | 1.3459 | PASS | 1245.9495 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 9.1785 | PASS | 1.3459 | PASS | 1245.9495 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 3.5965 | FAIL | 24.4726 | PASS | 24372.6163 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 31.9301 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 31.9301 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 6.4393 | PASS | 6.1487 | PASS | 6048.734 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 6.4393 | PASS | 1.7197 | PASS | 1619.6746 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 6.517 | PASS | 0.041048 | FAIL | -58.9521 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 6.517 | PASS | 0.059574 | FAIL | -40.4258 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 9.1804 | PASS | 1.3771 | PASS | 1277.1109 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 9.1804 | PASS | 1.3767 | PASS | 1276.7351 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 9.1804 | PASS | 1.3746 | PASS | 1274.6045 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 9.1804 | PASS | 1.3458 | PASS | 1245.7507 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 9.1804 | PASS | 1.3458 | PASS | 1245.7932 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 9.1804 | PASS | 1.3458 | PASS | 1245.7932 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 3.5973 | FAIL | 24.4744 | PASS | 24374.4395 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 31.9376 | PASS | 0.72357 | PASS | 623.5687 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 31.9376 | PASS | 0.72357 | PASS | 623.5687 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 6.4422 | PASS | 6.1476 | PASS | 6047.6242 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 6.4422 | PASS | 1.7197 | PASS | 1619.7413 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 6.5178 | PASS | 0.04105 | FAIL | -58.9499 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 6.5178 | PASS | 0.059572 | FAIL | -40.4276 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8847 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 31.9281 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 31.9281 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.18 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645558 [S3458-HOLT 3345.00] CKT 1 |  | FAIL |  | FAIL |  | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.877 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 26.6867 | PASS | 0.72292 | PASS | 622.9165 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 26.6867 | PASS | 0.72292 | PASS | 622.9165 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.181 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3513 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9789 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8845 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 31.3802 | PASS | 0.72351 | PASS | 623.512 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 31.3802 | PASS | 0.72351 | PASS | 623.512 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1794 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8851 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 31.9267 | PASS | 0.72357 | PASS | 623.5659 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 31.9267 | PASS | 0.72357 | PASS | 623.5659 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1815 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8766 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 30.0088 | PASS | 0.72335 | PASS | 623.3517 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 30.0088 | PASS | 0.72335 | PASS | 623.3517 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1799 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3513 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.979 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8769 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 28.3866 | PASS | 0.72313 | PASS | 623.1276 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 28.3866 | PASS | 0.72313 | PASS | 623.1276 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1816 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8849 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 31.9236 | PASS | 0.72357 | PASS | 623.5657 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 31.9236 | PASS | 0.72357 | PASS | 623.5657 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1813 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 31.751 | PASS | 0.72355 | PASS | 623.5492 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 31.751 | PASS | 0.72355 | PASS | 623.5492 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1813 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 31.9176 | PASS | 0.72356 | PASS | 623.5647 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 31.9176 | PASS | 0.72356 | PASS | 623.5647 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1811 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 31.9111 | PASS | 0.72356 | PASS | 623.5636 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 31.9111 | PASS | 0.72356 | PASS | 623.5636 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1811 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9795 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8521 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.973 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8767 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1822 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6475 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.1778 | PASS | 1.3773 | PASS | 1277.3491 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9767 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.1778 | PASS | 1.3748 | PASS | 1274.8492 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9705 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0132 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0132 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9132 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1624 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6488 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3503 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9779 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8505 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9716 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0143 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0143 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8915 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1724 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6479 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.3566 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9843 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.857 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9774 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0201 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0201 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 3.596 | FAIL | 24.4717 | PASS | 24371.6578 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 6.4377 | PASS | 6.1493 | PASS | 6049.2715 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 6.4377 | PASS | 1.7196 | PASS | 1619.6399 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.3644 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9922 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.865 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9846 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0273 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0273 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.7836 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 6.4379 | PASS | 6.1492 | PASS | 6049.2421 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.644 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.1772 | PASS | 1.3774 | PASS | 1277.3757 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.1772 | PASS | 1.377 | PASS | 1277.0037 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.1772 | PASS | 1.3749 | PASS | 1274.8766 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1245.995 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1246.0378 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1246.0378 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 3.596 | FAIL | 24.4717 | PASS | 24371.6764 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 31.923 | PASS | 0.72357 | PASS | 623.5655 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 31.923 | PASS | 0.72357 | PASS | 623.5655 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.4375 | PASS | 6.1492 | PASS | 6049.1587 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.6426 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.5164 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.5164 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3533 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.981 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8536 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9744 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0171 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0171 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.8781 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1856 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6473 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 9.151 | PASS | 1.3773 | PASS | 1277.3391 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 9.151 | PASS | 1.377 | PASS | 1276.9661 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 9.151 | PASS | 1.3748 | PASS | 1274.8379 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 9.151 | PASS | 1.346 | PASS | 1245.9648 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 9.151 | PASS | 1.346 | PASS | 1246.0074 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 9.151 | PASS | 1.346 | PASS | 1246.0074 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9729 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 6.438 | PASS | 6.1491 | PASS | 6049.0826 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 6.438 | PASS | 1.7197 | PASS | 1619.653 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 6.5163 | PASS | 0.041048 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659135 [STEGALL_-MB3345.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 9.1547 | PASS | 1.3776 | PASS | 1277.6227 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 9.1547 | PASS | 1.3773 | PASS | 1277.2537 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 9.1547 | PASS | 1.3751 | PASS | 1275.1293 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 9.1547 | PASS | 1.3462 | PASS | 1246.2277 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 9.1547 | PASS | 1.3463 | PASS | 1246.2706 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 9.1547 | PASS | 1.3463 | PASS | 1246.2706 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 3.596 | FAIL | 24.4714 | PASS | 24371.3917 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 31.9288 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 31.9288 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 6.4374 | PASS | 6.1493 | PASS | 6049.3438 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 6.4374 | PASS | 1.7196 | PASS | 1619.6294 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 6.5155 | PASS | 0.041044 | FAIL | -58.9563 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659425 [SD.LS-KS-MB3345.00] CKT Z | 6.5155 | PASS | 0.059578 | FAIL | -40.4223 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 9.1528 | PASS | 1.3774 | PASS | 1277.3843 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 9.1528 | PASS | 1.377 | PASS | 1277.012 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 9.1528 | PASS | 1.3749 | PASS | 1274.8845 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 9.1528 | PASS | 1.346 | PASS | 1246.0062 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 9.1528 | PASS | 1.346 | PASS | 1246.0488 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 9.1528 | PASS | 1.346 | PASS | 1246.0488 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 3.5962 | FAIL | 24.472 | PASS | 24371.9941 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 31.9287 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 31.9287 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 6.4381 | PASS | 6.1491 | PASS | 6049.0694 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 6.4381 | PASS | 1.7197 | PASS | 1619.6537 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 6.5163 | PASS | 0.041048 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659426 [SD.LS-LR-MB3345.00] CKT Z | 6.5163 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3569 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9846 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8573 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9777 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0204 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0204 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 3.5961 | FAIL | 24.4716 | PASS | 24371.6236 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 31.9296 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 31.9296 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.4378 | PASS | 6.1492 | PASS | 6049.1776 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.4378 | PASS | 1.7196 | PASS | 1619.6434 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.1685 | PASS | 1.3778 | PASS | 1277.8342 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.1685 | PASS | 1.3775 | PASS | 1277.4688 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.1685 | PASS | 1.3753 | PASS | 1275.3479 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.1685 | PASS | 1.3464 | PASS | 1246.4181 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.1685 | PASS | 1.3465 | PASS | 1246.4613 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.1685 | PASS | 1.3465 | PASS | 1246.4613 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 3.5935 | FAIL | 24.4656 | PASS | 24365.6304 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 31.9215 | PASS | 0.72356 | PASS | 623.5645 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 31.9215 | PASS | 0.72356 | PASS | 623.5645 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 6.4257 | PASS | 6.1483 | PASS | 6048.2906 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 6.4257 | PASS | 1.7195 | PASS | 1619.5173 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 6.5098 | PASS | 0.04104 | FAIL | -58.9597 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 6.5098 | PASS | 0.059582 | FAIL | -40.4184 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.3633 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9911 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.8639 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9836 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0264 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0264 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 3.596 | FAIL | 24.4713 | PASS | 24371.3214 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 31.9291 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 31.9291 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 6.4376 | PASS | 6.1491 | PASS | 6049.0651 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 6.4376 | PASS | 1.7196 | PASS | 1619.6368 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 9.1774 | PASS | 1.3774 | PASS | 1277.3787 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 9.1774 | PASS | 1.377 | PASS | 1277.0068 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 9.1774 | PASS | 1.3749 | PASS | 1274.8798 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 9.1774 | PASS | 1.346 | PASS | 1245.9978 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 9.1774 | PASS | 1.346 | PASS | 1246.0405 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 9.1774 | PASS | 1.346 | PASS | 1246.0405 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 3.596 | FAIL | 24.4716 | PASS | 24371.5588 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 6.4374 | PASS | 6.1494 | PASS | 6049.3586 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 6.4374 | PASS | 1.7196 | PASS | 1619.6379 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 6.5165 | PASS | 0.041046 | FAIL | -58.9536 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 6.5165 | PASS | 0.059575 | FAIL | -40.4246 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.181 | PASS | 1.3775 | PASS | 1277.4818 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.181 | PASS | 1.3771 | PASS | 1277.1056 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.181 | PASS | 1.375 | PASS | 1274.9721 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.181 | PASS | 1.3461 | PASS | 1246.1398 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.181 | PASS | 1.3462 | PASS | 1246.1822 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.181 | PASS | 1.3462 | PASS | 1246.1822 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 3.5966 | FAIL | 24.4728 | PASS | 24372.804 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 6.4396 | PASS | 6.1486 | PASS | 6048.5936 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 6.4396 | PASS | 1.7197 | PASS | 1619.6892 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 6.5179 | PASS | 0.041051 | FAIL | -58.9485 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 6.5179 | PASS | 0.059573 | FAIL | -40.4268 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.1804 | PASS | 1.3775 | PASS | 1277.4719 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.1804 | PASS | 1.3771 | PASS | 1277.0954 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.1804 | PASS | 1.375 | PASS | 1274.9617 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.1804 | PASS | 1.3461 | PASS | 1246.1319 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.1804 | PASS | 1.3462 | PASS | 1246.1742 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.1804 | PASS | 1.3462 | PASS | 1246.1742 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 3.5966 | FAIL | 24.4728 | PASS | 24372.8037 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 31.9292 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 31.9292 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 6.4396 | PASS | 6.1486 | PASS | 6048.5956 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 6.4396 | PASS | 1.7197 | PASS | 1619.6895 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 6.5179 | PASS | 0.041052 | FAIL | -58.9485 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 6.5179 | PASS | 0.059573 | FAIL | -40.4268 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.3905 | PASS | 1.3795 | PASS | 1279.5303 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.3905 | PASS | 1.3792 | PASS | 1279.1759 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.3905 | PASS | 1.3771 | PASS | 1277.0579 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.3905 | PASS | 1.3481 | PASS | 1248.1057 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.3905 | PASS | 1.3481 | PASS | 1248.1495 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.3905 | PASS | 1.3481 | PASS | 1248.1495 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 3.5803 | FAIL | 24.4362 | PASS | 24336.1555 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 31.9243 | PASS | 0.72356 | PASS | 623.5648 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 31.9243 | PASS | 0.72356 | PASS | 623.5648 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 6.3822 | PASS | 6.1683 | PASS | 6068.2965 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 6.3822 | PASS | 1.7183 | PASS | 1618.3238 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 6.4585 | PASS | 0.040998 | FAIL | -59.0017 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 6.4585 | PASS | 0.059665 | FAIL | -40.3354 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 9.1674 | PASS | 1.3776 | PASS | 1277.6363 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 9.1674 | PASS | 1.3773 | PASS | 1277.2679 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 9.1674 | PASS | 1.3751 | PASS | 1275.1437 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 9.1674 | PASS | 1.3462 | PASS | 1246.2404 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 9.1674 | PASS | 1.3463 | PASS | 1246.2833 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 9.1674 | PASS | 1.3463 | PASS | 1246.2833 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 3.5956 | FAIL | 24.4706 | PASS | 24370.5944 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 6.4361 | PASS | 6.1498 | PASS | 6049.8136 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 6.4361 | PASS | 1.7196 | PASS | 1619.6 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 6.4717 | PASS | 0.041071 | FAIL | -58.929 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 6.4717 | PASS | 0.059603 | FAIL | -40.3966 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 9.1813 | PASS | 1.3784 | PASS | 1278.4423 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 9.1813 | PASS | 1.3781 | PASS | 1278.0844 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 9.1813 | PASS | 1.376 | PASS | 1275.9704 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 9.1813 | PASS | 1.347 | PASS | 1246.9874 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 9.1813 | PASS | 1.347 | PASS | 1247.0311 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 9.1813 | PASS | 1.347 | PASS | 1247.0311 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 3.5966 | FAIL | 24.4729 | PASS | 24372.8953 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 31.9303 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 31.9303 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 6.4398 | PASS | 6.1486 | PASS | 6048.5679 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 6.4398 | PASS | 1.7197 | PASS | 1619.6882 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 6.5178 | PASS | 0.041048 | FAIL | -58.9516 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 6.5178 | PASS | 0.059575 | FAIL | -40.4247 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3629 | PASS | 1.38 | PASS | 1280.0222 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3629 | PASS | 1.3797 | PASS | 1279.6535 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3629 | PASS | 1.3775 | PASS | 1277.5099 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3629 | PASS | 1.3488 | PASS | 1248.7595 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3629 | PASS | 1.3488 | PASS | 1248.802 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3629 | PASS | 1.3488 | PASS | 1248.802 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.5897 | FAIL | 24.4576 | PASS | 24357.6306 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9261 | PASS | 0.72357 | PASS | 623.5654 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9261 | PASS | 0.72357 | PASS | 623.5654 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4155 | PASS | 6.157 | PASS | 6057.0291 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4155 | PASS | 1.7191 | PASS | 1619.1414 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.5055 | PASS | 0.041018 | FAIL | -58.9816 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.5055 | PASS | 0.059602 | FAIL | -40.3977 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 9.1748 | PASS | 1.3774 | PASS | 1277.4188 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 9.1748 | PASS | 1.377 | PASS | 1277.0473 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 9.1748 | PASS | 1.3749 | PASS | 1274.9209 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 9.1748 | PASS | 1.346 | PASS | 1246.0348 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 9.1748 | PASS | 1.3461 | PASS | 1246.0776 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 9.1748 | PASS | 1.3461 | PASS | 1246.0776 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 3.2677 | FAIL | 23.6694 | PASS | 23569.3909 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 4.817 | FAIL | 5.5978 | PASS | 5497.7626 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 4.817 | FAIL | 1.7808 | PASS | 1680.7938 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 6.5092 | PASS | 0.041042 | FAIL | -58.9578 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 6.5092 | PASS | 0.05958 | FAIL | -40.4195 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.175 | PASS | 1.3774 | PASS | 1277.4089 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.175 | PASS | 1.377 | PASS | 1277.0374 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.175 | PASS | 1.3749 | PASS | 1274.9107 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0257 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.175 | PASS | 1.3461 | PASS | 1246.0685 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.175 | PASS | 1.3461 | PASS | 1246.0685 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 3.2725 | FAIL | 23.4677 | PASS | 23367.7295 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 4.8365 | FAIL | 5.4402 | PASS | 5340.2065 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 4.8365 | FAIL | 1.7696 | PASS | 1669.5751 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 6.5097 | PASS | 0.041043 | FAIL | -58.9569 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 6.5097 | PASS | 0.05958 | FAIL | -40.4203 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 9.1762 | PASS | 1.3774 | PASS | 1277.3533 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 9.1762 | PASS | 1.377 | PASS | 1276.9809 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 9.1762 | PASS | 1.3749 | PASS | 1274.8535 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 9.1762 | PASS | 1.346 | PASS | 1245.975 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 9.1762 | PASS | 1.346 | PASS | 1246.0177 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 9.1762 | PASS | 1.346 | PASS | 1246.0177 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9276 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1604 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6504 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 9.1386 | PASS | 1.3777 | PASS | 1277.7072 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 9.1386 | PASS | 1.3773 | PASS | 1277.339 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 9.1386 | PASS | 1.3752 | PASS | 1275.2151 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 9.1386 | PASS | 1.3463 | PASS | 1246.3091 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 9.1386 | PASS | 1.3464 | PASS | 1246.3521 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 9.1386 | PASS | 1.3464 | PASS | 1246.3521 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 3.596 | FAIL | 24.4716 | PASS | 24371.6049 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 6.4375 | PASS | 6.1494 | PASS | 6049.353 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.6377 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 6.5079 | PASS | 0.041058 | FAIL | -58.942 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 6.5079 | PASS | 0.059577 | FAIL | -40.4227 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 9.1778 | PASS | 1.3776 | PASS | 1277.6003 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 9.1778 | PASS | 1.3772 | PASS | 1277.2315 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 9.1778 | PASS | 1.3751 | PASS | 1275.1074 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 9.1778 | PASS | 1.3462 | PASS | 1246.2031 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 9.1778 | PASS | 1.3462 | PASS | 1246.246 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 9.1778 | PASS | 1.3462 | PASS | 1246.246 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 3.5959 | FAIL | 24.4715 | PASS | 24371.5379 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 6.4373 | PASS | 6.1494 | PASS | 6049.3707 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 6.4373 | PASS | 1.7196 | PASS | 1619.6349 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 6.5158 | PASS | 0.041045 | FAIL | -58.9553 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 6.5158 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 9.168 | PASS | 1.3775 | PASS | 1277.4881 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 9.168 | PASS | 1.3771 | PASS | 1277.1174 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 9.168 | PASS | 1.375 | PASS | 1274.9915 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 9.168 | PASS | 1.3461 | PASS | 1246.1009 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 9.168 | PASS | 1.3461 | PASS | 1246.1437 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 9.168 | PASS | 1.3461 | PASS | 1246.1437 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 3.5959 | FAIL | 24.4717 | PASS | 24371.6692 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 6.4375 | PASS | 6.1493 | PASS | 6049.3089 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.6399 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 6.516 | PASS | 0.041048 | FAIL | -58.9521 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 6.516 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 9.1773 | PASS | 1.3775 | PASS | 1277.476 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 9.1773 | PASS | 1.3771 | PASS | 1277.1054 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 9.1773 | PASS | 1.375 | PASS | 1274.9798 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 9.1773 | PASS | 1.3461 | PASS | 1246.0878 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 9.1773 | PASS | 1.3461 | PASS | 1246.1306 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 9.1773 | PASS | 1.3461 | PASS | 1246.1306 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9555 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.1338 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6519 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9534 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 9.047 | PASS | 1.3775 | PASS | 1277.4615 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 9.047 | PASS | 1.3771 | PASS | 1277.0884 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 9.047 | PASS | 1.375 | PASS | 1274.9598 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 9.047 | PASS | 1.3461 | PASS | 1246.0878 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 9.047 | PASS | 1.3461 | PASS | 1246.1304 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 9.047 | PASS | 1.3461 | PASS | 1246.1304 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 3.5966 | FAIL | 24.4731 | PASS | 24373.1309 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 6.4396 | PASS | 6.1484 | PASS | 6048.3613 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 6.4396 | PASS | 1.7197 | PASS | 1619.7014 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 6.5152 | PASS | 0.041052 | FAIL | -58.9477 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 6.5152 | PASS | 0.059572 | FAIL | -40.4278 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3668 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9946 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8674 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9867 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0294 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0294 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8768 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1786 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6475 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 9.1712 | PASS | 1.3774 | PASS | 1277.4049 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 9.1712 | PASS | 1.377 | PASS | 1277.0332 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 9.1712 | PASS | 1.3749 | PASS | 1274.9065 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 9.1712 | PASS | 1.346 | PASS | 1246.0223 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 9.1712 | PASS | 1.3461 | PASS | 1246.065 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 9.1712 | PASS | 1.3461 | PASS | 1246.065 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8928 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 6.4379 | PASS | 6.1491 | PASS | 6049.1338 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 6.4379 | PASS | 1.7197 | PASS | 1619.6526 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 9.175 | PASS | 1.3774 | PASS | 1277.3836 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 9.175 | PASS | 1.377 | PASS | 1277.0116 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 9.175 | PASS | 1.3749 | PASS | 1274.8845 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0038 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0465 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0465 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 3.5959 | FAIL | 24.4716 | PASS | 24371.5985 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 6.4374 | PASS | 6.1494 | PASS | 6049.3584 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 6.4374 | PASS | 1.7196 | PASS | 1619.6371 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 6.5162 | PASS | 0.041046 | FAIL | -58.954 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 6.5162 | PASS | 0.059576 | FAIL | -40.4243 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 9.175 | PASS | 1.3774 | PASS | 1277.3836 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 9.175 | PASS | 1.377 | PASS | 1277.0116 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 9.175 | PASS | 1.3749 | PASS | 1274.8845 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0038 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0465 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 9.175 | PASS | 1.346 | PASS | 1246.0465 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 3.5959 | FAIL | 24.4716 | PASS | 24371.5985 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 6.4374 | PASS | 6.1494 | PASS | 6049.3584 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 6.4374 | PASS | 1.7196 | PASS | 1619.6371 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 6.5162 | PASS | 0.041046 | FAIL | -58.954 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 6.5162 | PASS | 0.059576 | FAIL | -40.4243 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 9.1765 | PASS | 1.3773 | PASS | 1277.3408 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 9.1765 | PASS | 1.377 | PASS | 1276.9683 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 9.1765 | PASS | 1.3748 | PASS | 1274.8407 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 9.1765 | PASS | 1.346 | PASS | 1245.9635 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 9.1765 | PASS | 1.346 | PASS | 1246.0062 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 9.1765 | PASS | 1.346 | PASS | 1246.0062 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.784 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 6.4378 | PASS | 6.1492 | PASS | 6049.2423 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 6.4378 | PASS | 1.7196 | PASS | 1619.6441 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9533 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 8.5767 | PASS | 1.3758 | PASS | 1275.7914 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 8.5767 | PASS | 1.3754 | PASS | 1275.3844 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 8.5767 | PASS | 1.3732 | PASS | 1273.2224 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 8.5767 | PASS | 1.3446 | PASS | 1244.6047 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 8.5767 | PASS | 1.3446 | PASS | 1244.6449 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 8.5767 | PASS | 1.3446 | PASS | 1244.6449 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 3.599 | FAIL | 24.4789 | PASS | 24378.8857 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 31.9333 | PASS | 0.72357 | PASS | 623.5678 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 31.9333 | PASS | 0.72357 | PASS | 623.5678 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 6.447 | PASS | 6.145 | PASS | 6045.0326 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 6.447 | PASS | 1.7199 | PASS | 1619.9338 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 6.5106 | PASS | 0.041079 | FAIL | -58.9212 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 6.5106 | PASS | 0.059559 | FAIL | -40.4414 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 8.2855 | PASS | 1.3778 | PASS | 1277.7964 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 8.2855 | PASS | 1.3774 | PASS | 1277.4107 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 8.2855 | PASS | 1.3753 | PASS | 1275.2616 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 8.2855 | PASS | 1.3465 | PASS | 1246.5485 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 8.2855 | PASS | 1.3466 | PASS | 1246.59 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 8.2855 | PASS | 1.3466 | PASS | 1246.59 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 3.5957 | FAIL | 24.4711 | PASS | 24371.1374 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 6.4362 | PASS | 6.1493 | PASS | 6049.261 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 6.4362 | PASS | 1.7196 | PASS | 1619.6263 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 6.511 | PASS | 0.041041 | FAIL | -58.9588 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 6.511 | PASS | 0.05958 | FAIL | -40.4197 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 9.2023 | PASS | 1.3764 | PASS | 1276.4247 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 9.2023 | PASS | 1.376 | PASS | 1276.0363 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 9.2023 | PASS | 1.3739 | PASS | 1273.8932 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 9.2023 | PASS | 1.3451 | PASS | 1245.1349 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 9.2023 | PASS | 1.3452 | PASS | 1245.1765 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 9.2023 | PASS | 1.3452 | PASS | 1245.1765 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 3.5975 | FAIL | 24.4746 | PASS | 24374.6344 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 31.9302 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 31.9302 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 6.4428 | PASS | 6.1473 | PASS | 6047.34 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 6.4428 | PASS | 1.7198 | PASS | 1619.7734 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 6.5196 | PASS | 0.041055 | FAIL | -58.9446 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 6.5196 | PASS | 0.05957 | FAIL | -40.4304 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 8.6475 | PASS | 1.3793 | PASS | 1279.3145 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 8.6475 | PASS | 1.379 | PASS | 1278.9633 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 8.6475 | PASS | 1.3769 | PASS | 1276.8529 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 8.6475 | PASS | 1.3478 | PASS | 1247.8408 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 8.6475 | PASS | 1.3479 | PASS | 1247.8849 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 8.6475 | PASS | 1.3479 | PASS | 1247.8849 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 3.5931 | FAIL | 24.4662 | PASS | 24366.2353 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.426 | PASS | 6.1519 | PASS | 6051.932 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.426 | PASS | 1.7195 | PASS | 1619.485 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.5021 | PASS | 0.041033 | FAIL | -58.9669 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.5021 | PASS | 0.05959 | FAIL | -40.4101 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 9.1685 | PASS | 1.3773 | PASS | 1277.3275 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 9.1685 | PASS | 1.377 | PASS | 1276.9547 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 9.1685 | PASS | 1.3748 | PASS | 1274.8267 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 9.1685 | PASS | 1.346 | PASS | 1245.9518 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 9.1685 | PASS | 1.346 | PASS | 1245.9945 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 9.1685 | PASS | 1.346 | PASS | 1245.9945 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 3.5961 | FAIL | 24.472 | PASS | 24372.0323 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 6.4378 | PASS | 6.149 | PASS | 6048.9923 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 6.4378 | PASS | 1.7197 | PASS | 1619.6711 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 9.1747 | PASS | 1.3774 | PASS | 1277.3655 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 9.1747 | PASS | 1.377 | PASS | 1276.9933 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 9.1747 | PASS | 1.3749 | PASS | 1274.8659 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 9.1747 | PASS | 1.346 | PASS | 1245.9868 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 9.1747 | PASS | 1.346 | PASS | 1246.0294 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 9.1747 | PASS | 1.346 | PASS | 1246.0294 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.8393 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 6.4375 | PASS | 6.149 | PASS | 6049.0028 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 6.4375 | PASS | 1.7197 | PASS | 1619.671 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 9.1307 | PASS | 1.3774 | PASS | 1277.4145 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 9.1307 | PASS | 1.377 | PASS | 1277.0423 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 9.1307 | PASS | 1.3749 | PASS | 1274.9144 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 9.1307 | PASS | 1.346 | PASS | 1246.0394 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 9.1307 | PASS | 1.3461 | PASS | 1246.0821 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 9.1307 | PASS | 1.3461 | PASS | 1246.0821 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 3.5949 | FAIL | 24.4712 | PASS | 24371.1625 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 6.4328 | PASS | 6.1494 | PASS | 6049.4236 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 6.4328 | PASS | 1.7198 | PASS | 1619.7998 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 6.5164 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 6.5164 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 9.1692 | PASS | 1.3775 | PASS | 1277.5045 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 9.1692 | PASS | 1.3771 | PASS | 1277.1336 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 9.1692 | PASS | 1.375 | PASS | 1275.0072 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 9.1692 | PASS | 1.3461 | PASS | 1246.1204 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 9.1692 | PASS | 1.3462 | PASS | 1246.1632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 9.1692 | PASS | 1.3462 | PASS | 1246.1632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8533 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 6.4378 | PASS | 6.1494 | PASS | 6049.3734 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 6.4378 | PASS | 1.7197 | PASS | 1619.6557 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.115 | PASS | 1.3776 | PASS | 1277.5623 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.115 | PASS | 1.3772 | PASS | 1277.1913 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.115 | PASS | 1.3751 | PASS | 1275.0638 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.115 | PASS | 1.3462 | PASS | 1246.1869 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.115 | PASS | 1.3462 | PASS | 1246.2296 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.115 | PASS | 1.3462 | PASS | 1246.2296 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 3.5957 | FAIL | 24.4717 | PASS | 24371.6938 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.4353 | PASS | 6.149 | PASS | 6048.9875 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.4353 | PASS | 1.7197 | PASS | 1619.7387 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.4522 | PASS | 1.3803 | PASS | 1280.3025 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.4522 | PASS | 1.38 | PASS | 1279.9536 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.4522 | PASS | 1.3778 | PASS | 1277.8368 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.4522 | PASS | 1.3489 | PASS | 1248.878 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.4522 | PASS | 1.3489 | PASS | 1248.9221 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.4522 | PASS | 1.3489 | PASS | 1248.9221 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.5962 | FAIL | 24.4722 | PASS | 24372.1879 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4376 | PASS | 6.1484 | PASS | 6048.3531 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4376 | PASS | 1.7197 | PASS | 1619.7122 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.5115 | PASS | 0.041041 | FAIL | -58.9591 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.5115 | PASS | 0.059582 | FAIL | -40.4177 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 9.0462 | PASS | 1.3779 | PASS | 1277.9372 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 9.0462 | PASS | 1.3776 | PASS | 1277.5716 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 9.0462 | PASS | 1.3754 | PASS | 1275.4494 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 9.0462 | PASS | 1.3465 | PASS | 1246.5297 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 9.0462 | PASS | 1.3466 | PASS | 1246.5728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 9.0462 | PASS | 1.3466 | PASS | 1246.5728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.909 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 6.4368 | PASS | 6.1475 | PASS | 6047.4645 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 6.4368 | PASS | 1.7197 | PASS | 1619.7391 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 6.4137 | PASS | 0.041094 | FAIL | -58.9057 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 6.4137 | PASS | 0.059629 | FAIL | -40.3712 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.1264 | PASS | 1.3775 | PASS | 1277.5086 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.1264 | PASS | 1.3771 | PASS | 1277.1368 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.1264 | PASS | 1.375 | PASS | 1275.0092 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.1264 | PASS | 1.3461 | PASS | 1246.1316 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.1264 | PASS | 1.3462 | PASS | 1246.1744 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.1264 | PASS | 1.3462 | PASS | 1246.1744 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 3.5959 | FAIL | 24.4719 | PASS | 24371.8668 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.4374 | PASS | 6.1499 | PASS | 6049.9242 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.4374 | PASS | 1.7197 | PASS | 1619.6728 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.4857 | PASS | 0.041095 | FAIL | -58.9055 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.4857 | PASS | 0.059611 | FAIL | -40.389 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.1075 | PASS | 1.3776 | PASS | 1277.629 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.1075 | PASS | 1.3773 | PASS | 1277.2592 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.1075 | PASS | 1.3751 | PASS | 1275.1335 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.1075 | PASS | 1.3462 | PASS | 1246.2412 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.1075 | PASS | 1.3463 | PASS | 1246.284 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.1075 | PASS | 1.3463 | PASS | 1246.284 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 3.5952 | FAIL | 24.4704 | PASS | 24370.4036 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.4347 | PASS | 6.1509 | PASS | 6050.9114 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.4347 | PASS | 1.7196 | PASS | 1619.6077 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.4735 | PASS | 0.041087 | FAIL | -58.9135 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.4735 | PASS | 0.059609 | FAIL | -40.3914 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 9.154 | PASS | 1.3774 | PASS | 1277.4033 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 9.154 | PASS | 1.377 | PASS | 1277.0312 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 9.154 | PASS | 1.3749 | PASS | 1274.9039 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 9.154 | PASS | 1.346 | PASS | 1246.0244 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 9.154 | PASS | 1.3461 | PASS | 1246.0671 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 9.154 | PASS | 1.3461 | PASS | 1246.0671 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 3.5951 | FAIL | 24.4695 | PASS | 24369.4645 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 6.4345 | PASS | 6.1502 | PASS | 6050.1902 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 6.4345 | PASS | 1.7196 | PASS | 1619.5527 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 4.8464 | FAIL | 0.043012 | FAIL | -56.9882 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 4.8464 | FAIL | 0.061109 | FAIL | -38.8911 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 9.1328 | PASS | 1.3775 | PASS | 1277.5423 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 9.1328 | PASS | 1.3772 | PASS | 1277.1717 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 9.1328 | PASS | 1.375 | PASS | 1275.0455 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 9.1328 | PASS | 1.3462 | PASS | 1246.1575 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 9.1328 | PASS | 1.3462 | PASS | 1246.2003 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 9.1328 | PASS | 1.3462 | PASS | 1246.2003 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 3.5884 | FAIL | 24.4673 | PASS | 24367.3314 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 6.3914 | PASS | 6.147 | PASS | 6047.0412 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 6.3914 | PASS | 1.7208 | PASS | 1620.8162 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 6.125 | PASS | 0.041354 | FAIL | -58.6458 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 6.125 | PASS | 0.059762 | FAIL | -40.2382 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 7.7033 | PASS | 1.3843 | PASS | 1284.29 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 7.7033 | PASS | 1.384 | PASS | 1283.9738 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 7.7033 | PASS | 1.3819 | PASS | 1281.8781 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 7.7033 | PASS | 1.3527 | PASS | 1252.7498 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 7.7033 | PASS | 1.3528 | PASS | 1252.796 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 7.7033 | PASS | 1.3528 | PASS | 1252.796 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.5912 | FAIL | 24.4687 | PASS | 24368.709 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4048 | PASS | 6.142 | PASS | 6042.008 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4048 | PASS | 1.7199 | PASS | 1619.9401 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.2269 | PASS | 0.041167 | FAIL | -58.8331 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.2269 | PASS | 0.059652 | FAIL | -40.348 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.4145 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1277.0431 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.9166 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0309 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 9.1776 | PASS | 1.3461 | PASS | 1246.0736 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 9.1776 | PASS | 1.3461 | PASS | 1246.0736 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 3.5966 | FAIL | 24.473 | PASS | 24372.9549 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 31.9293 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 31.9293 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 6.4397 | PASS | 6.1486 | PASS | 6048.621 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 6.4397 | PASS | 1.7197 | PASS | 1619.6871 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 6.517 | PASS | 0.041048 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 6.517 | PASS | 0.059574 | FAIL | -40.4255 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 9.1777 | PASS | 1.3776 | PASS | 1277.6007 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 9.1777 | PASS | 1.3772 | PASS | 1277.2289 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 9.1777 | PASS | 1.3751 | PASS | 1275.1005 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 9.1777 | PASS | 1.3462 | PASS | 1246.2282 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 9.1777 | PASS | 1.3463 | PASS | 1246.2709 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 9.1777 | PASS | 1.3463 | PASS | 1246.2709 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 3.5966 | FAIL | 24.4722 | PASS | 24372.211 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 6.4395 | PASS | 6.1481 | PASS | 6048.1497 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 6.4395 | PASS | 1.7197 | PASS | 1619.7055 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 6.5171 | PASS | 0.041058 | FAIL | -58.9423 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 6.5171 | PASS | 0.059582 | FAIL | -40.4184 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 9.1716 | PASS | 1.3774 | PASS | 1277.3664 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 9.1716 | PASS | 1.377 | PASS | 1276.9942 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 9.1716 | PASS | 1.3749 | PASS | 1274.867 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 9.1716 | PASS | 1.346 | PASS | 1245.9866 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 9.1716 | PASS | 1.346 | PASS | 1246.0293 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 9.1716 | PASS | 1.346 | PASS | 1246.0293 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 3.5932 | FAIL | 24.4666 | PASS | 24366.6203 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 31.9243 | PASS | 0.72357 | PASS | 623.5659 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 31.9243 | PASS | 0.72357 | PASS | 623.5659 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 6.4215 | PASS | 6.1459 | PASS | 6045.8966 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 6.4215 | PASS | 1.7198 | PASS | 1619.7788 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 6.5122 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 6.5122 | PASS | 0.059576 | FAIL | -40.4241 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 9.1775 | PASS | 1.3773 | PASS | 1277.3454 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 9.1775 | PASS | 1.377 | PASS | 1276.9729 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 9.1775 | PASS | 1.3748 | PASS | 1274.8455 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1245.9671 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1246.0098 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1246.0098 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 3.5943 | FAIL | 24.4684 | PASS | 24368.431 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 31.9269 | PASS | 0.72357 | PASS | 623.5658 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 31.9269 | PASS | 0.72357 | PASS | 623.5658 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 6.428 | PASS | 6.1478 | PASS | 6047.8311 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 6.428 | PASS | 1.7198 | PASS | 1619.7555 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 6.5152 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 6.5152 | PASS | 0.059575 | FAIL | -40.4246 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 9.1725 | PASS | 1.3773 | PASS | 1277.3392 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 9.1725 | PASS | 1.377 | PASS | 1276.9666 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 9.1725 | PASS | 1.3748 | PASS | 1274.839 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 9.1725 | PASS | 1.346 | PASS | 1245.9615 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 9.1725 | PASS | 1.346 | PASS | 1246.0041 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 9.1725 | PASS | 1.346 | PASS | 1246.0041 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 3.5943 | FAIL | 24.4689 | PASS | 24368.8538 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 6.4267 | PASS | 6.1459 | PASS | 6045.8907 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 6.4267 | PASS | 1.7198 | PASS | 1619.7544 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 6.5123 | PASS | 0.041048 | FAIL | -58.9519 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 6.5123 | PASS | 0.059575 | FAIL | -40.4246 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1692 | PASS | 1.3775 | PASS | 1277.4657 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1692 | PASS | 1.3771 | PASS | 1277.095 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1692 | PASS | 1.375 | PASS | 1274.9691 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1692 | PASS | 1.3461 | PASS | 1246.0783 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1692 | PASS | 1.3461 | PASS | 1246.1211 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1692 | PASS | 1.3461 | PASS | 1246.1211 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 3.5949 | FAIL | 24.4691 | PASS | 24369.0609 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 31.9242 | PASS | 0.72356 | PASS | 623.5648 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 31.9242 | PASS | 0.72356 | PASS | 623.5648 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 6.4306 | PASS | 6.1469 | PASS | 6046.9208 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 6.4306 | PASS | 1.7197 | PASS | 1619.6541 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 6.5106 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 6.5106 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.1789 | PASS | 1.3773 | PASS | 1277.3238 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.1789 | PASS | 1.377 | PASS | 1276.951 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.1789 | PASS | 1.3748 | PASS | 1274.8232 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.1789 | PASS | 1.3459 | PASS | 1245.9473 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.1789 | PASS | 1.346 | PASS | 1245.9899 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.1789 | PASS | 1.346 | PASS | 1245.9899 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 3.5958 | FAIL | 24.4683 | PASS | 24368.253 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 31.9337 | PASS | 0.72357 | PASS | 623.5677 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 31.9337 | PASS | 0.72357 | PASS | 623.5677 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.4372 | PASS | 6.1473 | PASS | 6047.3214 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.4372 | PASS | 1.7196 | PASS | 1619.616 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.517 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.517 | PASS | 0.059576 | FAIL | -40.4236 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 9.1779 | PASS | 1.3774 | PASS | 1277.3647 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9926 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 9.1779 | PASS | 1.3749 | PASS | 1274.8654 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9849 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0276 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0276 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 3.596 | FAIL | 24.4715 | PASS | 24371.4615 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 6.4375 | PASS | 6.1496 | PASS | 6049.5639 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.6271 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 6.5166 | PASS | 0.041046 | FAIL | -58.9539 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 6.5166 | PASS | 0.059576 | FAIL | -40.4244 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.1462 | PASS | 1.3774 | PASS | 1277.4347 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.1462 | PASS | 1.3771 | PASS | 1277.0632 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.1462 | PASS | 1.3749 | PASS | 1274.9366 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.1462 | PASS | 1.3461 | PASS | 1246.0515 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.1462 | PASS | 1.3461 | PASS | 1246.0943 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.1462 | PASS | 1.3461 | PASS | 1246.0943 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 3.5947 | FAIL | 24.4662 | PASS | 24366.1631 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 31.9274 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 31.9274 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.4308 | PASS | 6.1457 | PASS | 6045.66 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.4308 | PASS | 1.7196 | PASS | 1619.5617 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.4921 | PASS | 0.041051 | FAIL | -58.9486 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.4921 | PASS | 0.059585 | FAIL | -40.4153 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.1462 | PASS | 1.3774 | PASS | 1277.4347 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.1462 | PASS | 1.3771 | PASS | 1277.0632 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.1462 | PASS | 1.3749 | PASS | 1274.9366 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.1462 | PASS | 1.3461 | PASS | 1246.0515 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.1462 | PASS | 1.3461 | PASS | 1246.0943 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.1462 | PASS | 1.3461 | PASS | 1246.0943 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 3.5947 | FAIL | 24.4662 | PASS | 24366.1631 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 31.9274 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 31.9274 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.4308 | PASS | 6.1457 | PASS | 6045.66 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.4308 | PASS | 1.7196 | PASS | 1619.5617 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.4921 | PASS | 0.041051 | FAIL | -58.9486 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.4921 | PASS | 0.059585 | FAIL | -40.4153 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3358 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9632 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8356 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9583 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.001 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.001 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 3.596 | FAIL | 24.4702 | PASS | 24370.2144 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 31.9309 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 31.9309 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.4374 | PASS | 6.1482 | PASS | 6048.2321 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.4374 | PASS | 1.7196 | PASS | 1619.6317 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.5166 | PASS | 0.059576 | FAIL | -40.4245 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 9.177 | PASS | 1.3774 | PASS | 1277.3602 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 9.177 | PASS | 1.377 | PASS | 1276.988 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 9.177 | PASS | 1.3749 | PASS | 1274.8607 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1245.9808 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0235 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0235 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.7699 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 6.4377 | PASS | 6.1493 | PASS | 6049.3421 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 6.4377 | PASS | 1.7196 | PASS | 1619.6446 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 6.5161 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 6.5161 | PASS | 0.059575 | FAIL | -40.4247 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1728 | PASS | 1.3774 | PASS | 1277.4193 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1728 | PASS | 1.377 | PASS | 1277.0478 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1728 | PASS | 1.3749 | PASS | 1274.9213 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1728 | PASS | 1.346 | PASS | 1246.0353 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1728 | PASS | 1.3461 | PASS | 1246.0781 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1728 | PASS | 1.3461 | PASS | 1246.0781 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 3.595 | FAIL | 24.4692 | PASS | 24369.1544 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 31.9265 | PASS | 0.72357 | PASS | 623.5656 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 31.9265 | PASS | 0.72357 | PASS | 623.5656 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 6.4319 | PASS | 6.1476 | PASS | 6047.5608 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 6.4319 | PASS | 1.7197 | PASS | 1619.6525 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 6.5129 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 6.5129 | PASS | 0.059576 | FAIL | -40.4237 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1742 | PASS | 1.3774 | PASS | 1277.369 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1742 | PASS | 1.377 | PASS | 1276.9969 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1742 | PASS | 1.3749 | PASS | 1274.8698 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1742 | PASS | 1.346 | PASS | 1245.989 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1742 | PASS | 1.346 | PASS | 1246.0317 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1742 | PASS | 1.346 | PASS | 1246.0317 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 3.5951 | FAIL | 24.4694 | PASS | 24369.4075 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.4327 | PASS | 6.1481 | PASS | 6048.1323 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.4327 | PASS | 1.7196 | PASS | 1619.6179 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.5138 | PASS | 0.041047 | FAIL | -58.9534 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.5138 | PASS | 0.059576 | FAIL | -40.424 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1775 | PASS | 1.3773 | PASS | 1277.3477 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1775 | PASS | 1.377 | PASS | 1276.9752 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1775 | PASS | 1.3748 | PASS | 1274.8478 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1245.9692 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1246.0119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1246.0119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 3.5958 | FAIL | 24.472 | PASS | 24371.9601 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.4376 | PASS | 6.149 | PASS | 6049.0268 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.4376 | PASS | 1.7197 | PASS | 1619.6517 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.5164 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.5164 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.346 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9735 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.846 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9676 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0102 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0102 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24372.034 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 31.9288 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 31.9288 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.4383 | PASS | 6.149 | PASS | 6049.0037 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.4383 | PASS | 1.7197 | PASS | 1619.6545 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.4254 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 9.1782 | PASS | 1.3773 | PASS | 1277.3322 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 9.1782 | PASS | 1.377 | PASS | 1276.9596 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 9.1782 | PASS | 1.3748 | PASS | 1274.8319 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 9.1782 | PASS | 1.346 | PASS | 1245.955 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 9.1782 | PASS | 1.346 | PASS | 1245.9976 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 9.1782 | PASS | 1.346 | PASS | 1245.9976 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 3.5962 | FAIL | 24.4716 | PASS | 24371.6255 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 31.9333 | PASS | 0.72357 | PASS | 623.5677 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 31.9333 | PASS | 0.72357 | PASS | 623.5677 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 6.4383 | PASS | 6.149 | PASS | 6049.0291 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 6.4383 | PASS | 1.7197 | PASS | 1619.6548 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 6.5173 | PASS | 0.041048 | FAIL | -58.952 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 6.5173 | PASS | 0.059574 | FAIL | -40.4257 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3483 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9758 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8484 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9697 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0124 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0124 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.7541 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.1207 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.9528 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3483 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9758 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8484 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9697 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0124 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0124 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.7626 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 31.9294 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.1206 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.9528 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1746 | PASS | 1.3777 | PASS | 1277.6585 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1746 | PASS | 1.3773 | PASS | 1277.2905 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1746 | PASS | 1.3752 | PASS | 1275.1673 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1746 | PASS | 1.3463 | PASS | 1246.2559 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1746 | PASS | 1.3463 | PASS | 1246.2989 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1746 | PASS | 1.3463 | PASS | 1246.2989 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.5866 | FAIL | 24.4576 | PASS | 24357.5789 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 31.9233 | PASS | 0.72356 | PASS | 623.5646 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 31.9233 | PASS | 0.72356 | PASS | 623.5646 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.3929 | PASS | 6.1533 | PASS | 6053.3345 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.3929 | PASS | 1.7202 | PASS | 1620.1773 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.5141 | PASS | 0.04104 | FAIL | -58.9605 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.5141 | PASS | 0.059581 | FAIL | -40.4188 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.176 | PASS | 1.3773 | PASS | 1277.2757 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.176 | PASS | 1.3769 | PASS | 1276.9022 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.176 | PASS | 1.3748 | PASS | 1274.7738 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.176 | PASS | 1.3459 | PASS | 1245.903 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.176 | PASS | 1.3459 | PASS | 1245.9456 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.176 | PASS | 1.3459 | PASS | 1245.9456 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.596 | FAIL | 24.471 | PASS | 24370.9864 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 31.9276 | PASS | 0.72357 | PASS | 623.5667 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 31.9276 | PASS | 0.72357 | PASS | 623.5667 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.4362 | PASS | 6.1474 | PASS | 6047.4347 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.4362 | PASS | 1.7197 | PASS | 1619.6923 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.5149 | PASS | 0.041048 | FAIL | -58.9524 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.5149 | PASS | 0.059575 | FAIL | -40.4246 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.1776 | PASS | 1.3773 | PASS | 1277.3477 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9753 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.1776 | PASS | 1.3748 | PASS | 1274.8479 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9692 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.948 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.129 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6507 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9526 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.1776 | PASS | 1.3773 | PASS | 1277.3468 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9744 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.1776 | PASS | 1.3748 | PASS | 1274.8469 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9684 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.011 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.011 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9538 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.4382 | PASS | 6.1491 | PASS | 6049.1151 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.6512 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9526 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1716 | PASS | 1.3773 | PASS | 1277.3401 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1716 | PASS | 1.377 | PASS | 1276.9676 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1716 | PASS | 1.3748 | PASS | 1274.8401 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1716 | PASS | 1.346 | PASS | 1245.9624 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1716 | PASS | 1.346 | PASS | 1246.0051 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1716 | PASS | 1.346 | PASS | 1246.0051 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 3.5952 | FAIL | 24.4701 | PASS | 24370.0992 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 31.9031 | PASS | 0.72356 | PASS | 623.5647 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 31.9031 | PASS | 0.72356 | PASS | 623.5647 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.4323 | PASS | 6.1474 | PASS | 6047.4303 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.4323 | PASS | 1.7197 | PASS | 1619.6575 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.5115 | PASS | 0.041048 | FAIL | -58.9523 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.5115 | PASS | 0.059576 | FAIL | -40.4244 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 9.178 | PASS | 1.3773 | PASS | 1277.3376 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 9.178 | PASS | 1.377 | PASS | 1276.965 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 9.178 | PASS | 1.3748 | PASS | 1274.8375 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 9.178 | PASS | 1.346 | PASS | 1245.9599 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 9.178 | PASS | 1.346 | PASS | 1246.0025 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 9.178 | PASS | 1.346 | PASS | 1246.0025 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 3.5961 | FAIL | 24.4715 | PASS | 24371.4601 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5665 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 6.4381 | PASS | 6.1489 | PASS | 6048.8647 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6461 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1786 | PASS | 1.3773 | PASS | 1277.3294 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1786 | PASS | 1.377 | PASS | 1276.9567 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1786 | PASS | 1.3748 | PASS | 1274.829 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1786 | PASS | 1.346 | PASS | 1245.9524 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1786 | PASS | 1.346 | PASS | 1245.9951 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1786 | PASS | 1.346 | PASS | 1245.9951 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.5958 | FAIL | 24.4704 | PASS | 24370.4253 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 31.9384 | PASS | 0.72357 | PASS | 623.5693 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 31.9384 | PASS | 0.72357 | PASS | 623.5693 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.4372 | PASS | 6.1493 | PASS | 6049.2995 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.4372 | PASS | 1.7196 | PASS | 1619.6347 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.5176 | PASS | 0.041048 | FAIL | -58.9519 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.5176 | PASS | 0.059574 | FAIL | -40.4256 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.1773 | PASS | 1.3774 | PASS | 1277.3651 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.1773 | PASS | 1.377 | PASS | 1276.9929 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.1773 | PASS | 1.3749 | PASS | 1274.8657 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1245.9853 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0279 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0279 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 3.596 | FAIL | 24.4716 | PASS | 24371.6254 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 31.928 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 31.928 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.4373 | PASS | 6.1491 | PASS | 6049.0601 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.4373 | PASS | 1.7196 | PASS | 1619.6486 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.5163 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.352 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9796 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8522 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9732 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0159 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0159 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.886 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1937 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.648 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.347 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9746 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.8472 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9686 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0113 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0113 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.789 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.4379 | PASS | 6.1491 | PASS | 6049.0645 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.6464 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 3.596 | FAIL | 24.4714 | PASS | 24371.3729 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 31.9296 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 31.9296 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.4376 | PASS | 6.149 | PASS | 6049.0394 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.4376 | PASS | 1.7196 | PASS | 1619.6375 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.3477 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9753 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.8479 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9693 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9405 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.4382 | PASS | 6.1491 | PASS | 6049.1307 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.6504 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9527 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1776 | PASS | 1.3773 | PASS | 1277.347 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9745 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1776 | PASS | 1.3748 | PASS | 1274.8471 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9686 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0112 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0112 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.947 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.4382 | PASS | 6.1491 | PASS | 6049.1212 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.6508 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9526 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1773 | PASS | 1.3773 | PASS | 1277.3447 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1773 | PASS | 1.377 | PASS | 1276.9722 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1773 | PASS | 1.3748 | PASS | 1274.8447 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1245.9664 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0091 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0091 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.5934 | FAIL | 24.4649 | PASS | 24364.8537 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.4251 | PASS | 6.1477 | PASS | 6047.7199 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.4251 | PASS | 1.7198 | PASS | 1619.7862 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.5156 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 6.5156 | PASS | 0.059576 | FAIL | -40.4244 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 9.1783 | PASS | 1.3773 | PASS | 1277.3064 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 9.1783 | PASS | 1.3769 | PASS | 1276.9334 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 9.1783 | PASS | 1.3748 | PASS | 1274.8054 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 9.1783 | PASS | 1.3459 | PASS | 1245.9312 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9738 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9738 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 3.5961 | FAIL | 24.4697 | PASS | 24369.7298 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 31.931 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 31.931 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 6.4378 | PASS | 6.1474 | PASS | 6047.4306 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 6.4378 | PASS | 1.7197 | PASS | 1619.6834 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 6.5169 | PASS | 0.041048 | FAIL | -58.9523 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.3495 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.977 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.8496 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9708 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0134 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0134 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.8278 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.4378 | PASS | 6.1492 | PASS | 6049.2259 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.4378 | PASS | 1.7196 | PASS | 1619.645 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9533 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.1811 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8851 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.1817 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9794 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.852 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.973 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8776 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1862 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.1776 | PASS | 1.3773 | PASS | 1277.348 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.1776 | PASS | 1.377 | PASS | 1276.9756 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.1776 | PASS | 1.3748 | PASS | 1274.8481 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.1776 | PASS | 1.346 | PASS | 1245.9695 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.1776 | PASS | 1.346 | PASS | 1246.0121 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.1776 | PASS | 1.346 | PASS | 1246.0121 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 3.5957 | FAIL | 24.4706 | PASS | 24370.6175 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.4363 | PASS | 6.1492 | PASS | 6049.1905 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.4363 | PASS | 1.7196 | PASS | 1619.6163 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.5163 | PASS | 0.041047 | FAIL | -58.9533 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.5163 | PASS | 0.059575 | FAIL | -40.4247 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.3378 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9652 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.8376 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9601 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0028 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0028 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 3.5964 | FAIL | 24.4721 | PASS | 24372.0841 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.4384 | PASS | 6.1482 | PASS | 6048.1726 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.4384 | PASS | 1.7197 | PASS | 1619.6852 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.5168 | PASS | 0.041048 | FAIL | -58.9517 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.5168 | PASS | 0.059574 | FAIL | -40.4259 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.9313 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1978 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.65 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.1751 | PASS | 1.3774 | PASS | 1277.4065 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.1751 | PASS | 1.377 | PASS | 1277.0349 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.1751 | PASS | 1.3749 | PASS | 1274.9082 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1246.0235 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.1751 | PASS | 1.3461 | PASS | 1246.0663 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 9.1751 | PASS | 1.3461 | PASS | 1246.0663 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 3.2735 | FAIL | 23.4204 | PASS | 23320.4025 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 4.8403 | FAIL | 5.4044 | PASS | 5304.3912 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 4.8403 | FAIL | 1.767 | PASS | 1667.0335 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 6.5098 | PASS | 0.041043 | FAIL | -58.9567 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 6.5098 | PASS | 0.05958 | FAIL | -40.4205 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 9.1774 | PASS | 1.3774 | PASS | 1277.3707 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 9.1774 | PASS | 1.377 | PASS | 1276.9986 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 9.1774 | PASS | 1.3749 | PASS | 1274.8715 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1245.9905 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0332 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0332 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 3.5945 | FAIL | 24.4781 | PASS | 24378.1312 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 6.4297 | PASS | 6.1584 | PASS | 6058.4269 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 6.4297 | PASS | 1.7202 | PASS | 1620.1511 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 6.5163 | PASS | 0.041046 | FAIL | -58.9536 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4245 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9795 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8522 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9731 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0158 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0158 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24372.0216 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 6.4381 | PASS | 6.1493 | PASS | 6049.2695 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6539 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 9.1726 | PASS | 1.3774 | PASS | 1277.371 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 9.1726 | PASS | 1.377 | PASS | 1276.9989 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 9.1726 | PASS | 1.3749 | PASS | 1274.8717 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 9.1726 | PASS | 1.346 | PASS | 1245.9909 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 9.1726 | PASS | 1.346 | PASS | 1246.0336 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 9.1726 | PASS | 1.346 | PASS | 1246.0336 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 3.5941 | FAIL | 24.4726 | PASS | 24372.6458 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 6.4297 | PASS | 6.156 | PASS | 6056.0417 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 6.4297 | PASS | 1.7201 | PASS | 1620.0885 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 6.5121 | PASS | 0.041049 | FAIL | -58.9509 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 6.5121 | PASS | 0.059576 | FAIL | -40.4241 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3521 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9797 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8523 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9732 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.016 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.016 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 3.5955 | FAIL | 24.4706 | PASS | 24370.5623 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 6.434 | PASS | 6.1483 | PASS | 6048.3346 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 6.434 | PASS | 1.7198 | PASS | 1619.7535 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 9.1775 | PASS | 1.3774 | PASS | 1277.3637 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 9.1775 | PASS | 1.377 | PASS | 1276.9915 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 9.1775 | PASS | 1.3749 | PASS | 1274.8643 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1245.984 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1246.0267 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 9.1775 | PASS | 1.346 | PASS | 1246.0267 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 3.5947 | FAIL | 24.471 | PASS | 24371.0346 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 6.4289 | PASS | 6.1493 | PASS | 6049.2659 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 6.4289 | PASS | 1.72 | PASS | 1619.9843 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3579 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9857 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8584 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9787 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0214 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0214 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 3.5954 | FAIL | 24.4706 | PASS | 24370.6274 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 6.4358 | PASS | 6.1507 | PASS | 6050.6588 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 6.4358 | PASS | 1.7196 | PASS | 1619.5907 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9534 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4248 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.177 | PASS | 1.3773 | PASS | 1277.3352 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.177 | PASS | 1.377 | PASS | 1276.9626 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.177 | PASS | 1.3748 | PASS | 1274.8349 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1245.9577 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0004 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0004 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 3.5918 | FAIL | 24.4657 | PASS | 24365.6564 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.4107 | PASS | 6.143 | PASS | 6042.9587 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.4107 | PASS | 1.7206 | PASS | 1620.5518 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.5158 | PASS | 0.041048 | FAIL | -58.9521 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.5158 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.177 | PASS | 1.3773 | PASS | 1277.3349 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.177 | PASS | 1.377 | PASS | 1276.9623 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.177 | PASS | 1.3748 | PASS | 1274.8347 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1245.9574 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0001 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0001 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 3.5917 | FAIL | 24.4655 | PASS | 24365.5074 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.4099 | PASS | 6.1428 | PASS | 6042.8491 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.4099 | PASS | 1.7206 | PASS | 1620.5795 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.5158 | PASS | 0.041048 | FAIL | -58.9521 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.5158 | PASS | 0.059575 | FAIL | -40.4253 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 9.1773 | PASS | 1.3774 | PASS | 1277.3536 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 9.1773 | PASS | 1.377 | PASS | 1276.9813 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 9.1773 | PASS | 1.3749 | PASS | 1274.8539 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1245.9747 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0174 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0174 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 3.5956 | FAIL | 24.4723 | PASS | 24372.3203 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 31.9278 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 31.9278 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 6.435 | PASS | 6.1502 | PASS | 6050.222 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 6.435 | PASS | 1.7197 | PASS | 1619.7483 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 6.5163 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3532 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9809 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8535 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9743 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0169 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0169 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 3.5962 | FAIL | 24.4722 | PASS | 24372.1745 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 6.4381 | PASS | 6.1494 | PASS | 6049.3644 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6604 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.361 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9888 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.8615 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9815 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0242 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0242 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 3.5958 | FAIL | 24.4716 | PASS | 24371.6042 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 31.9278 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 31.9278 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 6.4354 | PASS | 6.1492 | PASS | 6049.235 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 6.4354 | PASS | 1.7197 | PASS | 1619.7479 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.3519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9796 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.8522 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9731 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 3.5954 | FAIL | 24.4701 | PASS | 24370.1383 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 6.4341 | PASS | 6.1481 | PASS | 6048.0518 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 6.4341 | PASS | 1.7197 | PASS | 1619.7135 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3512 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9788 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9725 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 3.5961 | FAIL | 24.4716 | PASS | 24371.6006 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 6.4379 | PASS | 6.1491 | PASS | 6049.0616 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.6361 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9794 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.852 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.7945 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 6.4379 | PASS | 6.1492 | PASS | 6049.1883 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.6435 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 3.596 | FAIL | 24.4719 | PASS | 24371.9249 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 6.4373 | PASS | 6.1492 | PASS | 6049.155 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 6.4373 | PASS | 1.7197 | PASS | 1619.655 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.1767 | PASS | 1.3774 | PASS | 1277.3524 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.1767 | PASS | 1.377 | PASS | 1276.98 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.1767 | PASS | 1.3749 | PASS | 1274.8526 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.1767 | PASS | 1.346 | PASS | 1245.9736 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.1767 | PASS | 1.346 | PASS | 1246.0163 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.1767 | PASS | 1.346 | PASS | 1246.0163 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 3.5956 | FAIL | 24.4662 | PASS | 24366.2202 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.4344 | PASS | 6.1439 | PASS | 6043.8687 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.4344 | PASS | 1.7195 | PASS | 1619.5458 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.5147 | PASS | 0.041048 | FAIL | -58.9524 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.5147 | PASS | 0.059576 | FAIL | -40.4245 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.9148 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1839 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6492 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 9.1751 | PASS | 1.3774 | PASS | 1277.3559 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 9.1751 | PASS | 1.377 | PASS | 1276.9835 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 9.1751 | PASS | 1.3749 | PASS | 1274.8561 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1245.9769 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1246.0196 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 9.1751 | PASS | 1.346 | PASS | 1246.0196 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 3.5946 | FAIL | 24.4665 | PASS | 24366.4536 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 6.4286 | PASS | 6.1446 | PASS | 6044.6293 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 6.4286 | PASS | 1.7198 | PASS | 1619.7725 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 6.5119 | PASS | 0.041048 | FAIL | -58.9517 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 6.5119 | PASS | 0.059577 | FAIL | -40.4235 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 9.1771 | PASS | 1.3774 | PASS | 1277.4033 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 9.1771 | PASS | 1.377 | PASS | 1277.0317 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 9.1771 | PASS | 1.3749 | PASS | 1274.905 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1246.0205 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 9.1771 | PASS | 1.3461 | PASS | 1246.0632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 9.1771 | PASS | 1.3461 | PASS | 1246.0632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 3.1894 | FAIL | 22.0291 | PASS | 21929.0938 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 4.4779 | FAIL | 4.5558 | PASS | 4455.7683 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 4.4779 | FAIL | 1.7308 | PASS | 1630.783 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 6.5119 | PASS | 0.041052 | FAIL | -58.9485 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 6.5119 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1782 | PASS | 1.3774 | PASS | 1277.3579 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1782 | PASS | 1.377 | PASS | 1276.9856 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1782 | PASS | 1.3749 | PASS | 1274.8583 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1782 | PASS | 1.346 | PASS | 1245.9786 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1782 | PASS | 1.346 | PASS | 1246.0213 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1782 | PASS | 1.346 | PASS | 1246.0213 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.861 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.438 | PASS | 6.1493 | PASS | 6049.253 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6466 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.5301 | PASS | 0.041039 | FAIL | -58.9609 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.5301 | PASS | 0.059592 | FAIL | -40.4079 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 9.1723 | PASS | 1.3774 | PASS | 1277.4322 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 9.1723 | PASS | 1.3771 | PASS | 1277.0608 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 9.1723 | PASS | 1.3749 | PASS | 1274.9344 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 9.1723 | PASS | 1.346 | PASS | 1246.048 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 9.1723 | PASS | 1.3461 | PASS | 1246.0908 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 9.1723 | PASS | 1.3461 | PASS | 1246.0908 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 3.5948 | FAIL | 24.47 | PASS | 24369.9621 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 6.4322 | PASS | 6.1502 | PASS | 6050.1588 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 6.4322 | PASS | 1.7196 | PASS | 1619.616 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 5.8975 | FAIL | 0.041578 | FAIL | -58.4225 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 5.8975 | FAIL | 0.060071 | FAIL | -39.9292 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 9.1767 | PASS | 1.3774 | PASS | 1277.3633 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 9.1767 | PASS | 1.377 | PASS | 1276.9911 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 9.1767 | PASS | 1.3749 | PASS | 1274.8638 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 9.1767 | PASS | 1.346 | PASS | 1245.9838 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 9.1767 | PASS | 1.346 | PASS | 1246.0265 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 9.1767 | PASS | 1.346 | PASS | 1246.0265 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 3.596 | FAIL | 24.4717 | PASS | 24371.6797 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 31.9279 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 31.9279 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 6.4375 | PASS | 6.1494 | PASS | 6049.3545 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.641 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 6.5111 | PASS | 0.041055 | FAIL | -58.9451 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 6.5111 | PASS | 0.059578 | FAIL | -40.4217 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3531 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9807 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8533 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9742 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0169 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0169 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.878 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1966 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6485 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 6.5187 | PASS | 0.041048 | FAIL | -58.9521 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 6.5187 | PASS | 0.059581 | FAIL | -40.4188 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 9.1772 | PASS | 1.3774 | PASS | 1277.3673 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 9.1772 | PASS | 1.377 | PASS | 1276.9952 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 9.1772 | PASS | 1.3749 | PASS | 1274.868 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1245.9874 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1246.03 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1246.03 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 3.596 | FAIL | 24.4717 | PASS | 24371.7368 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 6.4375 | PASS | 6.1494 | PASS | 6049.3864 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.643 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 6.5084 | PASS | 0.04106 | FAIL | -58.9399 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 6.5084 | PASS | 0.059581 | FAIL | -40.4193 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 9.1765 | PASS | 1.3774 | PASS | 1277.3806 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 9.1765 | PASS | 1.377 | PASS | 1277.0086 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 9.1765 | PASS | 1.3749 | PASS | 1274.8816 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 9.1765 | PASS | 1.346 | PASS | 1245.9997 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 9.1765 | PASS | 1.346 | PASS | 1246.0424 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 9.1765 | PASS | 1.346 | PASS | 1246.0424 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 3.5959 | FAIL | 24.4716 | PASS | 24371.6094 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 31.9276 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 31.9276 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 6.4371 | PASS | 6.1496 | PASS | 6049.5706 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 6.4371 | PASS | 1.7196 | PASS | 1619.6399 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 6.4972 | PASS | 0.041082 | FAIL | -58.9175 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 6.4972 | PASS | 0.059585 | FAIL | -40.4149 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 9.1771 | PASS | 1.3773 | PASS | 1277.3403 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 9.1771 | PASS | 1.377 | PASS | 1276.9679 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 9.1771 | PASS | 1.3748 | PASS | 1274.8403 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1245.9625 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1246.0052 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 9.1771 | PASS | 1.346 | PASS | 1246.0052 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 3.5497 | FAIL | 24.3255 | PASS | 24225.5396 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 6.1718 | PASS | 6.0359 | PASS | 5935.9247 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 6.1718 | PASS | 1.7266 | PASS | 1626.5543 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.1772 | PASS | 1.3773 | PASS | 1277.3341 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.1772 | PASS | 1.377 | PASS | 1276.9614 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.1772 | PASS | 1.3748 | PASS | 1274.8337 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1245.9569 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1245.9996 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.1772 | PASS | 1.346 | PASS | 1245.9996 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 3.2681 | FAIL | 23.8063 | PASS | 23706.3144 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 4.8154 | FAIL | 5.7093 | PASS | 5609.3267 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 4.8154 | FAIL | 1.7887 | PASS | 1688.7436 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.9526 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.4247 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 9.1773 | PASS | 1.3774 | PASS | 1277.3563 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 9.1773 | PASS | 1.377 | PASS | 1276.9841 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 9.1773 | PASS | 1.3749 | PASS | 1274.8567 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1245.9772 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0199 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 9.1773 | PASS | 1.346 | PASS | 1246.0199 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8998 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 6.4378 | PASS | 6.1493 | PASS | 6049.3481 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 6.4378 | PASS | 1.7196 | PASS | 1619.6497 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 6.5156 | PASS | 0.04105 | FAIL | -58.9495 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 6.5156 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 9.1687 | PASS | 1.3774 | PASS | 1277.3686 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 9.1687 | PASS | 1.377 | PASS | 1276.9963 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 9.1687 | PASS | 1.3749 | PASS | 1274.8689 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 9.1687 | PASS | 1.346 | PASS | 1245.9896 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 9.1687 | PASS | 1.346 | PASS | 1246.0323 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 9.1687 | PASS | 1.346 | PASS | 1246.0323 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 3.5961 | FAIL | 24.4729 | PASS | 24372.9146 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 6.437 | PASS | 6.1492 | PASS | 6049.2458 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 6.437 | PASS | 1.7198 | PASS | 1619.7906 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 5.1389 | FAIL | 0.042589 | FAIL | -57.4107 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 5.1389 | FAIL | 0.060831 | FAIL | -39.1691 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 9.1762 | PASS | 1.3773 | PASS | 1277.2569 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 9.1762 | PASS | 1.3769 | PASS | 1276.8831 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 9.1762 | PASS | 1.3748 | PASS | 1274.7544 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 9.1762 | PASS | 1.3459 | PASS | 1245.8861 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 9.1762 | PASS | 1.3459 | PASS | 1245.9287 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 9.1762 | PASS | 1.3459 | PASS | 1245.9287 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 2 | FAIL | 18.7353 | PASS | 18635.2629 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 1.7199 | FAIL | 3.591 | PASS | 3490.9804 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 1.7199 | FAIL | 1.969 | PASS | 1869.016 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 6.5131 | PASS | 0.041059 | FAIL | -58.941 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 6.5131 | PASS | 0.059575 | FAIL | -40.4254 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3524 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.98 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8527 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9736 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0162 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0162 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.886 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1995 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6482 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 6.519 | PASS | 0.041052 | FAIL | -58.9479 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 6.519 | PASS | 0.059582 | FAIL | -40.4176 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 9.1766 | PASS | 1.3774 | PASS | 1277.3814 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 9.1766 | PASS | 1.377 | PASS | 1277.0094 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 9.1766 | PASS | 1.3749 | PASS | 1274.8824 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 9.1766 | PASS | 1.346 | PASS | 1246.0004 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 9.1766 | PASS | 1.346 | PASS | 1246.0431 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 9.1766 | PASS | 1.346 | PASS | 1246.0431 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 3.5959 | FAIL | 24.4716 | PASS | 24371.6023 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 31.9276 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 31.9276 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 6.4371 | PASS | 6.1496 | PASS | 6049.5739 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 6.4371 | PASS | 1.7196 | PASS | 1619.6394 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 6.498 | PASS | 0.04108 | FAIL | -58.9196 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 6.498 | PASS | 0.059586 | FAIL | -40.414 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 9.174 | PASS | 1.3774 | PASS | 1277.4472 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 9.174 | PASS | 1.3771 | PASS | 1277.0761 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 9.174 | PASS | 1.3749 | PASS | 1274.9498 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 9.174 | PASS | 1.3461 | PASS | 1246.0619 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 9.174 | PASS | 1.3461 | PASS | 1246.1046 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 9.174 | PASS | 1.3461 | PASS | 1246.1046 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 3.588 | FAIL | 24.4671 | PASS | 24367.1384 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 6.3874 | PASS | 6.1433 | PASS | 6043.2612 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 6.3874 | PASS | 1.7201 | PASS | 1620.0698 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 6.0679 | PASS | 0.041729 | FAIL | -58.2712 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 6.0679 | PASS | 0.060185 | FAIL | -39.8149 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 9.1774 | PASS | 1.3774 | PASS | 1277.3601 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 9.1774 | PASS | 1.377 | PASS | 1276.9879 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 9.1774 | PASS | 1.3749 | PASS | 1274.8607 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1245.9807 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0234 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0234 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8994 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 6.4377 | PASS | 6.1493 | PASS | 6049.3492 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 6.4377 | PASS | 1.7197 | PASS | 1619.6504 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 6.5121 | PASS | 0.041054 | FAIL | -58.9465 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 6.5121 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1774 | PASS | 1.3774 | PASS | 1277.3533 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1774 | PASS | 1.377 | PASS | 1276.981 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1774 | PASS | 1.3749 | PASS | 1274.8536 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1245.9744 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0171 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0171 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8656 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4378 | PASS | 6.1492 | PASS | 6049.1613 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4378 | PASS | 1.7197 | PASS | 1619.6509 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4463 | PASS | 0.041131 | FAIL | -58.8691 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4463 | PASS | 0.059647 | FAIL | -40.3528 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 9.1775 | PASS | 1.3774 | PASS | 1277.353 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 9.1775 | PASS | 1.377 | PASS | 1276.9806 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 9.1775 | PASS | 1.3749 | PASS | 1274.8533 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 9.1775 | PASS | 1.346 | PASS | 1245.9741 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 9.1775 | PASS | 1.346 | PASS | 1246.0168 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 9.1775 | PASS | 1.346 | PASS | 1246.0168 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8511 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 6.4379 | PASS | 6.1492 | PASS | 6049.164 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 6.4379 | PASS | 1.7196 | PASS | 1619.6489 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 6.4768 | PASS | 0.041095 | FAIL | -58.9047 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 6.4768 | PASS | 0.059614 | FAIL | -40.3858 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1728 | PASS | 1.3773 | PASS | 1277.3428 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1728 | PASS | 1.377 | PASS | 1276.9702 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1728 | PASS | 1.3748 | PASS | 1274.8425 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1728 | PASS | 1.346 | PASS | 1245.9653 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1728 | PASS | 1.346 | PASS | 1246.008 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1728 | PASS | 1.346 | PASS | 1246.008 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.5952 | FAIL | 24.471 | PASS | 24371.0044 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4335 | PASS | 6.1499 | PASS | 6049.9473 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4335 | PASS | 1.7197 | PASS | 1619.6545 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 5.9171 | FAIL | 0.041556 | FAIL | -58.4435 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 5.9171 | FAIL | 0.060064 | FAIL | -39.9357 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 9.1793 | PASS | 1.3773 | PASS | 1277.303 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 9.1793 | PASS | 1.3769 | PASS | 1276.93 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 9.1793 | PASS | 1.3748 | PASS | 1274.8019 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 9.1793 | PASS | 1.3459 | PASS | 1245.9279 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 9.1793 | PASS | 1.346 | PASS | 1245.9705 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 9.1793 | PASS | 1.346 | PASS | 1245.9705 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 3.5966 | FAIL | 24.4729 | PASS | 24372.881 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 31.929 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 6.4396 | PASS | 6.1487 | PASS | 6048.7268 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 6.4396 | PASS | 1.7197 | PASS | 1619.6843 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 6.5246 | PASS | 0.041021 | FAIL | -58.979 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 6.5246 | PASS | 0.05958 | FAIL | -40.4198 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.177 | PASS | 1.3774 | PASS | 1277.4132 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.177 | PASS | 1.377 | PASS | 1277.0417 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.177 | PASS | 1.3749 | PASS | 1274.9152 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.177 | PASS | 1.346 | PASS | 1246.0296 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.177 | PASS | 1.3461 | PASS | 1246.0724 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.177 | PASS | 1.3461 | PASS | 1246.0724 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 3.5958 | FAIL | 24.4711 | PASS | 24371.1394 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 31.812 | PASS | 0.72356 | PASS | 623.5614 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 31.812 | PASS | 0.72356 | PASS | 623.5614 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.4368 | PASS | 6.1496 | PASS | 6049.5699 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.4368 | PASS | 1.7196 | PASS | 1619.6208 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.5164 | PASS | 0.041046 | FAIL | -58.9538 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.5164 | PASS | 0.059576 | FAIL | -40.4244 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 9.1777 | PASS | 1.3773 | PASS | 1277.3486 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9763 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 9.1777 | PASS | 1.3748 | PASS | 1274.8488 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9701 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0128 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0128 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9031 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 31.9279 | PASS | 0.72357 | PASS | 623.5657 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 31.9279 | PASS | 0.72357 | PASS | 623.5657 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 6.438 | PASS | 6.1491 | PASS | 6049.1439 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6491 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3503 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9779 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8505 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9716 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0143 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0143 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.8993 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 31.8136 | PASS | 0.72356 | PASS | 623.558 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 31.8136 | PASS | 0.72356 | PASS | 623.558 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1716 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6481 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 9.1777 | PASS | 1.3774 | PASS | 1277.3534 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 9.1777 | PASS | 1.377 | PASS | 1276.981 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 9.1777 | PASS | 1.3749 | PASS | 1274.8537 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 9.1777 | PASS | 1.346 | PASS | 1245.9744 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 9.1777 | PASS | 1.346 | PASS | 1246.0172 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 9.1777 | PASS | 1.346 | PASS | 1246.0172 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 3.5961 | FAIL | 24.4718 | PASS | 24371.8477 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 31.916 | PASS | 0.72356 | PASS | 623.5643 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 31.916 | PASS | 0.72356 | PASS | 623.5643 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 6.438 | PASS | 6.1492 | PASS | 6049.1993 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 6.438 | PASS | 1.7196 | PASS | 1619.6464 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3513 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.377 | PASS | 1276.9789 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1245.9725 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8922 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 31.928 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 31.928 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.438 | PASS | 6.1492 | PASS | 6049.1776 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.438 | PASS | 1.7196 | PASS | 1619.6478 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.176 | PASS | 1.3775 | PASS | 1277.5069 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.176 | PASS | 1.3771 | PASS | 1277.1368 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.176 | PASS | 1.375 | PASS | 1275.0115 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.176 | PASS | 1.3461 | PASS | 1246.1161 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.176 | PASS | 1.3462 | PASS | 1246.159 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.176 | PASS | 1.3462 | PASS | 1246.159 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.5953 | FAIL | 24.47 | PASS | 24370.0336 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 31.8181 | PASS | 0.72356 | PASS | 623.5584 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 31.8181 | PASS | 0.72356 | PASS | 623.5584 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.435 | PASS | 6.1503 | PASS | 6050.3038 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.435 | PASS | 1.7196 | PASS | 1619.5801 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.5159 | PASS | 0.041045 | FAIL | -58.9552 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.5159 | PASS | 0.059577 | FAIL | -40.4233 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 9.1785 | PASS | 1.3773 | PASS | 1277.2801 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 9.1785 | PASS | 1.3769 | PASS | 1276.9067 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 9.1785 | PASS | 1.3748 | PASS | 1274.7784 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 9.1785 | PASS | 1.3459 | PASS | 1245.9069 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 9.1785 | PASS | 1.3459 | PASS | 1245.9495 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 9.1785 | PASS | 1.3459 | PASS | 1245.9495 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 3.5965 | FAIL | 24.4726 | PASS | 24372.6162 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 31.9301 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 31.9301 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 6.4393 | PASS | 6.1487 | PASS | 6048.7339 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 6.4393 | PASS | 1.7197 | PASS | 1619.6746 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 6.517 | PASS | 0.041048 | FAIL | -58.9521 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 6.517 | PASS | 0.059574 | FAIL | -40.4258 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.1783 | PASS | 1.3773 | PASS | 1277.2954 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.1783 | PASS | 1.3769 | PASS | 1276.9222 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.1783 | PASS | 1.3748 | PASS | 1274.7941 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.1783 | PASS | 1.3459 | PASS | 1245.921 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9636 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9636 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.5964 | FAIL | 24.4725 | PASS | 24372.5153 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 31.8863 | PASS | 0.72356 | PASS | 623.5625 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 31.8863 | PASS | 0.72356 | PASS | 623.5625 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.4391 | PASS | 6.1488 | PASS | 6048.7821 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.4391 | PASS | 1.7197 | PASS | 1619.6705 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.517 | PASS | 0.041048 | FAIL | -58.9523 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 6.517 | PASS | 0.059574 | FAIL | -40.4257 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 9.1791 | PASS | 1.3772 | PASS | 1277.2302 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 9.1791 | PASS | 1.3769 | PASS | 1276.8561 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 9.1791 | PASS | 1.3747 | PASS | 1274.727 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 9.1791 | PASS | 1.3459 | PASS | 1245.8608 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 9.1791 | PASS | 1.3459 | PASS | 1245.9034 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 9.1791 | PASS | 1.3459 | PASS | 1245.9034 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 3.5967 | FAIL | 24.4732 | PASS | 24373.1694 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 31.9337 | PASS | 0.72357 | PASS | 623.5676 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 31.9337 | PASS | 0.72357 | PASS | 623.5676 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 6.4402 | PASS | 6.1484 | PASS | 6048.4021 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 6.4402 | PASS | 1.7197 | PASS | 1619.6948 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 6.5173 | PASS | 0.041049 | FAIL | -58.9514 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 6.5173 | PASS | 0.059574 | FAIL | -40.4264 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 9.1784 | PASS | 1.3773 | PASS | 1277.2889 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 9.1784 | PASS | 1.3769 | PASS | 1276.9157 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 9.1784 | PASS | 1.3748 | PASS | 1274.7874 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 9.1784 | PASS | 1.3459 | PASS | 1245.9149 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.9576 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.9576 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 3.5964 | FAIL | 24.4725 | PASS | 24372.5448 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 31.931 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 31.931 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 6.4391 | PASS | 6.1488 | PASS | 6048.7796 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 6.4391 | PASS | 1.7197 | PASS | 1619.6719 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 6.517 | PASS | 0.041048 | FAIL | -58.9522 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 6.517 | PASS | 0.059574 | FAIL | -40.4257 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 9.1784 | PASS | 1.3773 | PASS | 1277.2905 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 9.1784 | PASS | 1.3769 | PASS | 1276.9173 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 9.1784 | PASS | 1.3748 | PASS | 1274.7891 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 9.1784 | PASS | 1.3459 | PASS | 1245.9164 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.959 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 9.1784 | PASS | 1.346 | PASS | 1245.959 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 3.5964 | FAIL | 24.4725 | PASS | 24372.5306 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 31.9308 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 31.9308 | PASS | 0.72357 | PASS | 623.567 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 6.4391 | PASS | 6.1488 | PASS | 6048.789 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 6.4391 | PASS | 1.7197 | PASS | 1619.6714 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 6.517 | PASS | 0.041048 | FAIL | -58.9522 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 6.517 | PASS | 0.059574 | FAIL | -40.4257 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8771 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 26.6726 | PASS | 0.7229 | PASS | 622.9031 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 26.6726 | PASS | 0.7229 | PASS | 622.9031 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1807 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6473 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8772 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 29.9582 | PASS | 0.72334 | PASS | 623.3387 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 29.9582 | PASS | 0.72334 | PASS | 623.3387 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1839 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8763 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 31.9203 | PASS | 0.72356 | PASS | 623.5647 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 31.9203 | PASS | 0.72356 | PASS | 623.5647 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1802 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8851 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 31.0331 | PASS | 0.72348 | PASS | 623.48 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 31.0331 | PASS | 0.72348 | PASS | 623.48 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1801 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6475 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3508 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9784 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.851 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9721 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0148 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0148 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8756 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 24.8913 | PASS | 0.72263 | PASS | 622.628 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 24.8913 | PASS | 0.72263 | PASS | 622.628 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.175 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3512 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9789 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9725 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8771 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 28.3538 | PASS | 0.72312 | PASS | 623.1175 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 28.3538 | PASS | 0.72312 | PASS | 623.1175 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.182 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3507 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9783 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8509 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.972 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0147 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0147 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8913 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 29.4667 | PASS | 0.72331 | PASS | 623.3139 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 29.4667 | PASS | 0.72331 | PASS | 623.3139 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1729 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.648 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 31.8559 | PASS | 0.72356 | PASS | 623.5588 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 31.8559 | PASS | 0.72356 | PASS | 623.5588 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1814 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.566 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 31.9277 | PASS | 0.72357 | PASS | 623.566 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1813 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 31.7509 | PASS | 0.72355 | PASS | 623.5493 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 31.7509 | PASS | 0.72355 | PASS | 623.5493 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1813 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8766 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 28.4606 | PASS | 0.72315 | PASS | 623.1498 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 28.4606 | PASS | 0.72315 | PASS | 623.1498 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1808 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8849 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 31.6242 | PASS | 0.72353 | PASS | 623.53 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 31.6242 | PASS | 0.72353 | PASS | 623.53 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1809 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 31.911 | PASS | 0.72356 | PASS | 623.5636 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 31.911 | PASS | 0.72356 | PASS | 623.5636 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1812 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8849 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 31.8526 | PASS | 0.72356 | PASS | 623.5581 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 31.8526 | PASS | 0.72356 | PASS | 623.5581 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1809 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9792 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9728 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0155 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.884 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 29.2963 | PASS | 0.72327 | PASS | 623.2689 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 29.2963 | PASS | 0.72327 | PASS | 623.2689 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1756 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6478 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1778 | PASS | 1.3773 | PASS | 1277.3457 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9733 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1778 | PASS | 1.3748 | PASS | 1274.8458 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9674 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0101 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0101 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.9342 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 30.4424 | PASS | 0.72343 | PASS | 623.4263 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 30.4424 | PASS | 0.72343 | PASS | 623.4263 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.1394 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6494 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 9.1778 | PASS | 1.3773 | PASS | 1277.3457 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9733 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 9.1778 | PASS | 1.3748 | PASS | 1274.8458 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9674 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0101 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0101 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.9345 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 30.4423 | PASS | 0.72343 | PASS | 623.4263 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 30.4423 | PASS | 0.72343 | PASS | 623.4263 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.1394 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6494 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9529 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.979 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8921 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1774 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6478 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9794 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8521 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.973 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8767 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1821 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3504 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9781 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8507 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9717 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0144 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0144 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8832 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 31.927 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 31.927 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1724 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6479 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 9.1778 | PASS | 1.3774 | PASS | 1277.3502 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9779 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8504 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9716 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0143 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0143 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.8979 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1682 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6483 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 31.9283 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1814 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3513 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9789 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9725 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0152 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8913 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.928 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.928 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1668 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.648 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3522 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9799 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8525 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9734 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0161 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0161 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8687 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.184 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1778 | PASS | 1.3773 | PASS | 1277.3499 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9775 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1778 | PASS | 1.3749 | PASS | 1274.8501 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.9712 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0139 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0139 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8833 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1713 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9795 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8522 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9731 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0158 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0158 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8773 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1842 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6474 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3581 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9858 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8585 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9788 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0215 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0215 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.8342 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.2116 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6458 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 9.1778 | PASS | 1.3773 | PASS | 1277.3485 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 9.1778 | PASS | 1.377 | PASS | 1276.9761 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 9.1778 | PASS | 1.3748 | PASS | 1274.8487 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1245.97 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0127 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 9.1778 | PASS | 1.346 | PASS | 1246.0127 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 3.5962 | FAIL | 24.4719 | PASS | 24371.9129 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 6.4381 | PASS | 6.1492 | PASS | 6049.1601 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 6.4381 | PASS | 1.7196 | PASS | 1619.6488 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9794 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.852 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8767 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1821 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3523 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.98 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8526 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9735 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0162 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0162 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.877 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1832 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6475 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 9.1777 | PASS | 1.3774 | PASS | 1277.3523 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 9.1777 | PASS | 1.377 | PASS | 1276.98 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 9.1777 | PASS | 1.3749 | PASS | 1274.8526 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 9.1777 | PASS | 1.346 | PASS | 1245.9735 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 9.1777 | PASS | 1.346 | PASS | 1246.0162 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 9.1777 | PASS | 1.346 | PASS | 1246.0162 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 3.5961 | FAIL | 24.4719 | PASS | 24371.877 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 6.438 | PASS | 6.1492 | PASS | 6049.1832 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 6.438 | PASS | 1.7196 | PASS | 1619.6475 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8519 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8767 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1825 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.3567 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9844 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.8571 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9775 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0202 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0202 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 3.596 | FAIL | 24.4717 | PASS | 24371.6502 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 6.4377 | PASS | 6.1493 | PASS | 6049.2743 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 6.4377 | PASS | 1.7196 | PASS | 1619.6396 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.979 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8838 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1779 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9793 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.852 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8767 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.182 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8849 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1803 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8763 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1807 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.979 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8516 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8846 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.18 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3518 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9794 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.852 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.973 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0157 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8768 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1829 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9794 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.852 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9729 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0156 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8768 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1826 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3514 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.979 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9726 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0153 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8763 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1804 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6477 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3521 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9797 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8524 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9733 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.016 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.016 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8771 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.184 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6475 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3515 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9791 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8517 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9727 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0154 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.885 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 31.9284 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1814 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.6476 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1776 | PASS | 1.3774 | PASS | 1277.3644 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1776 | PASS | 1.377 | PASS | 1276.9922 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1776 | PASS | 1.3749 | PASS | 1274.865 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1245.9846 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0273 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1776 | PASS | 1.346 | PASS | 1246.0273 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.7836 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 6.4379 | PASS | 6.1492 | PASS | 6049.242 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.644 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 6.5167 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 645558 [S3458-HOLT 3345.00] TO BUS 645458 [S3458 3 345.00] CKT Z1 |  | FAIL |  | FAIL |  | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.7647 | PASS | 1.3826 | PASS | 1282.6394 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.7647 | PASS | 1.3823 | PASS | 1282.3357 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.7647 | PASS | 1.3803 | PASS | 1280.2694 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.7647 | PASS | 1.3509 | PASS | 1250.917 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.7647 | PASS | 1.351 | PASS | 1250.9645 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.7647 | PASS | 1.351 | PASS | 1250.9645 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.5955 | FAIL | 24.4705 | PASS | 24370.5113 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4356 | PASS | 6.1498 | PASS | 6049.8308 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.4356 | PASS | 1.7196 | PASS | 1619.6 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.5093 | PASS | 0.041039 | FAIL | -58.9607 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.5093 | PASS | 0.059583 | FAIL | -40.4166 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 9.1634 | PASS | 1.3772 | PASS | 1277.174 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 9.1634 | PASS | 1.3768 | PASS | 1276.7988 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 9.1634 | PASS | 1.3747 | PASS | 1274.6685 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 9.1634 | PASS | 1.3458 | PASS | 1245.8119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 9.1634 | PASS | 1.3459 | PASS | 1245.8544 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 9.1634 | PASS | 1.3459 | PASS | 1245.8544 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8624 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1875 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.647 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659133 [SIDNEY__-MB3345.00] TO BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659168 [SIDNEY__-MB913.800] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 9.1775 | PASS | 1.3774 | PASS | 1277.369 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 9.1775 | PASS | 1.377 | PASS | 1276.9969 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 9.1775 | PASS | 1.3749 | PASS | 1274.8698 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 9.1775 | PASS | 1.346 | PASS | 1245.9889 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 9.1775 | PASS | 1.346 | PASS | 1246.0316 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 9.1775 | PASS | 1.346 | PASS | 1246.0316 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 3.5961 | FAIL | 24.4718 | PASS | 24371.8196 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 6.4379 | PASS | 6.1492 | PASS | 6049.2141 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 6.4379 | PASS | 1.7196 | PASS | 1619.6452 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 640529 [BOBCAT.C 3345.00] CKT Z1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1616 | PASS | 1.3776 | PASS | 1277.5707 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1616 | PASS | 1.3772 | PASS | 1277.2013 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1616 | PASS | 1.3751 | PASS | 1275.0766 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1616 | PASS | 1.3462 | PASS | 1246.1766 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1616 | PASS | 1.3462 | PASS | 1246.2195 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1616 | PASS | 1.3462 | PASS | 1246.2195 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 3.596 | FAIL | 24.4716 | PASS | 24371.6345 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 31.9285 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.4376 | PASS | 6.1493 | PASS | 6049.2701 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.4376 | PASS | 1.7196 | PASS | 1619.6395 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.516 | PASS | 0.041046 | FAIL | -58.9538 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.516 | PASS | 0.059576 | FAIL | -40.4243 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 9.1744 | PASS | 1.3774 | PASS | 1277.3639 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 9.1744 | PASS | 1.377 | PASS | 1276.9916 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 9.1744 | PASS | 1.3749 | PASS | 1274.8643 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 9.1744 | PASS | 1.346 | PASS | 1245.9845 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 9.1744 | PASS | 1.346 | PASS | 1246.0272 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 9.1744 | PASS | 1.346 | PASS | 1246.0272 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 3.596 | FAIL | 24.4716 | PASS | 24371.5653 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 31.9282 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 6.4375 | PASS | 6.1493 | PASS | 6049.337 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 6.4375 | PASS | 1.7196 | PASS | 1619.6361 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 6.5163 | PASS | 0.041046 | FAIL | -58.9539 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659135 [STEGALL_-MB3345.00] TO BUS 659206 [STEGALL_-MB4230.00] TO BUS 659167 [STEGALL_-MB913.800] CKT 1 | 6.5163 | PASS | 0.059576 | FAIL | -40.4243 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 9.1634 | PASS | 1.3772 | PASS | 1277.174 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 9.1634 | PASS | 1.3768 | PASS | 1276.7987 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 9.1634 | PASS | 1.3747 | PASS | 1274.6685 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 9.1634 | PASS | 1.3458 | PASS | 1245.8119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 9.1634 | PASS | 1.3459 | PASS | 1245.8544 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 9.1634 | PASS | 1.3459 | PASS | 1245.8544 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 3.5961 | FAIL | 24.4719 | PASS | 24371.8624 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 31.9286 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 6.438 | PASS | 6.1492 | PASS | 6049.1875 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 6.438 | PASS | 1.7196 | PASS | 1619.647 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659210 [SIDNEY__-MB4230.00] TO BUS 659134 [SIDNEY___TS4230.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.1568 | PASS | 1.3777 | PASS | 1277.7209 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.1568 | PASS | 1.3774 | PASS | 1277.3534 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.1568 | PASS | 1.3752 | PASS | 1275.2303 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.1568 | PASS | 1.3463 | PASS | 1246.3179 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.1568 | PASS | 1.3464 | PASS | 1246.3609 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 9.1568 | PASS | 1.3464 | PASS | 1246.3609 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 3.5959 | FAIL | 24.4713 | PASS | 24371.3342 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 31.9287 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 6.4373 | PASS | 6.1494 | PASS | 6049.3778 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 6.4373 | PASS | 1.7196 | PASS | 1619.627 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 6.5154 | PASS | 0.041043 | FAIL | -58.9566 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659425 [SD.LS-KS-MB3345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 6.5154 | PASS | 0.059578 | FAIL | -40.4221 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1543 | PASS | 1.3775 | PASS | 1277.4606 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1543 | PASS | 1.3771 | PASS | 1277.0894 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1543 | PASS | 1.375 | PASS | 1274.963 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1543 | PASS | 1.3461 | PASS | 1246.0762 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1543 | PASS | 1.3461 | PASS | 1246.119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 9.1543 | PASS | 1.3461 | PASS | 1246.119 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9731 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 31.9288 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 31.9288 | PASS | 0.72357 | PASS | 623.5662 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.4381 | PASS | 6.1491 | PASS | 6049.0843 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.4381 | PASS | 1.7197 | PASS | 1619.6528 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.5163 | PASS | 0.041047 | FAIL | -58.9526 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 659426 [SD.LS-LR-MB3345.00] TO BUS 659131 [LARAMIE_-MB3345.00] CKT 1 | 6.5163 | PASS | 0.059575 | FAIL | -40.4252 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3566 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9843 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.857 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9774 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0201 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0201 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 3.5961 | FAIL | 24.4716 | PASS | 24371.6298 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 31.9296 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 31.9296 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 6.4379 | PASS | 6.1492 | PASS | 6049.1706 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 6.4379 | PASS | 1.7196 | PASS | 1619.6438 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 6.5168 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 6.5168 | PASS | 0.059575 | FAIL | -40.4251 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1676 | PASS | 1.3779 | PASS | 1277.9327 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1676 | PASS | 1.3776 | PASS | 1277.5687 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1676 | PASS | 1.3754 | PASS | 1275.4492 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1676 | PASS | 1.3465 | PASS | 1246.509 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1676 | PASS | 1.3466 | PASS | 1246.5523 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.1676 | PASS | 1.3466 | PASS | 1246.5523 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.5924 | FAIL | 24.4622 | PASS | 24362.2439 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 31.9197 | PASS | 0.72356 | PASS | 623.5642 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 31.9197 | PASS | 0.72356 | PASS | 623.5642 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.4214 | PASS | 6.1479 | PASS | 6047.9052 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.4214 | PASS | 1.7195 | PASS | 1619.4608 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.5086 | PASS | 0.041038 | FAIL | -58.9621 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.5086 | PASS | 0.059584 | FAIL | -40.4157 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 9.1783 | PASS | 1.3773 | PASS | 1277.3394 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 9.1783 | PASS | 1.377 | PASS | 1276.9668 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 9.1783 | PASS | 1.3748 | PASS | 1274.8392 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1245.9618 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1246.0045 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 9.1783 | PASS | 1.346 | PASS | 1246.0045 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 3.5963 | FAIL | 24.4718 | PASS | 24371.8189 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 31.9291 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 31.9291 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 6.4386 | PASS | 6.1488 | PASS | 6048.7708 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 6.4386 | PASS | 1.7197 | PASS | 1619.6667 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 6.5243 | PASS | 0.041228 | FAIL | -58.7723 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 6.5243 | PASS | 0.059742 | FAIL | -40.2581 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1774 | PASS | 1.3774 | PASS | 1277.358 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1774 | PASS | 1.377 | PASS | 1276.9857 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1774 | PASS | 1.3749 | PASS | 1274.8584 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1245.9787 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0214 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1774 | PASS | 1.346 | PASS | 1246.0214 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 3.5961 | FAIL | 24.4717 | PASS | 24371.7327 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 31.9247 | PASS | 0.72357 | PASS | 623.566 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 31.9247 | PASS | 0.72357 | PASS | 623.566 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 6.4377 | PASS | 6.149 | PASS | 6049.045 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 6.4377 | PASS | 1.7196 | PASS | 1619.6465 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 6.5165 | PASS | 0.041047 | FAIL | -58.953 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 6.5165 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 9.1777 | PASS | 1.3774 | PASS | 1277.3563 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 9.1777 | PASS | 1.377 | PASS | 1276.9841 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 9.1777 | PASS | 1.3749 | PASS | 1274.8567 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1245.9771 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0198 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 9.1777 | PASS | 1.346 | PASS | 1246.0198 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 3.596 | FAIL | 24.4716 | PASS | 24371.6237 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 31.9292 | PASS | 0.72357 | PASS | 623.5664 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 6.4376 | PASS | 6.1493 | PASS | 6049.3115 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 6.4376 | PASS | 1.7196 | PASS | 1619.6385 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 6.5166 | PASS | 0.041047 | FAIL | -58.9532 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 6.5166 | PASS | 0.059575 | FAIL | -40.4249 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1802 | PASS | 1.3771 | PASS | 1277.1327 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1802 | PASS | 1.3768 | PASS | 1276.7571 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1802 | PASS | 1.3746 | PASS | 1274.6268 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1802 | PASS | 1.3458 | PASS | 1245.7709 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1802 | PASS | 1.3458 | PASS | 1245.8133 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 9.1802 | PASS | 1.3458 | PASS | 1245.8133 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.5975 | FAIL | 24.4751 | PASS | 24375.1323 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4429 | PASS | 6.1477 | PASS | 6047.6663 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.4429 | PASS | 1.7198 | PASS | 1619.7703 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.5454 | PASS | 0.0411 | FAIL | -58.8999 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 6.5454 | PASS | 0.059527 | FAIL | -40.4728 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 9.1802 | PASS | 1.3771 | PASS | 1277.132 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 9.1802 | PASS | 1.3768 | PASS | 1276.7565 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 9.1802 | PASS | 1.3746 | PASS | 1274.6261 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 9.1802 | PASS | 1.3458 | PASS | 1245.7703 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 9.1802 | PASS | 1.3458 | PASS | 1245.8128 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 9.1802 | PASS | 1.3458 | PASS | 1245.8128 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 3.5975 | FAIL | 24.4751 | PASS | 24375.131 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 31.9298 | PASS | 0.72357 | PASS | 623.5666 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 6.4429 | PASS | 6.1477 | PASS | 6047.661 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 6.4429 | PASS | 1.7198 | PASS | 1619.7706 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 6.5448 | PASS | 0.041103 | FAIL | -58.8972 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 6.5448 | PASS | 0.059527 | FAIL | -40.4732 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3424 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9699 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8424 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9644 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.007 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.007 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9725 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 31.9304 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 31.9304 | PASS | 0.72357 | PASS | 623.5668 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 6.4382 | PASS | 6.1492 | PASS | 6049.1752 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.6565 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 6.5169 | PASS | 0.041047 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4254 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 9.1779 | PASS | 1.3773 | PASS | 1277.3411 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 9.1779 | PASS | 1.377 | PASS | 1276.9686 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 9.1779 | PASS | 1.3748 | PASS | 1274.8411 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1245.9632 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0059 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 9.1779 | PASS | 1.346 | PASS | 1246.0059 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 3.5962 | FAIL | 24.472 | PASS | 24371.9861 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 31.9306 | PASS | 0.72357 | PASS | 623.5669 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 31.9306 | PASS | 0.72357 | PASS | 623.5669 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 6.4382 | PASS | 6.1492 | PASS | 6049.1683 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 6.4382 | PASS | 1.7197 | PASS | 1619.658 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 6.5169 | PASS | 0.041048 | FAIL | -58.9525 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 6.5169 | PASS | 0.059575 | FAIL | -40.4255 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 9.0594 | PASS | 1.3776 | PASS | 1277.6114 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 9.0594 | PASS | 1.3772 | PASS | 1277.2419 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 9.0594 | PASS | 1.3751 | PASS | 1275.1169 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 9.0594 | PASS | 1.3462 | PASS | 1246.2196 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 9.0594 | PASS | 1.3463 | PASS | 1246.2625 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 9.0594 | PASS | 1.3463 | PASS | 1246.2625 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 3.5912 | FAIL | 24.4523 | PASS | 24352.3319 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 31.9243 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 31.9243 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 6.4124 | PASS | 6.136 | PASS | 6036.0396 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 6.4124 | PASS | 1.7194 | PASS | 1619.3604 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 6.4249 | PASS | 0.041065 | FAIL | -58.9353 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 6.4249 | PASS | 0.059607 | FAIL | -40.3928 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 9.154 | PASS | 1.3776 | PASS | 1277.5884 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 9.154 | PASS | 1.3772 | PASS | 1277.2192 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 9.154 | PASS | 1.3751 | PASS | 1275.0948 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 9.154 | PASS | 1.3462 | PASS | 1246.1923 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 9.154 | PASS | 1.3462 | PASS | 1246.2352 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 9.154 | PASS | 1.3462 | PASS | 1246.2352 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 3.5942 | FAIL | 24.4696 | PASS | 24369.639 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 31.9288 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 31.9288 | PASS | 0.72357 | PASS | 623.5663 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 6.4257 | PASS | 6.1469 | PASS | 6046.8507 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 6.4257 | PASS | 1.7198 | PASS | 1619.8068 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 3.7215 | FAIL | 0.04769 | FAIL | -52.31 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 3.7215 | FAIL | 0.064319 | FAIL | -35.6809 | 51.237 | 116.63
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 9.1777 | PASS | 1.3774 | PASS | 1277.3576 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 9.1777 | PASS | 1.377 | PASS | 1276.9853 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 9.1777 | PASS | 1.3749 | PASS | 1274.858 | 65.23 | 151.2
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 9.1777 | PASS | 1.346 | PASS | 1245.9783 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 9.1777 | PASS | 1.346 | PASS | 1246.021 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-015 | Holcomb 345 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 9.1777 | PASS | 1.346 | PASS | 1246.021 | 68.103 | 157.75
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-019 | 5th Street Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 3.5961 | FAIL | 24.4718 | PASS | 24371.8407 | 80 | 88
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-029 | Nearman 161 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 31.9281 | PASS | 0.72357 | PASS | 623.5661 | 85 | 90.78
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 6.438 | PASS | 6.1492 | PASS | 6049.199 | 75.216 | 184.8
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-032 | St. John 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 6.438 | PASS | 1.7196 | PASS | 1619.646 | 74.784 | 199.19
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 6.5167 | PASS | 0.041047 | FAIL | -58.9531 | 98.763 | 171.6
ERAS-2025-001 | 03 CENTRAL | 29WP | ERAS-2025-033 | Fort Dodge 115 kV Substation | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 6.5167 | PASS | 0.059575 | FAIL | -40.425 | 51.237 | 116.63
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | base | 12.4503 | PASS | 34.3945 | PASS | 34294.4605 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | base | 12.4503 | PASS | 82.8668 | PASS | 82766.774 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | base | 7.3444 | PASS | 14.2648 | PASS | 14164.8484 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | base | 12.6015 | PASS | 18.4264 | PASS | 18326.3603 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4499 | PASS | 34.398 | PASS | 34298.0148 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4499 | PASS | 82.7775 | PASS | 82677.5084 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3442 | PASS | 14.2647 | PASS | 14164.7107 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3815 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 12.4503 | PASS | 34.3948 | PASS | 34294.7692 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 12.4503 | PASS | 82.8588 | PASS | 82758.7981 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 7.3432 | PASS | 14.2665 | PASS | 14166.5283 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 12.6006 | PASS | 18.4265 | PASS | 18326.472 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.4502 | PASS | 34.3956 | PASS | 34295.5659 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.4502 | PASS | 82.8389 | PASS | 82738.8636 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.738 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3661 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 9.0172 | PASS | 42.8645 | PASS | 42764.4744 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 9.0172 | PASS | 22.975 | PASS | 22875.0104 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.7217 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 337903 [5DARDANELLE 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3568 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 5.4959 | FAIL | 34.9203 | PASS | 34820.3116 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 5.4959 | FAIL | 22.3415 | PASS | 22241.4879 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 7.3446 | PASS | 14.2639 | PASS | 14163.9008 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507195 [MAGZREC5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.381 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.4455 | PASS | 34.4369 | PASS | 34336.919 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.4455 | PASS | 81.8857 | PASS | 81785.7164 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 7.344 | PASS | 14.2633 | PASS | 14163.3301 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4179 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 12.4499 | PASS | 34.395 | PASS | 34295.0267 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 12.4499 | PASS | 82.8439 | PASS | 82743.9009 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 7.3444 | PASS | 14.264 | PASS | 14163.9661 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 12.6013 | PASS | 18.4263 | PASS | 18326.3489 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4495 | PASS | 34.3971 | PASS | 34297.0957 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4495 | PASS | 82.7944 | PASS | 82694.379 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 7.3448 | PASS | 14.2636 | PASS | 14163.649 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.6013 | PASS | 18.4263 | PASS | 18326.3043 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.45 | PASS | 34.3946 | PASS | 34294.6438 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.45 | PASS | 82.8566 | PASS | 82756.5563 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 7.3439 | PASS | 14.2648 | PASS | 14164.7687 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 12.601 | PASS | 18.4264 | PASS | 18326.4218 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 12.4507 | PASS | 34.4024 | PASS | 34302.4436 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 12.4507 | PASS | 82.6901 | PASS | 82590.1101 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 7.3458 | PASS | 14.2608 | PASS | 14160.7642 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 12.6008 | PASS | 18.4265 | PASS | 18326.5194 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4493 | PASS | 34.3969 | PASS | 34296.8551 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.4493 | PASS | 82.7969 | PASS | 82696.8513 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 7.3448 | PASS | 14.264 | PASS | 14164.0089 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 12.6014 | PASS | 18.4263 | PASS | 18326.3061 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 12.4434 | PASS | 34.4498 | PASS | 34349.7791 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 12.4434 | PASS | 81.5764 | PASS | 81476.4364 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 7.3436 | PASS | 14.264 | PASS | 14163.9667 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.4019 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5094 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 12.4503 | PASS | 82.8658 | PASS | 82765.8035 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8378 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3617 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.5094 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 12.4503 | PASS | 82.8658 | PASS | 82765.8035 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8378 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3617 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 12.4491 | PASS | 34.3954 | PASS | 34295.3766 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 12.4491 | PASS | 82.8151 | PASS | 82715.0812 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 7.3432 | PASS | 14.266 | PASS | 14166.0065 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509915 [ANTHEM7 345.00] CKT 1 | 12.6006 | PASS | 18.4264 | PASS | 18326.4143 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 12.4499 | PASS | 34.3974 | PASS | 34297.3633 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 12.4499 | PASS | 82.7899 | PASS | 82689.8988 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 7.3424 | PASS | 14.2676 | PASS | 14167.5629 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 12.599 | PASS | 18.4265 | PASS | 18326.5049 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.4757 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 12.4502 | PASS | 82.8662 | PASS | 82766.2263 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 7.3443 | PASS | 14.2649 | PASS | 14164.9224 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 12.6014 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.4483 | PASS | 34.3942 | PASS | 34294.1811 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.4483 | PASS | 82.8313 | PASS | 82731.2882 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 7.3445 | PASS | 14.264 | PASS | 14164.0255 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.601 | PASS | 18.4261 | PASS | 18326.0582 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4463 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4502 | PASS | 82.8669 | PASS | 82766.9289 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.9367 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511405 [BINGER 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.6036 | PASS | 18.4237 | PASS | 18323.7123 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5533 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 12.4503 | PASS | 82.8646 | PASS | 82764.6009 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 7.3424 | PASS | 14.2572 | PASS | 14157.2219 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 12.5749 | PASS | 18.4295 | PASS | 18329.4593 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 12.4503 | PASS | 34.3947 | PASS | 34294.7431 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 12.4503 | PASS | 82.8604 | PASS | 82760.4138 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 7.3412 | PASS | 14.2637 | PASS | 14163.6674 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 12.581 | PASS | 18.4441 | PASS | 18344.1075 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5613 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4503 | PASS | 82.8647 | PASS | 82764.6598 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 7.3426 | PASS | 14.2631 | PASS | 14163.137 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.3916 | PASS | 18.4452 | PASS | 18345.244 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4709 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.8057 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.8922 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.2712 | PASS | 18.4688 | PASS | 18368.8136 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4707 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.8084 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.8935 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.2697 | PASS | 18.4668 | PASS | 18366.8085 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4735 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7775 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.9431 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.6012 | PASS | 18.4263 | PASS | 18326.3025 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4628 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.4503 | PASS | 82.8667 | PASS | 82766.7484 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.7971 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511467 [L.E.S.-4 138.00] CKT 1 | 12.6018 | PASS | 18.4263 | PASS | 18326.3355 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4942 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.4503 | PASS | 82.8656 | PASS | 82765.6359 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 7.3439 | PASS | 14.2654 | PASS | 14165.421 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511477 [S.W.S.-4 138.00] CKT 1 | 12.3902 | PASS | 18.4423 | PASS | 18342.3098 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 12.4502 | PASS | 34.3947 | PASS | 34294.6894 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 12.4502 | PASS | 82.8595 | PASS | 82759.4588 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 7.3411 | PASS | 14.2576 | PASS | 14157.6224 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511607 [O.K.U.3-7 345.00] CKT Z1 | 12.4914 | PASS | 18.4426 | PASS | 18342.5994 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4825 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.4503 | PASS | 82.8663 | PASS | 82766.3404 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8117 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.6036 | PASS | 18.4263 | PASS | 18326.3357 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4905 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.4034 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.771 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.3264 | PASS | 18.4814 | PASS | 18381.3507 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5219 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.4503 | PASS | 82.8659 | PASS | 82765.8598 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 7.3439 | PASS | 14.2653 | PASS | 14165.3427 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.5931 | PASS | 18.4279 | PASS | 18327.9028 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 12.4502 | PASS | 34.3949 | PASS | 34294.856 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 12.4502 | PASS | 82.8596 | PASS | 82759.6449 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 7.3271 | PASS | 14.2002 | PASS | 14100.1803 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 12.4857 | PASS | 18.4529 | PASS | 18352.9417 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 12.4509 | PASS | 34.3958 | PASS | 34295.8452 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 12.4509 | PASS | 82.8448 | PASS | 82744.7527 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 7.3473 | PASS | 14.2587 | PASS | 14158.6974 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 12.6022 | PASS | 18.4322 | PASS | 18332.2023 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4755 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7541 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.723 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511488 [112GORE4 138.00] CKT 1 | 12.6016 | PASS | 18.4264 | PASS | 18326.3737 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5507 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 12.4503 | PASS | 82.865 | PASS | 82764.9749 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 7.3429 | PASS | 14.2627 | PASS | 14162.7081 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 12.3787 | PASS | 18.4294 | PASS | 18329.446 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4701 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.8154 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.9214 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.2326 | PASS | 18.4631 | PASS | 18363.0717 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4902 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.4027 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7915 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 12.281 | PASS | 18.4715 | PASS | 18371.4811 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.479 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.3769 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.6511 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.1283 | PASS | 18.5344 | PASS | 18434.3644 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4705 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.8111 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.8704 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511563 [ELSWORTH 4138.00] CKT 1 | 12.232 | PASS | 18.4704 | PASS | 18370.3691 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5124 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 12.4503 | PASS | 82.8656 | PASS | 82765.631 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.6698 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511510 [LAIRGST4 138.00] CKT 1 | 12.5834 | PASS | 18.434 | PASS | 18334.0312 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.527 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 12.4503 | PASS | 82.8653 | PASS | 82765.2717 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 7.3429 | PASS | 14.2614 | PASS | 14161.3741 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 529304 [OMDUNCN4 138.00] CKT 1 | 12.5903 | PASS | 18.4346 | PASS | 18334.556 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4355 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 12.4502 | PASS | 82.8674 | PASS | 82767.4233 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8325 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512727 [GRDA1 2 69.000] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3616 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4501 | PASS | 34.3946 | PASS | 34294.5718 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4501 | PASS | 82.8634 | PASS | 82763.4135 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7946 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3579 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.5197 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4502 | PASS | 82.8655 | PASS | 82765.5075 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.832 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3623 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.5197 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4502 | PASS | 82.8655 | PASS | 82765.5076 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8321 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3623 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.5079 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.4502 | PASS | 82.8655 | PASS | 82765.4504 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8236 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3669 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.5079 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.4502 | PASS | 82.8655 | PASS | 82765.4504 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 7.3443 | PASS | 14.2648 | PASS | 14164.8236 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512648 [MAID 5 161.00] CKT 2 | 12.6014 | PASS | 18.4264 | PASS | 18326.3669 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 12.447 | PASS | 34.4146 | PASS | 34314.6295 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 12.447 | PASS | 82.3822 | PASS | 82282.214 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 7.3445 | PASS | 14.2629 | PASS | 14162.8891 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512700 [WAGNOR 5 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3704 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4647 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.4503 | PASS | 82.8665 | PASS | 82766.5312 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8472 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3612 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 12.4456 | PASS | 34.4326 | PASS | 34332.5854 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 12.4456 | PASS | 81.9366 | PASS | 81836.6 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 7.3438 | PASS | 14.2635 | PASS | 14163.4916 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 513050 [LOCSTGV 5 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3995 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 12.4505 | PASS | 34.396 | PASS | 34296.017 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 12.4505 | PASS | 82.8321 | PASS | 82732.0592 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 7.3449 | PASS | 14.264 | PASS | 14164.0197 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 763472 [GEN-2019-002161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3589 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 12.4454 | PASS | 34.4007 | PASS | 34300.7171 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 12.4454 | PASS | 82.5989 | PASS | 82498.861 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 7.3432 | PASS | 14.2665 | PASS | 14166.5362 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512750 [TONECE7 345.00] CKT 1 | 12.6015 | PASS | 18.4263 | PASS | 18326.3467 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 12.449 | PASS | 34.3967 | PASS | 34296.6909 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 12.449 | PASS | 82.7851 | PASS | 82685.0758 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 7.3433 | PASS | 14.2662 | PASS | 14166.2309 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512865 [GREC TAP7 345.00] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.367 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4503 | PASS | 34.3947 | PASS | 34294.6574 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4503 | PASS | 82.863 | PASS | 82763.0249 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8024 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3637 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4706 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 12.4502 | PASS | 82.8665 | PASS | 82766.4731 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8446 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512757 [NWMAID5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3612 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4686 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.4502 | PASS | 82.8665 | PASS | 82766.4878 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8453 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512757 [NWMAID5 161.00] TO BUS 512760 [GERALDGAY5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3612 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4504 | PASS | 34.3952 | PASS | 34295.2331 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.4504 | PASS | 82.8495 | PASS | 82749.4564 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 7.3446 | PASS | 14.2645 | PASS | 14164.4866 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 513570 [CHOUTEAUCRK5161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3619 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4673 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 12.4503 | PASS | 82.8667 | PASS | 82766.6911 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.731 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.4341 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.5652 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 12.4502 | PASS | 82.863 | PASS | 82762.9616 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 7.3432 | PASS | 14.2667 | PASS | 14166.6561 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 515459 [ACORN 4 138.00] CKT 1 | 12.6005 | PASS | 18.427 | PASS | 18326.9754 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5864 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 12.4503 | PASS | 82.8634 | PASS | 82763.442 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 7.3434 | PASS | 14.2662 | PASS | 14166.2353 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514971 [GRNPAST4 138.00] CKT 1 | 12.6007 | PASS | 18.4269 | PASS | 18326.9172 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4801 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 12.4502 | PASS | 82.8662 | PASS | 82766.1792 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 7.3439 | PASS | 14.2641 | PASS | 14164.0656 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 12.5804 | PASS | 18.4287 | PASS | 18328.6965 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 12.4501 | PASS | 34.3945 | PASS | 34294.5496 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 12.4501 | PASS | 82.8618 | PASS | 82761.768 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 7.3441 | PASS | 14.2654 | PASS | 14165.4157 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 12.5917 | PASS | 18.4278 | PASS | 18327.8442 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5246 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4503 | PASS | 82.8653 | PASS | 82765.2638 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 7.3441 | PASS | 14.2651 | PASS | 14165.0716 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.5982 | PASS | 18.4263 | PASS | 18326.329 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.5379 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.4502 | PASS | 82.8644 | PASS | 82764.3523 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 7.3434 | PASS | 14.266 | PASS | 14165.9579 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514884 [DUNJEE 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.6001 | PASS | 18.4271 | PASS | 18327.0748 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4893 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4503 | PASS | 82.8659 | PASS | 82765.8858 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 7.3439 | PASS | 14.2637 | PASS | 14163.7257 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.5911 | PASS | 18.4287 | PASS | 18328.6559 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4894 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.4503 | PASS | 82.8659 | PASS | 82765.8856 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 7.3439 | PASS | 14.2637 | PASS | 14163.7381 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.5912 | PASS | 18.4286 | PASS | 18328.6467 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4881 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 12.4503 | PASS | 82.8659 | PASS | 82765.8993 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.9219 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 12.6009 | PASS | 18.4264 | PASS | 18326.3507 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 12.4502 | PASS | 34.3952 | PASS | 34295.2293 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 12.4502 | PASS | 82.8483 | PASS | 82748.2694 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 7.339 | PASS | 14.2464 | PASS | 14146.3745 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 12.6017 | PASS | 18.4267 | PASS | 18326.6789 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.5408 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 12.4502 | PASS | 82.863 | PASS | 82763.042 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 7.3431 | PASS | 14.2668 | PASS | 14166.7772 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 1 | 12.6025 | PASS | 18.4264 | PASS | 18326.3631 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.5408 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 12.4502 | PASS | 82.863 | PASS | 82763.042 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 7.3431 | PASS | 14.2668 | PASS | 14166.7772 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 2 | 12.6025 | PASS | 18.4264 | PASS | 18326.3631 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 12.4502 | PASS | 34.3945 | PASS | 34294.5408 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 12.4502 | PASS | 82.863 | PASS | 82763.042 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 7.3431 | PASS | 14.2668 | PASS | 14166.7772 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133345.00] CKT 3 | 12.6025 | PASS | 18.4264 | PASS | 18326.3631 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5293 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 12.4503 | PASS | 82.8656 | PASS | 82765.5891 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 7.3437 | PASS | 14.2614 | PASS | 14161.4087 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514927 [HSLEAST2 69.000] TO BUS 514937 [HSLWEST2 69.000] CKT 1 | 12.6012 | PASS | 18.4265 | PASS | 18326.541 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5426 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 12.4503 | PASS | 82.8643 | PASS | 82764.3484 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 7.3436 | PASS | 14.2653 | PASS | 14165.3364 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514966 [MIDWAY 4 138.00] CKT 1 | 12.5999 | PASS | 18.4271 | PASS | 18327.1095 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4991 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.4503 | PASS | 82.8654 | PASS | 82765.3986 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 7.344 | PASS | 14.2652 | PASS | 14165.2088 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514973 [RENO 4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3706 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4922 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.3801 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 7.3443 | PASS | 14.2636 | PASS | 14163.5648 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514964 [NE10TH 4 138.00] TO BUS 514986 [GLENDAL4 138.00] CKT 1 | 12.6 | PASS | 18.4266 | PASS | 18326.5824 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4616 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7541 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.6844 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514986 [GLENDAL4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 12.6013 | PASS | 18.4263 | PASS | 18326.3454 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 12.4503 | PASS | 34.395 | PASS | 34294.963 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 12.4503 | PASS | 82.8562 | PASS | 82756.1933 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 7.3427 | PASS | 14.2508 | PASS | 14150.7669 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514987 [DALE 4 138.00] TO BUS 515059 [SQUIRCK4 138.00] CKT 1 | 12.6006 | PASS | 18.4269 | PASS | 18326.8634 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4849 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 12.4503 | PASS | 82.8663 | PASS | 82766.303 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 7.3444 | PASS | 14.2637 | PASS | 14163.6858 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514993 [SE15TH 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 12.5994 | PASS | 18.4267 | PASS | 18326.6829 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 12.4502 | PASS | 34.3958 | PASS | 34295.7987 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 12.4502 | PASS | 82.834 | PASS | 82734.0143 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 7.3415 | PASS | 14.2619 | PASS | 14161.9092 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 515442 [LINCOLN4 138.00] CKT 1 | 12.6017 | PASS | 18.4265 | PASS | 18326.5228 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.3824 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 12.4502 | PASS | 82.8682 | PASS | 82768.1588 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14165.0237 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515046 [HAMMTAP4 138.00] TO BUS 520951 [HAMMETT4 138.00] CKT 1 | 12.6014 | PASS | 18.4263 | PASS | 18326.3357 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.5389 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.4502 | PASS | 82.8632 | PASS | 82763.2471 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 7.3439 | PASS | 14.2642 | PASS | 14164.2181 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 12.6018 | PASS | 18.4264 | PASS | 18326.44 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.5386 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.4502 | PASS | 82.8636 | PASS | 82763.5868 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 7.3439 | PASS | 14.2642 | PASS | 14164.2102 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 12.6018 | PASS | 18.4264 | PASS | 18326.4413 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 12.45 | PASS | 34.3947 | PASS | 34294.7162 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 12.45 | PASS | 82.8544 | PASS | 82754.3766 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 7.3419 | PASS | 14.2633 | PASS | 14163.266 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 12.5822 | PASS | 18.4308 | PASS | 18330.7645 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 12.4511 | PASS | 34.3971 | PASS | 34297.077 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 12.4511 | PASS | 82.8189 | PASS | 82718.9184 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 7.3468 | PASS | 14.2588 | PASS | 14158.8102 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 12.6031 | PASS | 18.429 | PASS | 18329.0497 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4745 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7664 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.6711 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 12.3953 | PASS | 18.4256 | PASS | 18325.5821 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4741 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 12.4503 | PASS | 82.8668 | PASS | 82766.7704 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.7721 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 12.5024 | PASS | 18.4258 | PASS | 18325.7755 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 12.4503 | PASS | 34.3945 | PASS | 34294.4741 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 12.4503 | PASS | 82.8668 | PASS | 82766.7704 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 7.3444 | PASS | 14.2648 | PASS | 14164.7721 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 12.5024 | PASS | 18.4258 | PASS | 18325.7755 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4511 | PASS | 34.3964 | PASS | 34296.438 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4511 | PASS | 82.834 | PASS | 82734.0206 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 7.3488 | PASS | 14.2573 | PASS | 14157.3236 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520512 [BC SW 4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.6531 | PASS | 18.587 | PASS | 18486.962 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4507 | PASS | 34.3953 | PASS | 34295.3307 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.4507 | PASS | 82.8535 | PASS | 82753.4854 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 7.3464 | PASS | 14.2614 | PASS | 14161.449 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520514 [BCVI SW4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 12.6261 | PASS | 18.5021 | PASS | 18402.1377 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5117 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 12.4503 | PASS | 82.8653 | PASS | 82765.2524 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 7.3436 | PASS | 14.2659 | PASS | 14165.8646 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520827 [BINGERJ4 138.00] TO BUS 521017 [ONEY 4 138.00] CKT 1 | 12.2297 | PASS | 18.4198 | PASS | 18319.7806 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4609 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.769 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8104 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 520838 [CADDO 2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4804 | PASS | 18.4543 | PASS | 18354.2632 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4791 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.4503 | PASS | 82.8662 | PASS | 82766.1901 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14164.9546 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 521027 [PINERTP2 69.000] TO BUS 521088 [WASHITA2 69.000] CKT 1 | 12.5467 | PASS | 18.4282 | PASS | 18328.2336 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 12.4504 | PASS | 34.3965 | PASS | 34296.4567 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 12.4504 | PASS | 82.8207 | PASS | 82720.6844 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 7.3449 | PASS | 14.264 | PASS | 14164.0196 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300031 [1CHOTST3 16.000] CKT 10 | 12.6014 | PASS | 18.4264 | PASS | 18326.3619 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 12.4504 | PASS | 34.3966 | PASS | 34296.6039 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 12.4504 | PASS | 82.8174 | PASS | 82717.3531 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 7.345 | PASS | 14.2639 | PASS | 14163.9021 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300032 [1CHOTCT1 16.000] CKT 11 | 12.6014 | PASS | 18.4264 | PASS | 18326.36 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 12.4504 | PASS | 34.3966 | PASS | 34296.6043 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 12.4504 | PASS | 82.8174 | PASS | 82717.3531 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 7.345 | PASS | 14.2639 | PASS | 14163.9021 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 300033 [1CHOTCT2 16.000] CKT 12 | 12.6014 | PASS | 18.4264 | PASS | 18326.36 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 12.4502 | PASS | 34.3946 | PASS | 34294.5816 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 12.4502 | PASS | 82.8627 | PASS | 82762.7307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7774 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300069 [5CHOTEAU1 161.00] TO BUS 301348 [5CHOTEAU2 161.00] CKT Z1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3556 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 12.4503 | PASS | 34.3947 | PASS | 34294.7355 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 12.4503 | PASS | 82.8601 | PASS | 82760.0841 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 7.3433 | PASS | 14.2664 | PASS | 14166.3654 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 300135 [4LUTHER 138.00] CKT 1 | 12.6006 | PASS | 18.4265 | PASS | 18326.487 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.3934 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 12.4502 | PASS | 82.8677 | PASS | 82767.7012 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14165.0101 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300136 [4MEMORALT 138.00] TO BUS 301541 [4MEMORAL 138.00] CKT 1 | 12.6014 | PASS | 18.4263 | PASS | 18326.3455 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.4499 | PASS | 34.3932 | PASS | 34293.1501 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.4499 | PASS | 82.8938 | PASS | 82793.8155 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 7.345 | PASS | 14.2639 | PASS | 14163.8517 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 12.6013 | PASS | 18.4262 | PASS | 18326.1756 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.5688 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.4502 | PASS | 82.8634 | PASS | 82763.4476 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7951 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.36 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.4502 | PASS | 34.3946 | PASS | 34294.5688 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.4502 | PASS | 82.8634 | PASS | 82763.448 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.7951 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.6014 | PASS | 18.4264 | PASS | 18326.36 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 11.6191 | PASS | 38.5051 | PASS | 38405.1035 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 11.6191 | PASS | 49.4896 | PASS | 49389.6041 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.8897 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337900 [3OLA AR 115.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3606 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 11.6174 | PASS | 38.5126 | PASS | 38412.5998 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 11.6174 | PASS | 49.4664 | PASS | 49366.4367 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.8945 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337901 [3DANVLE AR 115.00] TO BUS 337902 [5DANVLE AR! 161.00] TO BUS 337944 [1DANVLE AR 13.860] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3606 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.3946 | PASS | 30.3131 | PASS | 30213.1494 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.3946 | PASS | 20.5805 | PASS | 20480.4704 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.344 | PASS | 14.2651 | PASS | 14165.0649 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337902 [5DANVLE AR! 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3547 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 9.0707 | PASS | 35.7955 | PASS | 35695.4845 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 9.0707 | PASS | 21.7268 | PASS | 21626.7948 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.7433 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 337903 [5DARDANELLE 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3591 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 12.45 | PASS | 34.396 | PASS | 34295.9888 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 12.45 | PASS | 82.8313 | PASS | 82731.304 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 7.0197 | PASS | 13.0508 | PASS | 12950.8336 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505596 [EXPLOR 4 138.00] CKT 1 | 12.5996 | PASS | 18.4266 | PASS | 18326.6273 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4499 | PASS | 34.3967 | PASS | 34296.6893 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4499 | PASS | 82.8127 | PASS | 82712.7366 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 7.0187 | PASS | 13.2889 | PASS | 13188.9447 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.5994 | PASS | 18.4265 | PASS | 18326.4767 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 12.4502 | PASS | 34.3943 | PASS | 34294.2654 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 12.4502 | PASS | 82.8712 | PASS | 82771.2121 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 7.3462 | PASS | 14.3147 | PASS | 14214.6748 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 505650 [GERTY 4 138.00] CKT 1 | 12.6015 | PASS | 18.4263 | PASS | 18326.305 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 12.4502 | PASS | 34.3943 | PASS | 34294.3182 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 12.4502 | PASS | 82.8704 | PASS | 82770.3863 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 7.3459 | PASS | 14.3006 | PASS | 14200.5512 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505598 [ALLEN 4 138.00] TO BUS 510916 [ALLEN--4 138.00] CKT 1 | 12.6015 | PASS | 18.4263 | PASS | 18326.3195 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4502 | PASS | 34.3947 | PASS | 34294.6747 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4502 | PASS | 82.8609 | PASS | 82760.9395 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 6.9551 | PASS | 13.1258 | PASS | 13025.7965 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.4136 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4781 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 12.4503 | PASS | 82.8665 | PASS | 82766.537 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 7.3436 | PASS | 14.2679 | PASS | 14167.9411 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 505604 [DENISON4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3561 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4919 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 12.4503 | PASS | 82.866 | PASS | 82766.0389 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 7.3366 | PASS | 14.2297 | PASS | 14129.7336 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515157 [BROWN 4 138.00] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4213 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5032 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 12.4503 | PASS | 82.8659 | PASS | 82765.8723 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 7.3425 | PASS | 14.2716 | PASS | 14171.6146 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 515159 [COLBRTP4 138.00] CKT 1 | 12.6016 | PASS | 18.4264 | PASS | 18326.3655 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4984 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 12.4503 | PASS | 82.8659 | PASS | 82765.9263 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 7.3423 | PASS | 14.272 | PASS | 14172.0291 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 520963 [KRSEY2_4 138.00] CKT 1 | 12.6016 | PASS | 18.4264 | PASS | 18326.3593 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.565 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 12.4502 | PASS | 82.8633 | PASS | 82763.3005 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 7.2902 | PASS | 13.9827 | PASS | 13882.6912 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521044 [RUSSETT4 138.00] CKT 1 | 12.6008 | PASS | 18.4263 | PASS | 18326.3262 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4959 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 12.4502 | PASS | 82.8649 | PASS | 82764.859 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 7.3182 | PASS | 14.1308 | PASS | 14030.7623 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505602 [S BROWN4 138.00] TO BUS 521049 [SCLMNJC4 138.00] CKT 1 | 12.5993 | PASS | 18.4271 | PASS | 18327.1098 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 12.4504 | PASS | 34.3957 | PASS | 34295.6557 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 12.4504 | PASS | 82.8405 | PASS | 82740.5247 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 7.1503 | PASS | 13.1588 | PASS | 13058.8489 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505665 [CENTRATAP4 138.00] CKT 1 | 12.5994 | PASS | 18.4272 | PASS | 18327.2129 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 12.4503 | PASS | 34.395 | PASS | 34295.0453 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 12.4503 | PASS | 82.8543 | PASS | 82754.3347 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 7.2517 | PASS | 13.7176 | PASS | 13617.5617 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505668 [CENTRAHOMA1 13.200] CKT 1 | 12.6005 | PASS | 18.4268 | PASS | 18326.7596 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 12.4503 | PASS | 34.395 | PASS | 34295.032 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 12.4503 | PASS | 82.8543 | PASS | 82754.3346 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 7.2543 | PASS | 13.7345 | PASS | 13634.5458 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505666 [CENTRAHOMA4 138.00] TO BUS 505670 [CENTRAHOM_1 13.200] CKT 1 | 12.6005 | PASS | 18.4267 | PASS | 18326.7483 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 12.4502 | PASS | 34.3943 | PASS | 34294.2658 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 12.4502 | PASS | 82.8706 | PASS | 82770.6356 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 7.3342 | PASS | 15.0206 | PASS | 14920.6277 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 505672 [AHLOSO4 138.00] TO BUS 505671 [UNION VLY4 138.00] CKT 1 | 12.6012 | PASS | 18.4263 | PASS | 18326.2561 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 10.6262 | PASS | 41.6352 | PASS | 41535.1794 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 10.6262 | PASS | 42.9838 | PASS | 42883.8402 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 7.3444 | PASS | 14.2645 | PASS | 14164.5243 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 507192 [WBOONVL5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3682 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 9.3466 | PASS | 81.9369 | PASS | 81836.9284 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 9.3466 | PASS | 29.1577 | PASS | 29057.7118 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.7447 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507190 [NMAGZIN5 161.00] TO BUS 515316 [BRANCH 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 5.4886 | FAIL | 38.6622 | PASS | 38562.2086 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 5.4886 | FAIL | 23.2141 | PASS | 23114.1021 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 7.3446 | PASS | 14.2639 | PASS | 14163.8957 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 507195 [MAGZREC5 161.00] TO BUS 788938 [ERAS-05-TAP 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3819 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 12.443 | PASS | 34.3965 | PASS | 34296.4851 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 12.443 | PASS | 82.6625 | PASS | 82562.4822 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 7.3445 | PASS | 14.263 | PASS | 14163.0006 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 12.6008 | PASS | 18.4262 | PASS | 18326.1837 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.441 | PASS | 34.4459 | PASS | 34345.9302 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.441 | PASS | 81.6365 | PASS | 81536.5474 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 7.3453 | PASS | 14.2583 | PASS | 14158.3053 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 12.6007 | PASS | 18.4263 | PASS | 18326.3355 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 12.4503 | PASS | 34.3983 | PASS | 34298.29 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 12.4503 | PASS | 82.767 | PASS | 82667.0223 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 7.3448 | PASS | 14.264 | PASS | 14164.0166 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140345.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3933 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.4501 | PASS | 34.3966 | PASS | 34296.6156 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.4501 | PASS | 82.8127 | PASS | 82712.744 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 7.3435 | PASS | 14.2659 | PASS | 14165.8568 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.6 | PASS | 18.4264 | PASS | 18326.4152 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4692 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 12.4503 | PASS | 82.8674 | PASS | 82767.4358 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 7.3438 | PASS | 14.2652 | PASS | 14165.1607 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.500] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3709 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.6424 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4503 | PASS | 82.8656 | PASS | 82765.6108 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 7.3443 | PASS | 14.2646 | PASS | 14164.5795 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.6299 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 12.4503 | PASS | 82.8656 | PASS | 82765.603 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 7.3443 | PASS | 14.2646 | PASS | 14164.5783 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] TO BUS 509882 [RSST1 T1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 12.4504 | PASS | 34.4071 | PASS | 34307.1116 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 12.4504 | PASS | 82.5611 | PASS | 82461.1345 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 7.3479 | PASS | 14.258 | PASS | 14158.0343 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146345.00] CKT 1 | 12.601 | PASS | 18.4265 | PASS | 18326.5341 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.4499 | PASS | 34.399 | PASS | 34298.9704 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.4499 | PASS | 82.7548 | PASS | 82654.7576 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 7.3406 | PASS | 14.2698 | PASS | 14169.7882 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 12.5932 | PASS | 18.4275 | PASS | 18327.4957 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 12.4503 | PASS | 34.3947 | PASS | 34294.6557 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 12.4503 | PASS | 82.8655 | PASS | 82765.4633 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 7.3443 | PASS | 14.2646 | PASS | 14164.5678 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] TO BUS 509876 [RSST2 T1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.364 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4684 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 12.4503 | PASS | 82.867 | PASS | 82767.0226 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 7.3444 | PASS | 14.2646 | PASS | 14164.6225 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3652 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 12.4503 | PASS | 34.3944 | PASS | 34294.3794 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 12.4503 | PASS | 82.8688 | PASS | 82768.8024 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.767 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3631 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 12.4499 | PASS | 34.3948 | PASS | 34294.8449 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 12.4499 | PASS | 82.8518 | PASS | 82751.774 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 7.3444 | PASS | 14.2646 | PASS | 14164.6021 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 12.6014 | PASS | 18.4263 | PASS | 18326.3406 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 12.4503 | PASS | 34.3944 | PASS | 34294.3797 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 12.4503 | PASS | 82.8688 | PASS | 82768.8061 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7746 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3622 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 12.4503 | PASS | 34.3944 | PASS | 34294.4062 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 12.4503 | PASS | 82.8681 | PASS | 82768.1339 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7604 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3629 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.3771 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 12.4502 | PASS | 82.8683 | PASS | 82768.266 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8152 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509881 [ONETA1-1 13.800] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3594 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 12.4502 | PASS | 34.3944 | PASS | 34294.3913 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 12.4502 | PASS | 82.8683 | PASS | 82768.2562 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8086 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509868 [ONETA2-1 34.500] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3595 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 12.4502 | PASS | 34.3944 | PASS | 34294.3887 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 12.4502 | PASS | 82.8679 | PASS | 82767.9421 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 7.3444 | PASS | 14.2648 | PASS | 14164.8143 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] TO BUS 509874 [ONETA5-1 34.500] CKT 3 | 12.6015 | PASS | 18.4264 | PASS | 18326.3594 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4494 | PASS | 34.397 | PASS | 34296.9501 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4494 | PASS | 82.7962 | PASS | 82696.1796 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 7.3448 | PASS | 14.2638 | PASS | 14163.7956 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.6014 | PASS | 18.4263 | PASS | 18326.2883 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 12.4505 | PASS | 34.3969 | PASS | 34296.8986 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 12.4505 | PASS | 82.8142 | PASS | 82714.1874 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 7.3448 | PASS | 14.2636 | PASS | 14163.5854 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.000] TO BUS 511954 [COGEN S1 13.800] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4099 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 12.4505 | PASS | 34.3969 | PASS | 34296.8986 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 12.4505 | PASS | 82.8142 | PASS | 82714.1874 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 7.3448 | PASS | 14.2636 | PASS | 14163.5854 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.000] TO BUS 511956 [COGEN S2 13.800] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4099 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 12.4506 | PASS | 34.3973 | PASS | 34297.3221 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 12.4506 | PASS | 82.8069 | PASS | 82706.8602 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 7.345 | PASS | 14.2632 | PASS | 14163.2389 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.000] TO BUS 511958 [COGEN S3 13.800] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4135 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 12.4506 | PASS | 34.3996 | PASS | 34299.6113 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 12.4506 | PASS | 82.7528 | PASS | 82652.8438 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 7.3452 | PASS | 14.2627 | PASS | 14162.7161 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.000] CKT 1 | 12.6012 | PASS | 18.4264 | PASS | 18326.4229 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 12.4505 | PASS | 34.3981 | PASS | 34298.1189 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 12.4505 | PASS | 82.7863 | PASS | 82686.2551 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 7.345 | PASS | 14.2633 | PASS | 14163.3353 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.000] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4051 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 12.4505 | PASS | 34.398 | PASS | 34297.9851 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 12.4505 | PASS | 82.7889 | PASS | 82688.8671 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 7.3449 | PASS | 14.2634 | PASS | 14163.4266 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.000] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4052 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 12.4506 | PASS | 34.3996 | PASS | 34299.6113 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 12.4506 | PASS | 82.7528 | PASS | 82652.8438 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 7.3452 | PASS | 14.2627 | PASS | 14162.7161 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.000] CKT 1 | 12.6012 | PASS | 18.4264 | PASS | 18326.4229 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 12.4505 | PASS | 34.3981 | PASS | 34298.1189 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 12.4505 | PASS | 82.7863 | PASS | 82686.2551 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 7.345 | PASS | 14.2633 | PASS | 14163.3353 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.000] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4051 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 12.4505 | PASS | 34.398 | PASS | 34297.9851 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 12.4505 | PASS | 82.7889 | PASS | 82688.8671 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 7.3449 | PASS | 14.2634 | PASS | 14163.4266 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.000] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.4052 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5557 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4503 | PASS | 82.8651 | PASS | 82765.1 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7917 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.6011 | PASS | 18.4264 | PASS | 18326.3869 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4761 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 12.4502 | PASS | 82.8662 | PASS | 82766.2221 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.925 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] TO BUS 509894 [TNO2-1 34.500] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4707 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 12.4502 | PASS | 82.8657 | PASS | 82765.669 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.9186 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] TO BUS 509872 [SAPLPRD1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4503 | PASS | 34.3947 | PASS | 34294.6549 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.4503 | PASS | 82.8655 | PASS | 82765.4716 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 7.3443 | PASS | 14.2646 | PASS | 14164.562 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509875 [RSS T2 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.364 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5255 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 12.4503 | PASS | 82.8645 | PASS | 82764.5307 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 7.3442 | PASS | 14.2651 | PASS | 14165.0654 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3654 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 12.4509 | PASS | 34.3971 | PASS | 34297.0855 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 12.4509 | PASS | 82.8133 | PASS | 82713.3489 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 7.3457 | PASS | 14.2628 | PASS | 14162.8151 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3688 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4497 | PASS | 34.3949 | PASS | 34294.8745 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4497 | PASS | 82.8422 | PASS | 82742.2253 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 7.3437 | PASS | 14.2651 | PASS | 14165.1386 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.6007 | PASS | 18.4264 | PASS | 18326.4491 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.6119 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 12.4502 | PASS | 82.8628 | PASS | 82762.7728 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7658 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 763113 [G18-079-TAP 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3587 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.612 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 12.4502 | PASS | 82.8628 | PASS | 82762.771 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7661 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510379 [DELWARE4 138.00] TO BUS 510380 [DELWARE7 345.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3588 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4479 | PASS | 34.3945 | PASS | 34294.5235 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.4479 | PASS | 82.8162 | PASS | 82716.2253 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 7.3446 | PASS | 14.2638 | PASS | 14163.8031 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 12.6009 | PASS | 18.426 | PASS | 18326.0207 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4387 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.4502 | PASS | 82.8666 | PASS | 82766.5953 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 7.2431 | PASS | 14.0443 | PASS | 13944.3317 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 505600 [TUPELO 4 138.00] CKT 1 | 12.601 | PASS | 18.4264 | PASS | 18326.3541 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4476 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 12.4502 | PASS | 82.8662 | PASS | 82766.1597 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 7.244 | PASS | 13.957 | PASS | 13856.9702 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510880 [COALGTP4 138.00] CKT 1 | 12.6011 | PASS | 18.4264 | PASS | 18326.3949 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 12.4502 | PASS | 34.3943 | PASS | 34294.285 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 12.4502 | PASS | 82.8709 | PASS | 82770.9444 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 7.3469 | PASS | 14.383 | PASS | 14282.9879 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 510881 [ALLENGT4 138.00] TO BUS 510935 [EXPCOLT4 138.00] CKT 1 | 12.6012 | PASS | 18.4263 | PASS | 18326.2628 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 12.4507 | PASS | 34.3955 | PASS | 34295.4987 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 12.4507 | PASS | 82.8505 | PASS | 82750.4875 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 7.3469 | PASS | 14.258 | PASS | 14158.0017 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511920 [CDW-SUB 345.00] CKT 1 | 12.6068 | PASS | 18.4435 | PASS | 18343.5171 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 12.4506 | PASS | 34.3952 | PASS | 34295.2167 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 12.4506 | PASS | 82.8551 | PASS | 82755.1271 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 7.3457 | PASS | 14.2625 | PASS | 14162.464 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511409 [TREASILD7 345.00] TO BUS 511992 [HVBUS 345.00] CKT 1 | 12.6035 | PASS | 18.427 | PASS | 18327.0192 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5631 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 12.4503 | PASS | 82.8646 | PASS | 82764.6475 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 7.3428 | PASS | 14.2629 | PASS | 14162.909 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511421 [VERDEN 4 138.00] TO BUS 511502 [N29CHIK4 138.00] CKT 1 | 12.3933 | PASS | 18.4498 | PASS | 18349.7529 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4431 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 12.4502 | PASS | 82.867 | PASS | 82766.9602 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.9187 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511423 [FLE TAP4 138.00] TO BUS 511422 [FLETCHR4 138.00] CKT 1 | 12.6009 | PASS | 18.4256 | PASS | 18325.5823 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.473 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.446 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8387 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511428 [LG-YEAR4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3718 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 12.4502 | PASS | 34.3942 | PASS | 34294.2445 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 12.4502 | PASS | 82.8697 | PASS | 82769.7305 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 7.3438 | PASS | 14.2657 | PASS | 14165.6643 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511431 [LWS S4 138.00] CKT 1 | 12.5994 | PASS | 18.4242 | PASS | 18324.2044 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4611 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7678 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7898 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511439 [LWSTAP 4 138.00] TO BUS 511512 [RPPAPER4 138.00] CKT 1 | 12.6018 | PASS | 18.4264 | PASS | 18326.3844 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4936 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 12.4503 | PASS | 82.8656 | PASS | 82765.6419 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 7.3439 | PASS | 14.2654 | PASS | 14165.3602 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511445 [CARNEG-4 138.00] TO BUS 511463 [HOB-JCT4 138.00] CKT 1 | 12.3881 | PASS | 18.4477 | PASS | 18347.6854 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4605 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7743 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8431 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3592 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 12.4502 | PASS | 34.3946 | PASS | 34294.559 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 12.4502 | PASS | 82.8639 | PASS | 82763.9316 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 7.3434 | PASS | 14.263 | PASS | 14163.0408 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511584 [O.K.U.2-7 345.00] CKT Z1 | 12.5665 | PASS | 18.4302 | PASS | 18330.2449 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 12.451 | PASS | 34.3963 | PASS | 34296.2892 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 12.451 | PASS | 82.8362 | PASS | 82736.2306 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 7.3476 | PASS | 14.2597 | PASS | 14159.7084 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511999 [DVRSION-WIND345.00] CKT 1 | 12.6028 | PASS | 18.4277 | PASS | 18327.6801 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.5569 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 12.4502 | PASS | 82.864 | PASS | 82763.9513 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 7.3433 | PASS | 14.263 | PASS | 14163.039 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 525750 [G18-015-TAP 345.00] CKT 1 | 12.5659 | PASS | 18.4303 | PASS | 18330.2978 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4722 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 12.4503 | PASS | 82.8663 | PASS | 82766.2663 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 7.344 | PASS | 14.2655 | PASS | 14165.5385 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 999995 [ZSWSH_999995345.00] CKT 1 | 12.6043 | PASS | 18.4254 | PASS | 18325.3901 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511436 [COMANC-2 69.000] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4868 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511436 [COMANC-2 69.000] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.4335 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511436 [COMANC-2 69.000] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7824 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511436 [COMANC-2 69.000] CKT 1 | 12.5894 | PASS | 18.4296 | PASS | 18329.6336 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4913 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 12.4503 | PASS | 82.8662 | PASS | 82766.2426 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 7.3441 | PASS | 14.265 | PASS | 14165.0301 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511469 [LGORE-N2 69.000] CKT 1 | 12.5941 | PASS | 18.4394 | PASS | 18339.3935 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 12.4501 | PASS | 34.3941 | PASS | 34294.0728 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 12.4501 | PASS | 82.8722 | PASS | 82772.2108 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 7.3434 | PASS | 14.2664 | PASS | 14166.3845 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511470 [LGORE-S2 69.000] CKT 1 | 12.5984 | PASS | 18.4226 | PASS | 18322.5503 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4612 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7668 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.7452 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.6011 | PASS | 18.4264 | PASS | 18326.4457 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4612 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.4503 | PASS | 82.8668 | PASS | 82766.7665 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 7.3444 | PASS | 14.2647 | PASS | 14164.7335 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511466 [L.E.S.-2 69.000] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.6011 | PASS | 18.4265 | PASS | 18326.4501 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5335 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4503 | PASS | 82.8654 | PASS | 82765.3956 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.344 | PASS | 14.2644 | PASS | 14164.3701 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.5839 | PASS | 18.4304 | PASS | 18330.4217 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4813 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 12.4503 | PASS | 82.8665 | PASS | 82766.5436 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 7.3443 | PASS | 14.2641 | PASS | 14164.0644 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511414 [LES#4-1 13.800] CKT 1 | 12.5818 | PASS | 18.4329 | PASS | 18332.9342 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4959 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 12.4503 | PASS | 82.8664 | PASS | 82766.374 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 7.344 | PASS | 14.2638 | PASS | 14163.8176 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] TO BUS 511411 [LES#5-1 13.800] CKT 2 | 12.568 | PASS | 18.4389 | PASS | 18338.873 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4502 | PASS | 34.3947 | PASS | 34294.6903 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4502 | PASS | 82.8591 | PASS | 82759.0665 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 7.3405 | PASS | 14.259 | PASS | 14158.9919 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4988 | PASS | 18.4408 | PASS | 18340.8309 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 12.4502 | PASS | 34.3943 | PASS | 34294.2647 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 12.4502 | PASS | 82.8695 | PASS | 82769.5074 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 7.3439 | PASS | 14.2657 | PASS | 14165.6526 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511430 [LWS N4 138.00] CKT 1 | 12.601 | PASS | 18.4242 | PASS | 18324.1791 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4749 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7611 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.7408 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511471 [LWS-NTP4 138.00] TO BUS 511509 [53CACHE4 138.00] CKT 1 | 12.6017 | PASS | 18.4264 | PASS | 18326.3986 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4752 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 12.4503 | PASS | 82.8664 | PASS | 82766.4209 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8237 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511474 [SHERID4 138.00] TO BUS 511537 [ARTVLTP4 138.00] CKT 1 | 12.6018 | PASS | 18.4264 | PASS | 18326.3938 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4318 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 12.4502 | PASS | 82.8674 | PASS | 82767.4225 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14164.9869 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.400] CKT 1 | 12.5977 | PASS | 18.4233 | PASS | 18323.2681 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4324 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 12.4502 | PASS | 82.8674 | PASS | 82767.4156 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14164.9805 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.400] CKT 1 | 12.5979 | PASS | 18.4233 | PASS | 18323.3011 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 12.451 | PASS | 34.3964 | PASS | 34296.3743 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 12.451 | PASS | 82.8345 | PASS | 82734.5377 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 7.3465 | PASS | 14.2549 | PASS | 14154.8805 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.000] CKT 1 | 11.3373 | PASS | 18.7115 | PASS | 18611.5136 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4859 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 12.4503 | PASS | 82.8666 | PASS | 82766.6396 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.3446 | PASS | 14.2643 | PASS | 14164.3279 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 7.6129 | PASS | 19.8213 | PASS | 19721.293 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 12.4506 | PASS | 34.3952 | PASS | 34295.1649 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 12.4506 | PASS | 82.8557 | PASS | 82755.7359 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 7.3456 | PASS | 14.2608 | PASS | 14160.7638 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.800] TO BUS 511850 [SWS NG5 13.800] CKT 1 | 12.1736 | PASS | 18.5464 | PASS | 18446.3645 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5247 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 12.4503 | PASS | 82.8653 | PASS | 82765.2976 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 7.3435 | PASS | 14.2622 | PASS | 14162.2451 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511483 [NORGE--4 138.00] TO BUS 511449 [CORNVIL4 138.00] CKT 1 | 12.3842 | PASS | 18.4503 | PASS | 18350.2772 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4938 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 12.4502 | PASS | 82.866 | PASS | 82766.0206 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 7.3439 | PASS | 14.2647 | PASS | 14164.7194 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511486 [ELGINJT4 138.00] TO BUS 511487 [ELGINJT2 69.000] TO BUS 511412 [ELGJT1-1 13.800] CKT 1 | 12.5896 | PASS | 18.4209 | PASS | 18320.9276 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5062 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4503 | PASS | 82.8659 | PASS | 82765.8892 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.3442 | PASS | 14.2649 | PASS | 14164.9403 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511488 [112GORE4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.5987 | PASS | 18.4293 | PASS | 18329.3408 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5493 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.4503 | PASS | 82.865 | PASS | 82765.0315 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.344 | PASS | 14.264 | PASS | 14163.9949 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511494 [COMMTAP4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.5816 | PASS | 18.4311 | PASS | 18331.0848 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4209 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 12.4502 | PASS | 82.8672 | PASS | 82767.2055 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 7.3443 | PASS | 14.265 | PASS | 14165.0204 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511429 [L AIRGS4 138.00] CKT 1 | 12.6011 | PASS | 18.4259 | PASS | 18325.9064 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.5099 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 12.4503 | PASS | 82.8657 | PASS | 82765.6584 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 7.3444 | PASS | 14.2647 | PASS | 14164.6797 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511510 [LAIRGST4 138.00] TO BUS 511500 [CACHETP4 138.00] CKT 1 | 12.5822 | PASS | 18.4336 | PASS | 18333.5727 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 12.4504 | PASS | 34.3948 | PASS | 34294.8282 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 12.4504 | PASS | 82.8612 | PASS | 82761.1743 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 7.3452 | PASS | 14.2634 | PASS | 14163.3901 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511586 [TONKAWA4 138.00] TO BUS 511600 [HVBUS 138.00] CKT 1 | 12.6084 | PASS | 18.4301 | PASS | 18330.1144 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4502 | PASS | 34.3947 | PASS | 34294.6828 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4502 | PASS | 82.8593 | PASS | 82759.3423 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 7.3408 | PASS | 14.2589 | PASS | 14158.8655 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 500001 [COMANC7_TAP 345.00] CKT 1 | 12.4986 | PASS | 18.4409 | PASS | 18340.947 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4609 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.774 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8485 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 511607 [O.K.U.3-7 345.00] TO BUS 999994 [ZSWSH_999994345.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3603 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4354 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 12.4502 | PASS | 82.8674 | PASS | 82767.4247 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8325 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512625 [MAIDTP2 69.000] TO BUS 512671 [HUNT 2 69.000] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3616 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4468 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 12.4502 | PASS | 82.8676 | PASS | 82767.6358 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8276 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512681 [AMERCAST S2 69.000] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3617 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 12.4503 | PASS | 34.3942 | PASS | 34294.1554 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 12.4503 | PASS | 82.8736 | PASS | 82773.5658 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14165.0096 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512698 [REDDEN 2 69.000] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3609 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4481 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 12.4502 | PASS | 82.8671 | PASS | 82767.1012 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8404 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512836 [MAITER1 1 13.200] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3604 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.4613 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 12.4502 | PASS | 82.8668 | PASS | 82766.7655 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8412 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512626 [MAID 2 69.000] TO BUS 512648 [MAID 5 161.00] TO BUS 512837 [MAITER2 1 13.200] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3604 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4761 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4502 | PASS | 82.8653 | PASS | 82765.2668 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7918 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3554 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 12.4503 | PASS | 34.395 | PASS | 34294.9996 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 12.4503 | PASS | 82.8547 | PASS | 82754.6943 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 7.3445 | PASS | 14.2646 | PASS | 14164.591 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512629 [DRYGULCH5 161.00] TO BUS 512858 [GEN-2017-073161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3614 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 12.4495 | PASS | 34.3957 | PASS | 34295.7208 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 12.4495 | PASS | 82.8205 | PASS | 82720.4859 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 7.3442 | PASS | 14.265 | PASS | 14165.0353 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512637 [412SUB 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3604 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4386 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.4502 | PASS | 82.867 | PASS | 82767.0091 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8231 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512654 [PENSA 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3576 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 12.4503 | PASS | 34.3945 | PASS | 34294.5037 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 12.4503 | PASS | 82.8661 | PASS | 82766.0565 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 7.3444 | PASS | 14.2648 | PASS | 14164.8412 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512770 [KERR BRK1 5 161.00] CKT Z0 | 12.6015 | PASS | 18.4264 | PASS | 18326.3602 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 12.4503 | PASS | 34.3945 | PASS | 34294.5036 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 12.4503 | PASS | 82.8661 | PASS | 82766.0566 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 7.3444 | PASS | 14.2648 | PASS | 14164.841 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512771 [KERR BRK4 5 161.00] CKT Z0 | 12.6015 | PASS | 18.4264 | PASS | 18326.3602 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.5803 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 12.4502 | PASS | 82.8634 | PASS | 82763.3547 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8416 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3617 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 12.4502 | PASS | 34.3946 | PASS | 34294.5804 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 12.4502 | PASS | 82.8634 | PASS | 82763.354 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8415 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512635 [KERR GR5 161.00] TO BUS 512805 [SALNCRK5 161.00] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3617 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.5509 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 12.4502 | PASS | 82.8646 | PASS | 82764.5924 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8115 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 300993 [5ELMCRK 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3599 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4774 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 12.4503 | PASS | 82.8662 | PASS | 82766.2079 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.843 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512833 [CATTER1 1 13.800] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.361 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4773 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 12.4503 | PASS | 82.8662 | PASS | 82766.2095 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8362 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512636 [CATSAGR4 138.00] TO BUS 512834 [CATTER2 1 13.800] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3613 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 12.4503 | PASS | 34.3945 | PASS | 34294.4767 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 12.4503 | PASS | 82.8662 | PASS | 82766.2156 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 7.3444 | PASS | 14.2648 | PASS | 14164.8366 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512638 [CATSAGR5 161.00] TO BUS 512623 [CATSAGD4 138.00] TO BUS 512835 [CATTER3 1 13.800] CKT 3 | 12.6015 | PASS | 18.4264 | PASS | 18326.3613 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 12.4467 | PASS | 34.4101 | PASS | 34310.1471 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 12.4467 | PASS | 82.4764 | PASS | 82376.4054 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 7.3442 | PASS | 14.2636 | PASS | 14163.6056 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 505560 [FT GIB 5 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3554 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 12.4491 | PASS | 34.3966 | PASS | 34296.5536 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 12.4491 | PASS | 82.8066 | PASS | 82706.5686 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 7.3437 | PASS | 14.2653 | PASS | 14165.2512 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512640 [OKAYGR 5 161.00] TO BUS 512646 [OKAYGR 2 69.000] TO BUS 512848 [OKAY1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.366 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4733 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.78 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8488 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3603 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4733 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 12.4503 | PASS | 82.8668 | PASS | 82766.78 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 7.3444 | PASS | 14.2648 | PASS | 14164.8488 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512648 [MAID 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3603 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 12.4502 | PASS | 34.4021 | PASS | 34302.1129 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 12.4502 | PASS | 82.6772 | PASS | 82577.2342 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 7.3462 | PASS | 14.2619 | PASS | 14161.9259 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512688 [GRDA17-1 22.800] CKT 1 | 12.6013 | PASS | 18.4264 | PASS | 18326.3619 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 12.45 | PASS | 34.3954 | PASS | 34295.3699 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 12.45 | PASS | 82.8425 | PASS | 82742.5086 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.8872 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512821 [GRDA1 13.800] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3615 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 12.4501 | PASS | 34.3956 | PASS | 34295.5521 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 12.4501 | PASS | 82.8386 | PASS | 82738.5967 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 7.3444 | PASS | 14.2647 | PASS | 14164.7421 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512650 [GRDA1 7 345.00] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512826 [GRDA2 1 13.800] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3591 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4664 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 12.4502 | PASS | 82.8669 | PASS | 82766.8606 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.798 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 300997 [5KETONVL 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3687 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4681 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 12.4502 | PASS | 82.8663 | PASS | 82766.3137 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.8562 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512814 [CLARMR1 13.800] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3609 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 12.4502 | PASS | 34.3945 | PASS | 34294.4682 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 12.4502 | PASS | 82.8663 | PASS | 82766.3137 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 7.3443 | PASS | 14.2649 | PASS | 14164.8562 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512679 [CLARMR 2 69.000] TO BUS 512815 [CLARMR2 13.800] CKT 2 | 12.6015 | PASS | 18.4264 | PASS | 18326.3609 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 12.4502 | PASS | 34.3951 | PASS | 34295.1112 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 12.4502 | PASS | 82.8493 | PASS | 82749.2506 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.9192 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512651 [CLARMR 5 161.00] TO BUS 512707 [CLARMR 4 138.00] TO BUS 512813 [CLARMR4 13.800] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3648 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.4502 | PASS | 34.395 | PASS | 34294.9729 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.4502 | PASS | 82.8531 | PASS | 82753.0972 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 7.3439 | PASS | 14.2655 | PASS | 14165.5351 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 12.6006 | PASS | 18.4264 | PASS | 18326.4154 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 12.4502 | PASS | 34.395 | PASS | 34295.036 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 12.4502 | PASS | 82.8518 | PASS | 82751.7876 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 7.3438 | PASS | 14.2656 | PASS | 14165.5935 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 12.6006 | PASS | 18.4264 | PASS | 18326.4134 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 12.4503 | PASS | 34.3946 | PASS | 34294.5511 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 12.4503 | PASS | 82.8653 | PASS | 82765.3414 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 7.3441 | PASS | 14.2652 | PASS | 14165.1672 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.800] CKT 1 | 12.6008 | PASS | 18.4264 | PASS | 18326.4181 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 12.4506 | PASS | 34.3932 | PASS | 34293.2308 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 12.4506 | PASS | 82.8983 | PASS | 82798.2626 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 7.3444 | PASS | 14.2649 | PASS | 14164.8821 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 300972 [2WAGNERW 69.000] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3576 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 12.4502 | PASS | 34.3949 | PASS | 34294.876 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 12.4502 | PASS | 82.8571 | PASS | 82757.1193 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.7791 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512690 [WAGNRTP2 69.000] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3613 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 12.4505 | PASS | 34.3932 | PASS | 34293.218 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 12.4505 | PASS | 82.8986 | PASS | 82798.5545 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 7.3444 | PASS | 14.2649 | PASS | 14164.8951 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512759 [WAGCTY22 69.000] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3575 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 12.4495 | PASS | 34.3963 | PASS | 34296.3216 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 12.4495 | PASS | 82.8165 | PASS | 82716.5429 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 7.344 | PASS | 14.265 | PASS | 14164.9832 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512697 [WAGNOR 2 69.000] TO BUS 512700 [WAGNOR 5 161.00] TO BUS 512818 [WAGNOR1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3647 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4452 | PASS | 34.4294 | PASS | 34329.3855 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4452 | PASS | 82.0291 | PASS | 81929.0674 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.344 | PASS | 14.2621 | PASS | 14162.0681 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512700 [WAGNOR 5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3886 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 12.4502 | PASS | 34.3944 | PASS | 34294.4359 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 12.4502 | PASS | 82.8674 | PASS | 82767.4228 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 7.3443 | PASS | 14.2648 | PASS | 14164.8322 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512727 [GRDA1 2 69.000] TO BUS 512656 [GRDA1 5 161.00] TO BUS 512816 [GRDA1 1 13.800] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3616 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4943 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4502 | PASS | 82.8656 | PASS | 82765.6004 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.3444 | PASS | 14.2649 | PASS | 14164.8558 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512742 [WMAIN ST5 161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3615 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.4475 | PASS | 34.3969 | PASS | 34296.9271 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.4475 | PASS | 82.7403 | PASS | 82640.2886 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 7.3437 | PASS | 14.2658 | PASS | 14165.7575 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 506935 [FLINTCR7 345.00] CKT 1 | 12.6014 | PASS | 18.4263 | PASS | 18326.3377 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 12.4503 | PASS | 34.3949 | PASS | 34294.8687 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 12.4503 | PASS | 82.8572 | PASS | 82757.2309 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 7.3444 | PASS | 14.2648 | PASS | 14164.8228 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512750 [TONECE7 345.00] TO BUS 512751 [TONECE5 161.00] TO BUS 512752 [TONECE1 13.200] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3612 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 12.4504 | PASS | 34.3952 | PASS | 34295.2331 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 12.4504 | PASS | 82.8495 | PASS | 82749.4564 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 7.3446 | PASS | 14.2645 | PASS | 14164.4866 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512785 [GEN-2017-061161.00] TO BUS 512786 [G17-061XFMR134.500] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.3619 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 12.4504 | PASS | 34.4007 | PASS | 34300.6621 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 12.4504 | PASS | 82.7155 | PASS | 82615.5234 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 7.3462 | PASS | 14.262 | PASS | 14161.9708 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512614 [GRECCTG_1 20.000] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3528 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 12.4505 | PASS | 34.3984 | PASS | 34298.4353 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 12.4505 | PASS | 82.7727 | PASS | 82672.6586 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 7.3456 | PASS | 14.263 | PASS | 14162.9841 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 512615 [GRECSTG_1 21.000] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3571 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4506 | PASS | 34.3942 | PASS | 34294.2249 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.4506 | PASS | 82.8798 | PASS | 82779.8031 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 7.3445 | PASS | 14.264 | PASS | 14163.9655 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 512865 [GREC TAP7 345.00] TO BUS 513596 [IGLOOV 7 345.00] CKT 1 | 12.6009 | PASS | 18.4265 | PASS | 18326.5001 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 12.4456 | PASS | 34.4323 | PASS | 34332.3047 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 12.4456 | PASS | 81.9437 | PASS | 81843.7238 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 7.3438 | PASS | 14.2635 | PASS | 14163.4886 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 513050 [LOCSTGV 5 161.00] TO BUS 301344 [5CDRCRST 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.398 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4502 | PASS | 34.3949 | PASS | 34294.8649 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.4502 | PASS | 82.8569 | PASS | 82756.9032 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 7.3443 | PASS | 14.2649 | PASS | 14164.8682 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 513570 [CHOUTEAUCRK5161.00] TO BUS 512656 [GRDA1 5 161.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3622 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4502 | PASS | 34.3946 | PASS | 34294.6161 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.4502 | PASS | 82.8618 | PASS | 82761.7865 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 7.3427 | PASS | 14.2673 | PASS | 14167.318 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514840 [JONESTP4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 12.6003 | PASS | 18.4266 | PASS | 18326.6321 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4547 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.4503 | PASS | 82.867 | PASS | 82767.0199 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 7.3443 | PASS | 14.2647 | PASS | 14164.721 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514842 [CHTWOOD4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 12.6015 | PASS | 18.4264 | PASS | 18326.4356 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4885 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 12.4503 | PASS | 82.8662 | PASS | 82766.2323 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 7.3441 | PASS | 14.2649 | PASS | 14164.8966 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514501 [KELLYAV4 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.3639 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 12.4502 | PASS | 34.3945 | PASS | 34294.4971 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 12.4502 | PASS | 82.8661 | PASS | 82766.1296 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 7.3439 | PASS | 14.2652 | PASS | 14165.1553 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514870 [STNWAL 4 138.00] CKT 1 | 12.6009 | PASS | 18.4265 | PASS | 18326.501 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4721 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.4503 | PASS | 82.8668 | PASS | 82766.7935 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 7.3443 | PASS | 14.2646 | PASS | 14164.5977 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514874 [REMNGPK4 138.00] TO BUS 514969 [NE30TH 2 138.00] CKT 1 | 12.6014 | PASS | 18.4264 | PASS | 18326.4003 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 12.4503 | PASS | 34.3945 | PASS | 34294.4583 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 12.4503 | PASS | 82.8675 | PASS | 82767.5499 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 7.3437 | PASS | 14.2587 | PASS | 14158.688 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 12.5689 | PASS | 18.4327 | PASS | 18332.6684 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 12.4503 | PASS | 34.3945 | PASS | 34294.4738 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 12.4503 | PASS | 82.8666 | PASS | 82766.6198 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 7.3443 | PASS | 14.2648 | PASS | 14164.8212 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.800] CKT 2 | 12.6016 | PASS | 18.4265 | PASS | 18326.4983 | 175 | 226.8
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 12.4503 | PASS | 34.3945 | PASS | 34294.4735 | 151.059 | 174.15
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-005 | Danville - Magazine 161kV Line | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 12.4503 | PASS | 82.867 | PASS | 82766.9664 | 151 | 174.82
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-022 | Monte Vista 138 kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 7.3443 | PASS | 14.2648 | PASS | 14164.8335 | 123 | 141.3
ERAS-2025-001 | 04 SOUTHEAST | 29SP | ERAS-2025-025 | Washita 138kV Substation | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.800] CKT 3 | 12.6016 | PASS | 18.4265 | PASS | 18326.4918 | 175 | 226.8