ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 3.2833 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 3.2833 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 3.2833 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532814 [FR4345KV-TAP345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 3.2858 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 3.2858 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 3.2858 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532999 [GEN-2016-111345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 3.2867 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 3.2867 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 3.2867 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 3.2842 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 3.2842 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 3.2842 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.2828 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.2828 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.2828 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 3.2823 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 3.2823 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 2 | 3.2823 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533416 [RENO 3 115.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 3.2865 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 3.2865 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533429 [MOUNDRG3 115.00] CKT 1 | 3.2865 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 3.2874 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 3.2874 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 533438 [WMCPHER3 115.00] CKT 1 | 3.2874 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.3684 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.3684 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.3684 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539740 [EDODGE 3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 3.2858 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 3.2858 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539783 [CRKCK 3 115.00] CKT 1 | 3.2858 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.0484 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.0484 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539696 [ST-JOHN3 115.00] CKT 1 | 2.0484 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2877 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2676 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2676 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2676 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2877 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 3.2891 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 3.2891 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 763758 [GEN-2019-044115.00] CKT 1 | 3.2891 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 3.2887 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539784 [ENSNGW 3 115.00] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 3.2879 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 3.2879 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541500 [KETCHEM7 345.00] CKT 1 | 3.2879 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 3.2887 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541501 [OSBORN7 345.00] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 3.2894 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 3.2894 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 3.2894 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546655 [KAW W 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546669 [WOLCOTT5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546677 [MAYWOOD2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546722 [MAYSOTH5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546684 [FIBGLAS5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546692 [QUINDA 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546693 [V WEST2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546694 [QUINDB 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 3.2844 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 3.2844 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 3.2844 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 2 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 3.2889 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 3.2889 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 3.2678 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 3.2678 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 3.2678 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 3.2896 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 3.2896 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523823 [CARPENTER 7345.00] TO BUS 764980 [GEN-2020-008345.00] CKT 1 | 3.2896 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.2829 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.2829 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.2829 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 2.5279 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 2.5279 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 530618 [HUNTSVL3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT 1 | 2.5279 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 2.5412 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 2.5412 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 530724 [CENTENNIAL3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 2.5412 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531379 [JONES3 115.00] TO BUS 531426 [JAMESON3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531392 [PIONTAP3 115.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531393 [PLYMELL3 115.00] TO BUS 531408 [PIERCVL3 115.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531400 [PK_GOAB3 115.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531440 [WILLIAM3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531420 [FLETCHR3 115.00] TO BUS 531399 [LAKIN 1 34.500] TO BUS 531500 [FLETCHER-1 13.200] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 3.2891 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 3.2891 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531459 [S2 GEN 1 13.800] CKT 1 | 3.2891 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 3.2888 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531461 [S4 GEN 1 13.200] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 3.2888 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531462 [S5 GEN 1 13.200] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531476 [SWNDTAP3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531480 [KSAVWTP3 115.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531421 [GC-C 1 34.500] TO BUS 531254 [GC-CITY1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531427 [GC-C2 1 34.500] TO BUS 531256 [GC-CTY 1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531445 [GRDNCTY3 115.00] TO BUS 531422 [GC-W 1 34.500] TO BUS 531255 [GCWHEAT1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 3.2916 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 3.2916 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531447 [HOLCGEN1 22.000] CKT 1 | 3.2916 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 3.2877 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531448 [HOLCOMB3 115.00] TO BUS 531449 [HOLCOMB7 345.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 3.2894 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 3.2894 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [SLMNFRK7 345.00] CKT 1 | 3.2894 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 3.2782 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 3.2782 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 3.2782 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGO1 1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531453 [MINGO2 1 13.800] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 3.2863 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 3.2863 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531433 [SCOTCTY3 115.00] CKT 1 | 3.2863 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531485 [CNTRLPL3 115.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 3.2871 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 3.2871 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531464 [SETAB 3 115.00] TO BUS 531465 [SETAB 7 345.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 3.2871 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.287 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.287 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.287 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 3.2866 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 3.2866 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 530583 [POSTROCK7 345.00] CKT 1 | 3.2866 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 3.2886 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 3.2874 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 3.2874 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 3.2874 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 3.2877 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-1 13.800] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 3.2682 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 3.2682 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531468 [SPERTER1 13.800] CKT 1 | 3.2682 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.2773 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.2773 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531501 [BUCKNER7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.2773 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 3.2889 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531502 [CIMRRN 7 345.00] TO BUS 531503 [CIMRRN 1 34.500] CKT 1 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 3.2888 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 531504 [CIMWD2 7 345.00] TO BUS 531505 [CIMWD2 1 34.500] TO BUS 531506 [CIMWD2-T 1 13.800] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 3.284 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 3.284 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532767 [GEARY 7 345.00] CKT 1 | 3.284 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 3.2861 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 3.2861 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 539863 [CIRRUS7 345.00] CKT 1 | 3.2861 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 3.2859 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 3.2859 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532773 [SUMMIT 7 345.00] TO BUS 532873 [SUMMIT 6 230.00] TO BUS 532813 [SUMMIT 1 14.400] CKT 1 | 3.2859 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 534109 [GEN-2016-073345.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 3.2856 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 3.2856 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 3.2856 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 3.2854 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 3.2854 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 3.2854 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 533069 [BUFFALO4 138.00] TO BUS 532820 [BUFFALO11 1 13.800] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 3.2864 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 3.2864 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 3.2864 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 3.2869 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 3.2869 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 3.2869 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 3.2886 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 532795 [FR2WEST7 345.00] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533131 [FR2ELV11 34.500] TO BUS 533127 [F2EAST11 13.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532792 [FR2EAST7 345.00] TO BUS 533132 [FR2ELV21 34.500] TO BUS 533128 [F2EAST21 13.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.2796 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.2796 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.2796 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 3.2886 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 3.2863 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 3.2863 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 3.2863 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532803 [BURNS 7 345.00] TO BUS 532790 [EXPED WF7 345.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532814 [FR4345KV-TAP345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532994 [WICHTA11_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.2886 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532997 [WICHTA12_4 138.00] TO BUS 533040 [EVANS N4 138.00] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.2848 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.2848 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532998 [G16-111-TAP 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 3.2848 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532999 [GEN-2016-111345.00] TO BUS 538002 [G16-111XFMR134.500] TO BUS 532836 [SIDNEY_SO_B113.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533071 [WACO 4 138.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 3.2878 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 3.2878 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 3.2878 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532798 [VIOLA 7 345.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 3.2834 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 3.2834 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532695 [HEC GT1 13.800] CKT 1 | 3.2834 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 2.5439 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 2.5439 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533412 [ARKVALJ3 115.00] CKT 1 | 2.5439 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 3.2868 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 3.2868 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533419 [HEC 3 115.00] CKT 1 | 3.2868 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 3.2683 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 3.2683 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 533421 [HEC GT 3 115.00] CKT 1 | 3.2683 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533413 [CIRCLE 3 115.00] TO BUS 532871 [CIRCLE 6 230.00] TO BUS 532892 [CIRCLE 1 13.800] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 3.2874 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 3.2874 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533414 [CITIES 3 115.00] CKT 1 | 3.2874 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 3.2861 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 3.2861 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533420 [WHARV3 115.00] CKT 1 | 3.2861 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533415 [DAVIS 3 115.00] TO BUS 533506 [DAVIS 2 69.000] TO BUS 533444 [DAVIS 1 34.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 3.284 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 3.284 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 3.284 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 3.2838 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 3.2838 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533416 [RENO 3 115.00] TO BUS 532771 [RENO 7 345.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 3.2838 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 3.2875 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 3.2875 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533369 [JADE 3 115.00] CKT 1 | 3.2875 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533430 [MNDRGCT3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 3.2878 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 3.2878 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533429 [MOUNDRG3 115.00] TO BUS 533013 [MOUND 4 138.00] TO BUS 533097 [MOUN 2X1 7.2000] CKT 1 | 3.2878 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 3.2879 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 3.2879 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533394 [CORONAD3 115.00] CKT 1 | 3.2879 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 3.288 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 3.288 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533428 [MCPHER 3 115.00] CKT 1 | 3.288 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533437 [MOHAWK3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 3.2866 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 3.2866 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 533438 [WMCPHER3 115.00] TO BUS 533439 [WHEATLD3 115.00] CKT 1 | 3.2866 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 3.2868 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 3.2868 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 3.2868 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539008 [MILAN_GOAB4 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 3.2842 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 3.2842 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539009 [CONWAY 4 138.00] TO BUS 539881 [SPRVLSTR 138.00] CKT 1 | 3.2842 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 2.3675 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 2.3675 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539010 [SADLHRN3 115.00] TO BUS 539648 [PRICHRD3 115.00] CKT 1 | 2.3675 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539645 [DCBEEF3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 3.2862 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 3.2862 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539646 [KISMET 3 115.00] CKT 1 | 3.2862 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539659 [CUDAHY 3 115.00] TO BUS 539706 [CUDAHY 1 34.500] TO BUS 539906 [CUDAHY-1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539699 [W-DODGE3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539727 [S-DODGE1 34.500] TO BUS 539930 [S-DODG-1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 3.288 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 3.288 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539688 [S-DODGE3 115.00] TO BUS 539747 [SDODG2 1 34.500] TO BUS 539947 [SDODG2 T 4.8000] CKT 1 | 3.288 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 3.1647 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 3.1647 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 530679 [SEWRDMW3 115.00] CKT 1 | 3.1647 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 2.5558 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 2.5558 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539692 [SEWARD 3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 2.5558 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539732 [SPEARVL1 34.500] TO BUS 539936 [SPERVLD1 13.800] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 3.2877 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539694 [SPEARVL3 115.00] TO BUS 539695 [SPEARVL6 230.00] TO BUS 539935 [SPERVLT1 13.800] CKT 1 | 3.2877 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 1.0583 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 1.0583 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539696 [ST-JOHN3 115.00] TO BUS 530624 [ST JOHN3 115.00] CKT Z1 | 1.0583 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539680 [N-DODGE3 115.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 3.2879 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 3.2879 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539740 [EDODGE 3 115.00] TO BUS 539739 [EDODGE 1 34.500] TO BUS 539942 [E-DODG-1 13.800] CKT 1 | 3.2879 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 3.2671 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 3.2671 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539763 [SSTARTP3 115.00] CKT 1 | 3.2671 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 3.2882 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539758 [FORD 3 115.00] TO BUS 539765 [FORD 1 34.500] TO BUS 539968 [FORD-T 1 13.800] CKT 1 | 3.2882 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 2 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2863 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2863 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539783 [CRKCK 3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.2863 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 3.2888 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539784 [ENSNGW 3 115.00] TO BUS 539785 [ENSIGNW1 34.500] TO BUS 539948 [ENSGNW-T 13.800] CKT 1 | 3.2888 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 3.2881 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 3.2881 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541200 [PHILL 7 345.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541414 [SIB REA1 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 542972 [HAWTH 7 345.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541201 [SIBLEY 7 345.00] TO BUS 541202 [SIBLEY 5 161.00] TO BUS 541360 [SIBLEY T 13.800] CKT 11 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541411 [MC REAC1 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541412 [MC REAC2 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541413 [MC REAC3 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT Z1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.288 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.288 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541500 [KETCHEM7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.288 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 3.2887 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541501 [OSBORN7 345.00] TO BUS 541502 [OSBORN_B1_1 34.500] TO BUS 541505 [OSBORN_TER_113.800] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.2887 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 3.2889 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541553 [OUTLAW_WFTP7345.00] CKT Z1 | 3.2889 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 3.2887 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541512 [ROCKCK_T1_1 34.500] TO BUS 541508 [ROCKCK_TR1_113.200] CKT 1 | 3.2887 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 3.2886 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 541511 [ROCKCK7 345.00] TO BUS 541515 [ROCKCK_T2_1 34.500] TO BUS 541509 [ROCKCK_TR2_113.200] CKT 1 | 3.2886 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546654 [SUNSET 5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546665 [TURNER 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546690 [KAW WST2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546655 [KAW W 5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546656 [MAYWOOD5 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546663 [GM PLT 5 161.00] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 543134 [WALDRON5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546669 [WOLCOTT5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546677 [MAYWOOD2 69.000] TO BUS 546670 [OAK KNOL 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546681 [MUNCIE 2 69.000] TO BUS 546687 [COL PAL2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546684 [FIBGLAS5 161.00] TO BUS 546667 [FAIRFX-5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546692 [QUINDA 2 69.000] TO BUS 546652 [QUIND 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546682 [EVERETT2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546694 [QUINDB 2 69.000] TO BUS 546695 [QUINDC 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546668 [PIPER 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546722 [MAYSOTH5 161.00] TO BUS 546742 [METRO 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546653 [NEARMAN5 161.00] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 546751 [NM4 BUS 161.00] TO BUS 546723 [NM CT4 1 13.200] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547459 [WWR477 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547462 [SVRCK469 5 161.00] TO BUS 547607 [JOP422 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547470 [JOP145 5 161.00] TO BUS 547539 [JOP145 2 69.000] TO BUS 547707 [JOP145 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 505486 [NEO SPA5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 2 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547592 [JOP389 2 69.000] TO BUS 547713 [JOP389 1 12.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547526 [JOP 64 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547555 [GAL278 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547539 [JOP145 2 69.000] TO BUS 547574 [JOP341 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547438 [EXP449T2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547592 [JOP389 2 69.000] TO BUS 547608 [JOP430 2 69.000] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763417 [GEN-2018-128345.00] TO BUS 763418 [G18-128-XFM134.500] CKT 1 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2833 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2833 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763421 [G18-128-TAP 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 3.2833 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 3.2891 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 3.2891 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 763758 [GEN-2019-044115.00] TO BUS 763759 [G19-044-XFM134.500] CKT 1 | 3.2891 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 3.2883 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 764310 [G20-079-TAP 161.00] TO BUS 764300 [GEN-2020-079161.00] CKT 1 | 3.2883 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.29 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.29 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 | 3.29 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 3.29 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 3.29 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 770039 [GEN-2023-SR2115.00] TO BUS 770038 [G23-SR28XFMR34.500] CKT 1 | 3.29 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 852252 [TEST-FR4 345.00] TO BUS 533143 [FR4 XMF1 34 34.500] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 3.2885 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 852253 [TEST-FR5-0 345.00] TO BUS 534103 [FR5-XFMR 34.500] CKT 1 | 3.2885 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 3.2775 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 3.2775 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 & 2 | 3.2775 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 3.284 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 3.284 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 539771 [NFTDODG3 115.00] TO BUS 539671 [FTDODGE3 115.00] CKT 1 & 2 | 3.284 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 3.2884 | FAIL | Kinsley 115 kV Substation | ERAS-2025-019
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 03 CENTRAL | 29SP | OPEN LINE FROM BUS 547483 [JOP389 5 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 & 2 | 3.2884 | FAIL | St. John 115 kV Substation | ERAS-2025-032
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7597 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.979 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9858 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 788941 [ERA-28-TAP 345.00] CKT 1 | 4.1916 | FAIL | Mahoney 230kV Substation | ERAS-2025-027
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 788941 [ERA-28-TAP 345.00] CKT 1 | 4.1916 | FAIL | Mahoney 230kV Substation | ERAS-2025-027
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 788941 [ERA-28-TAP 345.00] CKT 1 | 4.1916 | FAIL | Tuco-Yoakum 345kV Line | ERAS-2025-028
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 788941 [ERA-28-TAP 345.00] CKT 1 | 4.1916 | FAIL | Tuco-Yoakum 345kV Line | ERAS-2025-028
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 788941 [ERA-28-TAP 345.00] CKT 1 | 4.1916 | FAIL | Tuco-Yoakum 345kV Line | ERAS-2025-028
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.342 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1 | 3.1948 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1577 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.7546 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.9802 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.9871 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 789915 [ERA-030-TAP 230.00] CKT 1 | 2.3266 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | Oasis 230kV Substation | ERAS-2025-018
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030
ERAS-2025-001 | 05 SOUTHWEST | 29WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 & 2 | 2.1611 | FAIL | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS-2025-030

## JTIQ Participant Summary
JTIQ Participant Gen Number | Group | JTIQ Participant MW | Monthly Indicative JTIQ Generator Rate ($/MW-Mo) for JTIQ Upgrades | Monthly Indicative JTIQ Generator Charge = Monthly Indicative JTIQ Generator Rate * Generator Committed MW ($) | Annual Indicative JTIQ Generator Charge = Monthly Indicative JTIQ Generator Charge * 12 ($) | Total Indicative JTIQ Generator Charge = Sum of Indicative JTIQ Generator Charges over 20 years for each JTIQ Upgrade ($) | Net SPP JTIQ Security per MW ($) | SPP Security to be Collected from Generator ($) | Net MISO JTIQ Security per MW ($) | MISO Security to be Collected from Generator ($)
ERAS-2025-001 | 02 NEBRASKA | 104 | 608.71 | 63305.84 | 759670.08 | 15193401.6 | 24827 | 2582008 | 38754.65 | 4030483.6
ERAS-2025-003 | 04 SOUTHEAST | 186 | 608.71 | 113220.06 | 1358640.72 | 27172814.4 | 24827 | 4617822 | 38754.65 | 7208364.9
ERAS-2025-004 | 04 SOUTHEAST | 779 | 608.71 | 474185.09 | 5690221.08 | 113804421.6 | 24827 | 19340233 | 38754.65 | 30189872.35
ERAS-2025-005 | 04 SOUTHEAST | 150 | 608.71 | 91306.5 | 1095678 | 21913560 | 24827 | 3724050 | 38754.65 | 5813197.5
ERAS-2025-007 | 03 CENTRAL | 450.6 | 608.71 | 274284.726 | 3291416.712 | 65828334.24 | 24827 | 11187046.2 | 38754.65 | 17462845.29
ERAS-2025-009 | 04 SOUTHEAST | 450 | 608.71 | 273919.5 | 3287034 | 65740680 | 24827 | 11172150 | 38754.65 | 17439592.5
ERAS-2025-010 | 04 SOUTHEAST | 496 | 608.71 | 301920.16 | 3623041.92 | 72460838.4 | 24827 | 12314192 | 38754.65 | 19222306.4
ERAS-2025-011 | 01 NORTH | 750 | 608.71 | 456532.5 | 5478390 | 109567800 | 24827 | 18620250 | 38754.65 | 29065987.5
ERAS-2025-012 | 01 NORTH | 750 | 608.71 | 456532.5 | 5478390 | 109567800 | 24827 | 18620250 | 38754.65 | 29065987.5
ERAS-2025-013 | 03 CENTRAL | 450.6 | 608.71 | 274284.726 | 3291416.712 | 65828334.24 | 24827 | 11187046.2 | 38754.65 | 17462845.29
ERAS-2025-022 | 04 SOUTHEAST | 123 | 608.71 | 74871.33 | 898455.96 | 17969119.2 | 24827 | 3053721 | 38754.65 | 4766821.95
ERAS-2025-023 | 04 SOUTHEAST | 510 | 608.71 | 310442.1 | 3725305.2 | 74506104 | 24827 | 12661770 | 38754.65 | 19764871.5
ERAS-2025-029 | 03 CENTRAL | 170 | 608.71 | 103480.7 | 1241768.4 | 24835368 | 24827 | 4220590 | 38754.65 | 6588290.5
ERAS-2025-031 | 03 CENTRAL | 150 | 608.71 | 91306.5 | 1095678 | 21913560 | 24827 | 3724050 | 38754.65 | 5813197.5
ERAS-2025-034 | 03 CENTRAL | 250 | 608.71 | 152177.5 | 1826130 | 36522600 | 24827 | 6206750 | 38754.65 | 9688662.5
ERAS-2025-035 | 01 NORTH | 137.96 | 608.71 | 83977.6316 | 1007731.5792 | 20154631.584 | 24827 | 3425132.92 | 38754.65 | 5346591.514
Notes:
1) The Indicative JTIQ Generator Rate shown here is the total of the JTIQ Generator Rates for each the JTIQ Upgrades in the JTIQ Portfolio approved by the MISO and SPP Boards of Directors and reflects the total rate that would be effective after all of the JTIQ Upgrades are in-service. This Indicative JTIQ Generator Rate is calculated based on information provided by SPP and by MISO Transmission Owners and calculated in accordance with Attachment JJJ of the MISO Tariff and Attachment AV of the SPP Tariff.
2) Generator interconnection customers in both MISO and SPP that are subject to the JTIQ Generator Rate will be responsible for paying the JTIQ Generator Rate for all JTIQ Upgrades in the JTIQ Portfolio, regardless of the RTO in which they are connecting. The Indicative JTIQ Generator Rate assumes the generator has executed the Generator Interconnection Agreement prior to any JTIQ Upgrades being placed in-service. Actual charges will be dependent on a number of variables.
3) The Indicative Generator Rate shown here is based on the JTIQ Threshold MW Value of 24,310, which is the smallest MW level that will be utized as the denominator of the calculated JTIQ Generator Rate. If actual committed MW exceed the JTIQ Threshold MW Value, the actual committed MW will be utized as the denominator of the calculated JTIQ Generator Rate, which will reduce the JTIQ Generator Rate.
4) The Transmission Owners that will be constructing the JTIQ Upgrades or portions of the JTIQ Upgrades in the JTIQ Portfolio are OTP (Otter Tail Power), NSP (Northern States Power), ITCM (ITC Midwest), MEC (MidAmerican Energy Company), OPPD (Omaha Public Power District), NPPD (Nebraska Public Power District), EKC (Evergy Kansas Central), EM (Evergy Metro), EMW (Evergy Missouri West).
5) Annual Revenue Requirements for each JTIQ Upgrade are calculated based on the methodology described in Attachment JJJ in the MISO Tariff and Attachment AV in the SPP Tariff and reflect current cost of capital, FERC-approved return on equity (ROE) value (plus any applicable adders), and corporate tax rate information. Annual Revenue Requirements reflect assumed funding, as applicable, under the Department of Energy (DOE) Grid Resilience and Innovation Partnerships (GRIP) program and includes allowances for AFUDC and inflation.
6) The SPP Security amount is based on the projected Engineering and Construction (E&C) Cost infomation provided by the SPP JTIQ Tranmission Owners for the JTIQ in SPP less assumed DOE GRIP funding. The MW used in the denominator of the $/MW SPP Security rate is based the Threshold MW Value described in Note 3 above and will be used until the JTIQ portfolio is fully subscribed at which time the Final Commitment MW Total value will be used.
7) Indicative JTIQ Rates are posted on the SPP Website. https://spp.org/engineering/spp-miso-jtiq/