## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
ERAS-2025-001 | 02 NEBRASKA | Yes | Yes | Yes
ERAS-2025-002 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-003 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-004 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-005 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-006 | 03 CENTRAL | Yes | No | No
ERAS-2025-007 | 03 CENTRAL | Yes | Yes | Yes
ERAS-2025-008 | 03 CENTRAL | Yes | No | No
ERAS-2025-009 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-010 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-011 | 01 NORTH | Yes | Yes | Yes
ERAS-2025-012 | 01 NORTH | Yes | Yes | Yes
ERAS-2025-013 | 03 CENTRAL | Yes | Yes | Yes
ERAS-2025-014 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-015 | 03 CENTRAL | Yes | No | No
ERAS-2025-016 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-017 | 03 CENTRAL | Yes | No | No
ERAS-2025-018 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-019 | 03 CENTRAL | Yes | Yes | Yes
ERAS-2025-020 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-021 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-022 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-023 | 04 SOUTHEAST | Yes | Yes | Yes
ERAS-2025-024 | 04 SOUTHEAST | Yes | No | No
ERAS-2025-025 | 04 SOUTHEAST | Yes | No | No
ERAS-2025-026 | 04 SOUTHEAST | Yes | No | No
ERAS-2025-027 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-028 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-029 | 03 CENTRAL | Yes | Yes | Yes
ERAS-2025-030 | 05 SOUTHWEST | Yes | No | No
ERAS-2025-031 | 03 CENTRAL | Yes | Yes | Yes
ERAS-2025-032 | 03 CENTRAL | Yes | No | No
ERAS-2025-033 | 03 CENTRAL | Yes | No | No
ERAS-2025-034 | 03 CENTRAL | Yes | Yes | Yes
ERAS-2025-035 | 01 NORTH | Yes | Yes | Yes
ERAS-2025-036 | 05 SOUTHWEST | Yes | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00385 | 0.4004 | No
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00537 | 0.55848 | No
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.0127 | 1.3208 | Yes
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01493 | 1.5527 | Yes
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.07239 | 7.5286 | Yes
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00142 | 0.30814 | No
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00247 | 0.53599 | No
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00277 | 0.60109 | No
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00345 | 0.74865 | No
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00943 | 2.0463 | Yes
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01101 | 2.3892 | Yes
ERAS-2025-002 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01932 | 4.1924 | Yes
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00123 | 0.22878 | No
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00229 | 0.42594 | No
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00309 | 0.57474 | No
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00954 | 1.7744 | Yes
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00983 | 1.8284 | Yes
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01167 | 2.1706 | Yes
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02141 | 3.9823 | Yes
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00121 | 0.92323 | No
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00226 | 1.7244 | Yes
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00305 | 2.3272 | Yes
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00951 | 7.2561 | Yes
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00959 | 7.3172 | Yes
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01171 | 8.9347 | Yes
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02099 | 16.0154 | Yes
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00035 | 0.0525 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00049 | 0.0735 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | 0.00064 | 0.096 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 0.00064 | 0.096 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00111 | 0.1665 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00127 | 0.1905 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00147 | 0.2205 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00151 | 0.2265 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.00499 | 0.7485 | No
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00779 | 1.1685 | Yes
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01104 | 1.656 | Yes
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01602 | 2.403 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00201 | 1.4428 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00212 | 1.5217 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00318 | 2.2826 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00518 | 3.7182 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01091 | 7.8312 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.02129 | 15.282 | Yes
ERAS-2025-006 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.04804 | 34.4831 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00288 | 1.2977 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00437 | 1.9691 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01498 | 6.75 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.0158 | 7.1195 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.02635 | 11.8733 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.04924 | 22.1875 | Yes
ERAS-2025-007 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.08681 | 39.1166 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00163 | 1.1754 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00274 | 1.9758 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.0042 | 3.0286 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01026 | 7.3985 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01106 | 7.9754 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.0153 | 11.0328 | Yes
ERAS-2025-008 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.03513 | 25.3322 | Yes
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00108 | 0.486 | No
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00215 | 0.9675 | No
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00331 | 1.4895 | Yes
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.0086 | 3.87 | Yes
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00965 | 4.3425 | Yes
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01907 | 8.5815 | Yes
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02029 | 9.1305 | Yes
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00121 | 0.60016 | No
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00226 | 1.121 | Yes
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00305 | 1.5128 | Yes
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00951 | 4.717 | Yes
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00959 | 4.7566 | Yes
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01171 | 5.8082 | Yes
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02099 | 10.411 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.01329 | 9.9675 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.01329 | 9.9675 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 0.02066 | 15.495 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | 0.02066 | 15.495 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.03394 | 25.455 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.03433 | 25.7475 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.03491 | 26.1825 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.07675 | 57.5625 | Yes
ERAS-2025-011 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | 0.07726 | 57.945 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.01324 | 9.93 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.01324 | 9.93 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 0.02071 | 15.5325 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | 0.02071 | 15.5325 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.0339 | 25.425 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.03483 | 26.1225 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.03487 | 26.1525 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.07649 | 57.3675 | Yes
ERAS-2025-012 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | 0.07721 | 57.9075 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00288 | 1.2977 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00437 | 1.9691 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01498 | 6.75 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.0158 | 7.1195 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.02635 | 11.8733 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.04924 | 22.1875 | Yes
ERAS-2025-013 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.08681 | 39.1166 | Yes
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00147 | 0.23447 | No
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00158 | 0.25201 | No
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00252 | 0.40194 | No
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00271 | 0.43225 | No
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00942 | 1.5025 | Yes
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01136 | 1.8119 | Yes
ERAS-2025-014 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.0189 | 3.0145 | Yes
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00032 | 0.128 | No
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.00169 | 0.676 | No
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00195 | 0.78 | No
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.0025 | 1 | Yes
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00258 | 1.032 | Yes
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.00264 | 1.056 | Yes
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00284 | 1.136 | Yes
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00779 | 3.116 | Yes
ERAS-2025-015 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01136 | 4.544 | Yes
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00147 | 0.34177 | No
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00176 | 0.4092 | No
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00251 | 0.58357 | No
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00272 | 0.6324 | No
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00942 | 2.1902 | Yes
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01133 | 2.6342 | Yes
ERAS-2025-016 | 05 SOUTHWEST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01895 | 4.4059 | Yes
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.0001 | 0.06 | No
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00089 | 0.534 | No
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00207 | 1.242 | Yes
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00303 | 1.818 | Yes
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.00337 | 2.022 | Yes
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00861 | 5.166 | Yes
ERAS-2025-017 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01327 | 7.962 | Yes
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00103 | 0.26368 | No
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00138 | 0.35328 | No
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00177 | 0.45312 | No
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00224 | 0.57344 | No
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00235 | 0.6016 | No
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00412 | 1.0547 | Yes
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00423 | 1.0829 | Yes
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00866 | 2.217 | Yes
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00971 | 2.4858 | Yes
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01595 | 4.0832 | Yes
ERAS-2025-018 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01772 | 4.5363 | Yes
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00141 | 0.1128 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00141 | 0.1128 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00192 | 0.1536 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00294 | 0.2352 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00303 | 0.2424 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00579 | 0.4632 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00596 | 0.4768 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.0093 | 0.744 | No
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01661 | 1.3288 | Yes
ERAS-2025-019 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02802 | 2.2416 | Yes
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00104 | 0.416 | No
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00136 | 0.544 | No
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00215 | 0.86 | No
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00225 | 0.9 | No
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00234 | 0.936 | No
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00412 | 1.648 | Yes
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00423 | 1.692 | Yes
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00867 | 3.468 | Yes
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00963 | 3.852 | Yes
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01565 | 6.26 | Yes
ERAS-2025-020 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.0178 | 7.12 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00108 | 0.54 | No
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00132 | 0.66 | No
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.0023 | 1.15 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00231 | 1.155 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00367 | 1.835 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00413 | 2.065 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00425 | 2.125 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00868 | 4.34 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00938 | 4.69 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01454 | 7.27 | Yes
ERAS-2025-021 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01821 | 9.105 | Yes
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00094 | 0.11562 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00109 | 0.13407 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00192 | 0.23616 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00226 | 0.27798 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00359 | 0.44157 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.0037 | 0.4551 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.006 | 0.738 | No
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00862 | 1.0603 | Yes
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01269 | 1.5609 | Yes
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01615 | 1.9865 | Yes
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00117 | 0.5967 | No
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00224 | 1.1424 | Yes
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00348 | 1.7748 | Yes
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00969 | 4.9419 | Yes
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00975 | 4.9725 | Yes
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.01834 | 9.3534 | Yes
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02255 | 11.5005 | Yes
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00121 | 0.90024 | No
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00226 | 1.6814 | Yes
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00287 | 2.1353 | Yes
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00936 | 6.9638 | Yes
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00941 | 7.001 | Yes
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00972 | 7.2317 | Yes
ERAS-2025-024 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01965 | 14.6196 | Yes
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00116 | 0.203 | No
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00123 | 0.21525 | No
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00215 | 0.37625 | No
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00255 | 0.44625 | No
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00422 | 0.7385 | No
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00434 | 0.7595 | No
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00835 | 1.4613 | Yes
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00885 | 1.5487 | Yes
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00987 | 1.7272 | Yes
ERAS-2025-025 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01928 | 3.374 | Yes
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00121 | 0.90024 | No
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00226 | 1.6814 | Yes
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00287 | 2.1353 | Yes
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00935 | 6.9564 | Yes
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00941 | 7.001 | Yes
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00973 | 7.2391 | Yes
ERAS-2025-026 | 04 SOUTHEAST | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01964 | 14.6122 | Yes
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00104 | 0.26 | No
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00137 | 0.3425 | No
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00208 | 0.52 | No
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00225 | 0.5625 | No
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00234 | 0.585 | No
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00412 | 1.03 | Yes
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00423 | 1.0575 | Yes
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00867 | 2.1675 | Yes
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00965 | 2.4125 | Yes
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01571 | 3.9275 | Yes
ERAS-2025-027 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01779 | 4.4475 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00105 | 0.4032 | No
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00135 | 0.5184 | No
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00227 | 0.87168 | No
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00232 | 0.89088 | No
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00279 | 1.0714 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00412 | 1.5821 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00424 | 1.6282 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00867 | 3.3293 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00951 | 3.6518 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01515 | 5.8176 | Yes
ERAS-2025-028 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01795 | 6.8928 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.0019 | 0.323 | No
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.0031 | 0.527 | No
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00411 | 0.6987 | No
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00411 | 0.6987 | No
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00766 | 1.3022 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.01121 | 1.9057 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.01153 | 1.9601 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01162 | 1.9754 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01823 | 3.0991 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.021 | 3.57 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.03878 | 6.5926 | Yes
ERAS-2025-029 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.05701 | 9.6917 | Yes
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00103 | 0.3605 | No
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00138 | 0.483 | No
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.00163 | 0.5705 | No
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00224 | 0.784 | No
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00235 | 0.8225 | No
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00412 | 1.442 | Yes
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00423 | 1.4805 | Yes
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00866 | 3.031 | Yes
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00973 | 3.4055 | Yes
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01606 | 5.621 | Yes
ERAS-2025-030 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01769 | 6.1915 | Yes
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00202 | 0.303 | No
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.0033 | 0.495 | No
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00823 | 1.2345 | Yes
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.01244 | 1.866 | Yes
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01804 | 2.706 | Yes
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.02289 | 3.4335 | Yes
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.03933 | 5.8995 | Yes
ERAS-2025-031 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.05738 | 8.607 | Yes
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00141 | 0.2115 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00141 | 0.2115 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00192 | 0.288 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00294 | 0.441 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00303 | 0.4545 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00579 | 0.8685 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00596 | 0.894 | No
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.0093 | 1.395 | Yes
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01661 | 2.4915 | Yes
ERAS-2025-032 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02802 | 4.203 | Yes
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.0007 | 0.105 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.0007 | 0.105 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00176 | 0.264 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.0019 | 0.285 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00287 | 0.4305 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.0042 | 0.63 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00432 | 0.648 | No
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00863 | 1.2945 | Yes
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01376 | 2.064 | Yes
ERAS-2025-033 | 03 CENTRAL | G03 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.01388 | 2.082 | Yes
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.0011 | 0.275 | No
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00218 | 0.545 | No
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.00244 | 0.61 | No
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00367 | 0.9175 | No
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00904 | 2.26 | Yes
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00987 | 2.4675 | Yes
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.02099 | 5.2475 | Yes
ERAS-2025-034 | 03 CENTRAL | G00 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.02344 | 5.86 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.01377 | 1.8997 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.01377 | 1.8997 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.02108 | 2.9082 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 0.0223 | 3.0765 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | 0.0223 | 3.0765 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.03574 | 4.9307 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.03676 | 5.0714 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.03832 | 5.2866 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.0801 | 11.0506 | Yes
ERAS-2025-035 | 01 NORTH | G00 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | 0.08162 | 11.2603 | Yes
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00102 | 0.1428 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | 0.0012 | 0.168 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00139 | 0.1946 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00222 | 0.3108 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00237 | 0.3318 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00412 | 0.5768 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00423 | 0.5922 | No
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00866 | 1.2124 | Yes
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00982 | 1.3748 | Yes
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | 0.01642 | 2.2988 | Yes
ERAS-2025-036 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.01761 | 2.4654 | Yes

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.06468
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:MEC:OBRIEN | 0.05343
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:906::EHV: | 0.0538
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:903::EHV: | 0.05405
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | 0.05365
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.1303
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.05941
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.05941
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635730 MONTEZUMA 3 345 1 | P55:345:MEC:CBEC | 0.05187
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:MEC:RACCOON TRAIL | 0.06532
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:OPPD:S3740 3::FN13:EHV: | 0.09463
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635730 MONTEZUMA 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.06957
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 635014 OVERLAND 3 345 1 | P55:345:MEC:ORIENT | 0.06443
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635580 ARBOR HILL 3 345 635623 BADGER CRK 3 345 1 | P55:345:MEC:ORIENT | 0.06256
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635730 MONTEZUMA 3 345 1 | P55:345:MEC:HILLS | 0.05035
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P23:345:MEC:ARBOR HILL:902::EHV: | 0.06786
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635730 MONTEZUMA 3 345 1 | P55:345:MEC:ORIENT | 0.05167
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635730 MONTEZUMA 3 345 1 | P11:345:MEC:GDMEC:3:ST | 0.05978
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635635 MADISON3 345 635640 NORWALK 3 345 1 | P55:345:MEC:GRIMES | 0.05545
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 635014 OVERLAND 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.0581
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635700 SYCAMORE 3 345 1 | P12:345:MEC:SE POLK:GDMEC:1 | 0.0537
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635580 ARBOR HILL 3 345 635623 BADGER CRK 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.05603
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | P55:345:MEC:ORIENT | 0.06256
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635635 MADISON3 345 635640 NORWALK 3 345 1 | P23:345:MEC:GRIMES:903::EHV: | 0.05466
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.05767
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.05767
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635700 SYCAMORE 3 345 1 | P13:345-161:MEC:SE POLK:9T1:MULTI | 0.05519
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635580 ARBOR HILL 3 345 635623 BADGER CRK 3 345 1 | P23:345:MEC:ORIENT:905::EHV: | 0.05669
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 635014 OVERLAND 3 345 1 | P23:345:MEC:ORIENT:905::EHV: | 0.05875
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.05603
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635014 OVERLAND 3 345 635590 FALLOW AVE 3 345 1 | P55:345:MEC:ORIENT | 0.06256
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635600 GRIMES 3 345 635622 RCCN TRL 3 345 2 | P12:345:MEC:GRIMES:RCCN TRL:1 | 0.05309
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635600 GRIMES 3 345 635622 RCCN TRL 3 345 1 | P12:345:MEC:GRIMES:RCCN TRL:2 | 0.05307
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635580 ARBOR HILL 3 345 635590 FALLOW AVE 3 345 1 | P23:345:MEC:ORIENT:905::EHV: | 0.05669
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635680 BONDURANT3 345 635730 MONTEZUMA 3 345 1 | Base Case | 0.05978
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635014 OVERLAND 3 345 635590 FALLOW AVE 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.05603
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | Base Case | 0.08923
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635014 OVERLAND 3 345 635590 FALLOW AVE 3 345 1 | P23:345:MEC:ORIENT:905::EHV: | 0.05669
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P55:345:OPPD:S3451 3::FN13:EHV: | 0.06166
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P23:345:OPPD:S3451-RAUN:::EHV: | 0.06117
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P22:345:OPPD:S3451-RAUN:::EHV: | 0.06117
ERAS-2025-001 | 02 NEBRASKA | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | 0.06117
ERAS-2025-003 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | POI 509782_8 | 0.05312
ERAS-2025-004 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | POI 509782_8 | 0.0527
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | P22:345:EES:MUSKOGE7!:::EHV: | 0.07012
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | P22:345:EES:MUSKOGE7!:::EHV: | 0.07012
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.05233
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | P55:345:XEL:SHC BUS 1 | 0.0535
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | P22:345:EES:MUSKOGE7!:::EHV: | 0.07012
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.05316
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | P21:161:EES:5S.LEAD HILL:BULL SHOALS!:1:HV: | 0.05897
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.05233
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | P55:345:XEL:SHC BUS 1 | 0.0535
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.05316
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | P21:161:EES:5S.LEAD HILL:BULL SHOALS!:1:HV: | 0.05897
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.05233
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | P55:345:XEL:SHC BUS 1 | 0.0535
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.05316
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | 338120 5S.LEAD HILL 161 505461 BULL SH W5 161 1 | 0.05897
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 998425 8P.HILL% 161 1 | P23:500:EES-EAI:KEO:B4941::EHV: | 0.05165
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337923 5P.HILL% 161 998425 8P.HILL% 161 1 | P23:500:EES-EAI:KEO:B4941::EHV: | 0.05165
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 998425 8P.HILL% 161 1 | P12:161:EES:8ANO%:5ANO%:1:HV: | 0.11594
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337923 5P.HILL% 161 998425 8P.HILL% 161 1 | P12:161:EES:8ANO%:5ANO%:1:HV: | 0.11594
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | P23:500:EES-EAI:KEO:B4941::EHV: | 0.09207
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | Base Case | 0.0535
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | P23:500:EES-EAI:KEO:B4921::EHV: | 0.09218
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | Base Case | 0.0535
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 998425 8P.HILL% 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.06453
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337923 5P.HILL% 161 998425 8P.HILL% 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.06453
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.09847
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.09847
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338104 5HARRISON.E! 161 338107 5EVERTON RD 161 1 | Base Case | 0.0535
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.11556
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 0.10148
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8ISES%:8POWERLN_RD%:1:EHV: | 0.10148
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | 338832 5CLINTON.W# 161 338834 5BOTKINBURG# 161 1 | 0.08849
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | 338109 5MARSHALL 161 338834 5BOTKINBURG# 161 1 | 0.08849
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | P21:161:EES-EAI:MARSL2:BOTKINBURG:1:HV: | 0.08849
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 998426 ANO 161 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.11488
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337912 5ANO% 161 998426 ANO 161 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.11488
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.11764
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337905 5RUSSELVL.E! 161 337916 5RUSLVL.E_RX 161 R1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.11764
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P52:345:AEPW:NR4R.S.S.-7:::: | 0.06437
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P55:345:AEPW:NR4R.S.S.-7:::: | 0.06437
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | P12:500:EES:8BXTRWILSON%:8PERRYVILLE%:1:EHV: | 0.05466
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 336830 8BXTRWILSON% 500 337427 8PERRYVILLE% 500 1 | 0.05466
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.09302
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.09302
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.05194
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.05059
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 998426 ANO 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.10314
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337912 5ANO% 161 998426 ANO 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.10314
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.05194
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.13556
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.13556
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.05194
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | P12:500:EES:8SHERIDAN%:8MAGNETCOVE%:1:EHV: | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | P23:500:EES-EAI:SH_EHV:B5018::EHV: | 0.05005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.0624
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.08589
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.08589
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.09302
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 336830 8BXTRWILSON% 500 337427 8PERRYVILLE% 500 1 | P23:500:EES-EAI:KEO:B4941::EHV: | 0.05832
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.24526
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | 0.06903
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | P12:500:EES:8SHERIDAN%:8MABELVALE%:1:EHV: | 0.06903
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.09302
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | 0.09302
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 336830 8BXTRWILSON% 500 337427 8PERRYVILLE% 500 1 | P23:500:EES-EAI:KEO:B4921::EHV: | 0.0558
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.09847
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.09847
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.06988
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 998426 ANO 161 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.09359
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 998426 ANO 161 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.09359
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337912 5ANO% 161 998426 ANO 161 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.09359
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337912 5ANO% 161 998426 ANO 161 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.09359
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.12305
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 998425 8P.HILL% 161 1 | Base Case | 0.06299
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337905 5RUSSELVL.E! 161 337916 5RUSLVL.E_RX 161 R1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.12305
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Base Case | 0.0818
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337905 5RUSSELVL.E! 161 337916 5RUSLVL.E_RX 161 R1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337905 5RUSSELVL.E! 161 337916 5RUSLVL.E_RX 161 R1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337905 5RUSSELVL.E! 161 337916 5RUSLVL.E_RX 161 R1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337923 5P.HILL% 161 998425 8P.HILL% 161 1 | Base Case | 0.06299
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | P12:500:EES:8SHERIDAN%:8MAGNETCOVE%:1:EHV: | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | P23:500:EES-EAI:SH_EHV:B5018::EHV: | 0.05005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | P12:500:EES:8SHERIDAN%:8MAGNETCOVE%:1:EHV: | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | P23:500:EES-EAI:SH_EHV:B5018::EHV: | 0.05005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 998426 ANO 161 1 | P12:161:EES:8P.HILL%:5P.HILL%:1:HV: | 0.12503
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337912 5ANO% 161 998426 ANO 161 1 | P12:161:EES:8P.HILL%:5P.HILL%:1:HV: | 0.12503
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.11556
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | P23:500:EES-EAI:MABELV:B5918::EHV: | 0.06203
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.11764
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 0.10892
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.05194
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 337922 8P.HILL% 500 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.10314
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.10945
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338198 8DRIVER% 500 338400 8SANDYBAYOU% 500 1 | 0.08589
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505507 SWPINEY5 161 1 | Base Case | 0.08834
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.24526
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 0.10234
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8ISES%:8POWERLN_RD%:1:EHV: | 0.10148
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 0.10148
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337903 5DARDANELLE 161 505508 DARDANE5 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.32528
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | P21:161:EES:5RUSSELVL.N:5ANO%:1:HV: | 0.11818
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 0.11818
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.1056
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.1056
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | P21:161:EES:5BONO:5P.HILL%:1:HV: | 0.06178
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | 337919 5BONO 161 337923 5P.HILL% 161 1 | 0.06178
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337707 3HS VILLAGE 115 338743 3HOLLIS# 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337707 3HS VILLAGE 115 338743 3HOLLIS# 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337707 3HS VILLAGE 115 338743 3HOLLIS# 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337707 3HS VILLAGE 115 338743 3HOLLIS# 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | P23:500:EES-EAI:MABELV:B5918::EHV: | 0.06203
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | P23:500:EES-EAI:MABELV:B5918::EHV: | 0.06203
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338737 3NIMROD# 115 338743 3HOLLIS# 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338737 3NIMROD# 115 338743 3HOLLIS# 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338737 3NIMROD# 115 338743 3HOLLIS# 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338737 3NIMROD# 115 338743 3HOLLIS# 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.25053
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | P12:500:EES:8SHERIDAN%:8MAGNETCOVE%:1:EHV: | 0.05013
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.25005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.25005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.25005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | P23:500:EES-EAI:SH_EHV:B5018::EHV: | 0.05005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 338737 3NIMROD# 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 338737 3NIMROD# 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 338737 3NIMROD# 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 338737 3NIMROD# 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.09719
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.09719
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.12305
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.12282
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337903 5DARDANELLE 161 505508 DARDANE5 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.32765
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337707 3HS VILLAGE 115 338743 3HOLLIS# 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337903 5DARDANELLE 161 505508 DARDANE5 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.32736
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337903 5DARDANELLE 161 505508 DARDANE5 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.32736
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337903 5DARDANELLE 161 505508 DARDANE5 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.32736
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 998442 8EL DORADO% 345 2 | P23:500:EES:MOUNTSOLIVE:R3976::EHV: | 0.05362
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338737 3NIMROD# 115 338743 3HOLLIS# 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337562 7EL DORADO 345 998442 8EL DORADO% 345 2 | P23:500:EES:MOUNTSOLIVE:R3976::EHV: | 0.05362
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.09341
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.09341
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.09341
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | P23:500:EES-EAI:MABELV:B5918::EHV: | 0.06203
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | P23:500:EES-EAI:KEO:B4911::EHV: | 0.11618
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 998442 8EL DORADO% 345 2 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 0.05303
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 998442 8EL DORADO% 345 2 | P12:500:EES:8MT_OLIVE%:8EL DORADO%:1:EHV: | 0.05303
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337562 7EL DORADO 345 998442 8EL DORADO% 345 2 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 0.05303
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337562 7EL DORADO 345 998442 8EL DORADO% 345 2 | P12:500:EES:8MT_OLIVE%:8EL DORADO%:1:EHV: | 0.05303
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.25053
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.25005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.25005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.25005
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 338737 3NIMROD# 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | Base Case | 0.05059
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | Base Case | 0.08238
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.1189
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.1189
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | Base Case | 0.05697
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 337903 5DARDANELLE 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.32528
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | Base Case | 0.0818
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | Base Case | 0.06995
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 998442 8EL DORADO% 345 2 | P22:500:EES:MOUNTOLIVE:WESTBUS::EHV: | 0.05105
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 998442 8EL DORADO% 345 2 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | 0.05105
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337562 7EL DORADO 345 998442 8EL DORADO% 345 2 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | 0.05105
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337562 7EL DORADO 345 998442 8EL DORADO% 345 2 | P22:500:EES:MOUNTOLIVE:WESTBUS::EHV: | 0.05105
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 337901 3DANVLE AR 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.1189
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 337901 3DANVLE AR 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 337901 3DANVLE AR 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 337901 3DANVLE AR 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.1189
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | 0.1189
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 998426 ANO 161 1 | Base Case | 0.10377
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505461 BULL SH W5 161 1 | P21:161:EES:5ST JOE:5HILLTOP%:1:HV: | 0.0583
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505461 BULL SH W5 161 1 | 338108 5ST JOE 161 338110 5HILLTOP% 161 1 | 0.0583
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337912 5ANO% 161 998426 ANO 161 1 | Base Case | 0.10377
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337420 8STERLING% 500 337561 8EL DORADO% 500 1 | P12:500:EES:8MT_OLIVE%:8EL DORADO%:1:EHV: | 0.05828
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337420 8STERLING% 500 337561 8EL DORADO% 500 1 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 0.05828
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505461 BULL SH W5 161 1 | P12:161:EES-EAI:HRSN_E:EVRTON:1 | 0.0583
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505461 BULL SH W5 161 1 | P12:161:EES:5HARRISON.E!:5HILLTOP%:1:HV: | 0.0583
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337937 8MAYFLOWER% 500 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.08311
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337937 8MAYFLOWER% 500 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.08311
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338110 5HILLTOP% 161 505461 BULL SH W5 161 1 | 338107 5EVERTON RD 161 338108 5ST JOE 161 1 | 0.0583
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 337937 8MAYFLOWER% 500 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.16768
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 337903 5DARDANELLE 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.32765
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 337903 5DARDANELLE 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.32736
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 337903 5DARDANELLE 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.32736
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 337903 5DARDANELLE 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.32736
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.13111
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.13111
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | Base Case | 0.11588
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337905 5RUSSELVL.E! 161 337916 5RUSLVL.E_RX 161 R1 | Base Case | 0.11588
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 337562 7EL DORADO 345 1 | P23:500:EES:MOUNTSOLIVE:R3976::EHV: | 0.05362
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337907 5ATKINS 161 337921 5MORILTON.E! 161 1 | P21:161:EES:5RUSSELVL.N:5ANO%:1:HV: | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337907 5ATKINS 161 337921 5MORILTON.E! 161 1 | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 337901 3DANVLE AR 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 337562 7EL DORADO 345 1 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 0.05303
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 337562 7EL DORADO 345 1 | P12:500:EES:8MT_OLIVE%:8EL DORADO%:1:EHV: | 0.05303
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | Base Case | 0.06989
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337901 3DANVLE AR 115 998427 5DANVLE AR! 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 998427 5DANVLE AR! 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | P11:22:EES:1ANO U2:1::EHV: | 0.11696
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337901 3DANVLE AR 115 998427 5DANVLE AR! 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337901 3DANVLE AR 115 998427 5DANVLE AR! 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337901 3DANVLE AR 115 998427 5DANVLE AR! 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 998427 5DANVLE AR! 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 998427 5DANVLE AR! 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 998427 5DANVLE AR! 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P23:500:EES-EAI:KEO:B4911::EHV: | 0.09864
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337937 8MAYFLOWER% 500 1 | P23:500:EES-EAI:KEO:B4941::EHV: | 0.08967
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | P12:22:EES:8ANO%:1ANO U2:1:EHV: | 0.11696
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | 336830 8BXTRWILSON% 500 337427 8PERRYVILLE% 500 1 | 0.05006
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | P12:500:EES:8BXTRWILSON%:8PERRYVILLE%:1:EHV: | 0.05006
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | P23:500:EES:PERRYVILLE:R9872::EHV: | 0.05006
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 788938 TAP 161 1 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 0.42844
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | Base Case | 0.11588
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.09851
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.09851
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 788938 TAP 161 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.42994
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337937 8MAYFLOWER% 500 1 | P23:500:EES-EAI:KEO:B4921::EHV: | 0.08555
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 788938 TAP 161 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.42951
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 788938 TAP 161 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.42951
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 788938 TAP 161 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.42951
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.09851
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:138:EES:8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL1:HV: | 0.09851
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337907 5ATKINS 161 337921 5MORILTON.E! 161 1 | P12:161:EES-EAI:RUSL_E:ANO:1 | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337907 5ATKINS 161 337921 5MORILTON.E! 161 1 | P12:161:EES:5RUSSELVL.E!:5ANO%:1:HV: | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337901 3DANVLE AR 115 998427 5DANVLE AR! 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 998427 5DANVLE AR! 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337907 5ATKINS 161 337921 5MORILTON.E! 161 1 | P21:161:EES-EAI:RUSL_N:RUSL.E_:1:HV: | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.09333
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337907 5ATKINS 161 1 | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337907 5ATKINS 161 1 | P21:161:EES:5RUSSELVL.N:5ANO%:1:HV: | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 337562 7EL DORADO 345 1 | 337368 8MT_OLIVE% 500 509366 LAYFLD8 500 1 | 0.05105
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 337562 7EL DORADO 345 1 | P22:500:EES:MOUNTOLIVE:WESTBUS::EHV: | 0.05105
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10894
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10894
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337707 3HS VILLAGE 115 338743 3HOLLIS# 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338737 3NIMROD# 115 338743 3HOLLIS# 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.1341
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.1341
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 338737 3NIMROD# 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337909 8ANO% 500 337922 8P.HILL% 500 1 | Base Case | 0.05675
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337907 5ATKINS 161 1 | P12:161:EES-EAI:RUSL_E:ANO:1 | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | P11:16:EES:1TRACTBEL C1:1::EHV: | 0.05947
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337907 5ATKINS 161 1 | P12:161:EES:5RUSSELVL.E!:5ANO%:1:HV: | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:KEO:B4941::EHV: | 0.05324
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337907 5ATKINS 161 1 | 337906 5RUSSELVL.N 161 337916 5RUSLVL.E_RX 161 1 | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337905 5RUSSELVL.E! 161 1 | P21:161:EES:5RUSSELVL.N:5ANO%:1:HV: | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337905 5RUSSELVL.E! 161 1 | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 0.18329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | Base Case | 0.08581
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.15622
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | P23:500:EES:MOUNTSOLIVE:R3976::EHV: | 0.06531
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | P12:500:EES:8BXTRWILSON%:8PERRYVILLE%:1:EHV: | 0.05501
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | P42:500:OKGE:SB_FTTH8585:::EHV: | 0.10229
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.10215
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337905 5RUSSELVL.E! 161 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.1145
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | P12:500:EES:8MT_OLIVE%:8EL DORADO%:1:EHV: | 0.06337
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | 337368 8MT_OLIVE% 500 337561 8EL DORADO% 500 1 | 0.06337
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | 508585 TENRUSK7 345 508586 TENGEN 7 345 1 | 0.05095
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | P12:345:EES:TENRUSK7!:TENGEN 7!:1:EHV: | 0.05095
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337515 8MCNEIL% 500 337754 8ETTA% 500 1 | P23:500:EES-EAI:SH_EHV:B5018::EHV: | 0.05595
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | Base Case | 0.11696
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 337937 8MAYFLOWER% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.18152
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337515 8MCNEIL% 500 337754 8ETTA% 500 1 | P12:500:EES:8SHERIDAN%:8MAGNETCOVE%:1:EHV: | 0.05677
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337515 8MCNEIL% 500 337754 8ETTA% 500 1 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 0.05677
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | P23:500:EES-EAI:SH_EHV:B5026::EHV: | 0.10098
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337905 5RUSSELVL.E! 161 1 | P12:161:EES:5MORILTON.E!:5P.HILL%:1:HV: | 0.09821
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337905 5RUSSELVL.E! 161 1 | 337921 5MORILTON.E! 161 337923 5P.HILL% 161 1 | 0.09821
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 337937 8MAYFLOWER% 500 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.1018
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 337937 8MAYFLOWER% 500 1 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | 0.1018
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 337937 8MAYFLOWER% 500 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.1018
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | Base Case | 0.12328
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337903 5DARDANELLE 161 505508 DARDANE5 161 1 | Base Case | 0.32227
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | Base Case | 0.23843
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337643 8SHERIDAN% 500 337651 8WHT BLUFF% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.06329
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | Base Case | 0.05947
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P12:500:OKGE-EES:BKRBKR3170:::EHV: | 0.07914
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 0.07914
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | Base Case | 0.06823
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:KEO:B4911::EHV: | 0.09836
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 301406 8WNEWMADRID 500 338187 8DELL% 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05857
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 301406 8WNEWMADRID 500 338187 8DELL% 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05857
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337900 3OLA AR 115 337901 3DANVLE AR 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 337643 8SHERIDAN% 500 1 | P12:500:EES:8HS EHV%:8ETTA%:1:EHV: | 0.1295
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 337643 8SHERIDAN% 500 1 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 0.1295
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 337643 8SHERIDAN% 500 1 | P23:500:EES-EAI:SH_EHV:B5018::EHV: | 0.09551
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337705 3CHEETAH% 115 337707 3HS VILLAGE 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 337643 8SHERIDAN% 500 1 | P12:500:EES:8SHERIDAN%:8MAGNETCOVE%:1:EHV: | 0.09197
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 337643 8SHERIDAN% 500 1 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 0.09197
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.1869
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337901 3DANVLE AR 115 998427 5DANVLE AR! 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 998427 5DANVLE AR! 115 1 | Base Case | 0.10001
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337922 8P.HILL% 500 337937 8MAYFLOWER% 500 1 | Base Case | 0.11974
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 301406 8WNEWMADRID 500 338187 8DELL% 500 1 | 338198 8DRIVER% 500 338400 8SANDYBAYOU% 500 1 | 0.05857
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 301406 8WNEWMADRID 500 338187 8DELL% 500 1 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | 0.05511
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 301406 8WNEWMADRID 500 338187 8DELL% 500 1 | P12:345:EES:7NEWMAD%:7NEWMADGSU2:1:EHV: | 0.05511
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | Base Case | 0.23843
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337376 7SAREPTA% 345 508809 LONGWD 7 345 1 | Base Case | 0.0549
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337937 8MAYFLOWER% 500 1 | Base Case | 0.12198
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | Base Case | 0.09761
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337907 5ATKINS 161 337921 5MORILTON.E! 161 1 | Base Case | 0.12255
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 337903 5DARDANELLE 161 1 | Base Case | 0.32227
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337515 8MCNEIL% 500 337754 8ETTA% 500 1 | Base Case | 0.05947
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337902 5DANVLE AR! 161 788938 TAP 161 1 | Base Case | 0.42228
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | Base Case | 0.11967
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337907 5ATKINS 161 1 | Base Case | 0.12255
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337561 8EL DORADO% 500 337643 8SHERIDAN% 500 1 | Base Case | 0.08985
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 301406 8WNEWMADRID 500 338187 8DELL% 500 1 | Base Case | 0.05511
ERAS-2025-005 | 04 SOUTHEAST | G04 29SP | 337862 5RUSSELVL.IN 161 337905 5RUSSELVL.E! 161 1 | Base Case | 0.12255
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.05017
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05038
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.05923
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.05923
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05038
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05038
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.06749
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1 | 0.06112
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P11:24:AECI:1THLG3:1::: | 0.06112
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P21:345:AECI:THOMHL:THOMHLGSU3:1:: | 0.06112
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.05661
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.07724
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.05419
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.05451
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.06457
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.05673
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:OPPD:S3740 3::FN13:EHV: | 0.05008
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 635014 OVERLAND 3 345 1 | P55:345:MEC:ORIENT | 0.05122
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | Base Case | 0.05419
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.10236
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.05747
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.05747
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | Base Case | 0.06112
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.08786
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | Base Case | 0.06447
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.08414
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.08451
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.08764
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P55:345:OPPD:S3451 3::FN13:EHV: | 0.06831
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P23:345:OPPD:S3451-RAUN:::EHV: | 0.06727
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P22:345:OPPD:S3451-RAUN:::EHV: | 0.06727
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | 0.06727
ERAS-2025-007 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Base Case | 0.08414
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P51:25:WERE:WOLFCRK7:EHV: | 0.05133
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.05048
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.05067
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P55:345:XEL:SHC BUS 1 | 0.05067
ERAS-2025-009 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | Base Case | 0.05067
ERAS-2025-010 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | POI 509782_8 | 0.0527
ERAS-2025-011 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P11:22:GRE:GRE-COAL42G:2 | 0.08876
ERAS-2025-011 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P11:22:GRE:GRE-COAL41G:1 | 0.08876
ERAS-2025-011 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P51:25:WERE:WOLFCRK7:EHV: | 0.06766
ERAS-2025-011 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.06639
ERAS-2025-011 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.06606
ERAS-2025-011 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P55:345:XEL:SHC BUS 1 | 0.06605
ERAS-2025-011 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.05738
ERAS-2025-011 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.05738
ERAS-2025-011 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05105
ERAS-2025-011 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05105
ERAS-2025-011 | 01 NORTH | G00 29SP | 635223 PLYMOUTH 5 161 652566 SIOUXCY5 161 1 | P55:345:MEC:RAUN | 0.05106
ERAS-2025-011 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:MEC:CBEC | 0.05391
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.10372
ERAS-2025-011 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.0642
ERAS-2025-011 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | Base Case | 0.06606
ERAS-2025-011 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 657791 CENTER 3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.1147
ERAS-2025-011 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 657791 CENTER 3 345 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.09688
ERAS-2025-011 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:XEL:SHC BUS 1 | 0.06195
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:MEC:CBEC | 0.05391
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:MEC:OBRIEN | 0.12635
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:MEC:CBEC | 0.05391
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:906::EHV: | 0.12717
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05581
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.05581
ERAS-2025-011 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P55:345:XEL:CNC | 0.08179
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:903::EHV: | 0.12645
ERAS-2025-011 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.09758
ERAS-2025-011 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05525
ERAS-2025-011 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05525
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | 0.12376
ERAS-2025-011 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.09758
ERAS-2025-011 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | Base Case | 0.06197
ERAS-2025-011 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.0594
ERAS-2025-011 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P11:345:MEC:LOUISA:1 | 0.06197
ERAS-2025-011 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P23:345:MEC:SUB 93:954::EHV: | 0.06205
ERAS-2025-011 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:MEC:CBEC | 0.0623
ERAS-2025-011 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P12:345:XEL-GRE:PARKERS3:GRE-DICKNSN3:1 | 0.06674
ERAS-2025-011 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:GRE:DKN 62JB4:::EHV: | 0.06674
ERAS-2025-011 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:XEL:PRI1 | 0.06194
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.05581
ERAS-2025-011 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.07871
ERAS-2025-011 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8M12 PKL:::EHV: | 0.05936
ERAS-2025-011 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338198 8DRIVER% 500 338400 8SANDYBAYOU% 500 1 | 0.05525
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | 0.05581
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.05581
ERAS-2025-011 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.07605
ERAS-2025-011 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.07605
ERAS-2025-011 | 01 NORTH | G00 29SP | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.06697
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.05738
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.05738
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06228
ERAS-2025-011 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06351
ERAS-2025-011 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 657791 CENTER 3 345 1 | Base Case | 0.10259
ERAS-2025-011 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 0.06064
ERAS-2025-011 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06128
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Base Case | 0.10362
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05105
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05105
ERAS-2025-011 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05185
ERAS-2025-011 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:MEC:GDMEC | 0.05156
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.07871
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.07871
ERAS-2025-011 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.0642
ERAS-2025-011 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06274
ERAS-2025-011 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05419
ERAS-2025-011 | 01 NORTH | G00 29SP | 657110 MPC4300 POI 345 657946 PRAIRIE3 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.05925
ERAS-2025-011 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.05618
ERAS-2025-011 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05618
ERAS-2025-011 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:XEL:SHC BUS 1 | 0.06195
ERAS-2025-011 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06699
ERAS-2025-011 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05638
ERAS-2025-011 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | Base Case | 0.08876
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05185
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05185
ERAS-2025-011 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.05447
ERAS-2025-011 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.05447
ERAS-2025-011 | 01 NORTH | G00 29SP | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.06697
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:MEC:GDMEC | 0.05156
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:MEC:GDMEC | 0.05156
ERAS-2025-011 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.05447
ERAS-2025-011 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.05225
ERAS-2025-011 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P55:345:XEL:BIN | 0.0517
ERAS-2025-011 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | Base Case | 0.05187
ERAS-2025-011 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI1 | 0.06127
ERAS-2025-011 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P11:345:MEC:LOUISA:1 | 0.06197
ERAS-2025-011 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI | 0.06142
ERAS-2025-011 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8P33 KOL:::EHV: | 0.06591
ERAS-2025-011 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P23:345:MEC:SUB 93:954::EHV: | 0.06205
ERAS-2025-011 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:MEC:CBEC | 0.0623
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI1 | 0.06279
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0684
ERAS-2025-011 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07881
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05719
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI | 0.07247
ERAS-2025-011 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:XEL:PRI1 | 0.06194
ERAS-2025-011 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.07832
ERAS-2025-011 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.07832
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06912
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::37LOOSECREEK:EHV: | 0.0536
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::20LOOSECREEK:EHV: | 0.0536
ERAS-2025-011 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI1 | 0.05412
ERAS-2025-011 | 01 NORTH | G00 29SP | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06647
ERAS-2025-011 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Base Case | 0.06197
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0693
ERAS-2025-011 | 01 NORTH | G00 29SP | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.05925
ERAS-2025-011 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06029
ERAS-2025-011 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI | 0.05331
ERAS-2025-011 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.06101
ERAS-2025-011 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.06101
ERAS-2025-011 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:SHC BUS 1 | 0.05059
ERAS-2025-011 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:901::EHV: | 0.07677
ERAS-2025-011 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P55:345:MEC:KOSSUTH | 0.07677
ERAS-2025-011 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:902::EHV: | 0.07677
ERAS-2025-011 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:904::EHV: | 0.07677
ERAS-2025-011 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P12:345:CE-ALTW:QUAD13-11:ROCKCK3:1 | 0.06029
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0625
ERAS-2025-011 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI1 | 0.06323
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08486
ERAS-2025-011 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P23:500:XEL:CHISCO3:9P1::EHV: | 0.05552
ERAS-2025-011 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P23:500:XEL:CHISCO3:9P20::EHV: | 0.05552
ERAS-2025-011 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P54:500:XEL:CHI | 0.05552
ERAS-2025-011 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P12:500:XEL-GRE-MP:FORBES-CHISAGO COUNTY 500 | 0.05552
ERAS-2025-011 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P23:500:XEL:601LX FBS:::EHV: | 0.05552
ERAS-2025-011 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07888
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.06273
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | Base Case | 0.05187
ERAS-2025-011 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI1 | 0.06648
ERAS-2025-011 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI | 0.07304
ERAS-2025-011 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Base Case | 0.05187
ERAS-2025-011 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.12256
ERAS-2025-011 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.08602
ERAS-2025-011 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI1 | 0.05631
ERAS-2025-011 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07657
ERAS-2025-011 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.12256
ERAS-2025-011 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07463
ERAS-2025-011 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI | 0.0594
ERAS-2025-011 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06297
ERAS-2025-011 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI | 0.05545
ERAS-2025-011 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.0632
ERAS-2025-011 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06252
ERAS-2025-011 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P12:345:CE-ALTW:QUAD13-11:ROCKCK3:1 | 0.06252
ERAS-2025-011 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.06101
ERAS-2025-011 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P23:500:EES-EAI:KEO:B4931::EHV: | 0.05733
ERAS-2025-011 | 01 NORTH | G00 29SP | 631143 OTTUMWA3 345 635730 MONTEZUMA 3 345 1 | P55:345:MEC:SUB 93 | 0.05196
ERAS-2025-011 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | Base Case | 0.05791
ERAS-2025-011 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.06101
ERAS-2025-011 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P12:161:XEL-GRE:BYRON5:GRE-PLVLLY5:1 | 0.0732
ERAS-2025-011 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06706
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:PRI1 | 0.06778
ERAS-2025-011 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.10077
ERAS-2025-011 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | Base Case | 0.07675
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P13:230:OTP:SQBUTTE4:CENTER3:CENTR2TE2:HV: | 0.10097
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P13:230:OTP:SQBUTTE4:CENTER3:CENTR2TE2:HV: | 0.10097
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P23:345:AMMO:::17BLAND:EHV: | 0.05143
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P11:22:GRE:GRE-COAL42G:2 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P11:22:GRE:GRE-COAL41G:1 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 345445 7SKNKRVR 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:MONTEZUMA:901::EHV: | 0.05495
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.06647
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.06647
ERAS-2025-011 | 01 NORTH | G00 29SP | 345445 7SKNKRVR 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:MONTEZUMA:903::EHV: | 0.05607
ERAS-2025-011 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | 0.13809
ERAS-2025-011 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | 0.13809
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.06556
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.06556
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AECI-AMMO:FRANKS:BLAND:1:: | 0.05127
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS3:EHV: | 0.05127
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS:EHV | 0.05127
ERAS-2025-011 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | 300041 7FRANKS 345 344154 7BLAND 345 1 | 0.05127
ERAS-2025-011 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | Base Case | 0.06135
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | Base Case | 0.06273
ERAS-2025-011 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06128
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 657951 CNTSHNT3 345 Z1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.05925
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P11:22:GRE:GRE-COAL42G:2 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 601022 PARKERS3 345 601025 EDEN PR3 345 1 | P12:345:XEL:BLUELK3:PARKERS3:1 | 0.06367
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P11:22:GRE:GRE-COAL41G:1 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 67020 MPC03839POI 345 657951 CNTSHNT3 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.05925
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P23:500:EES-EAI:KEO:B4911::EHV: | 0.05504
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.05538
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.05538
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.05538
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.05538
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P23:345:XEL:8S85 NRH:::EHV: | 0.06658
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:PRI1 | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 601022 PARKERS3 345 601025 EDEN PR3 345 1 | P23:345:XEL:8M27 BLL:::EHV: | 0.06026
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:PRI | 0.05941
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.05754
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P55:345:XEL:NRH1 | 0.06781
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.05463
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.05463
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.05463
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.05463
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.07392
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.07392
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI1 | 0.06892
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0759
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.08456
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P12:115:XEL:ASKING7:WILOWRV7:1 | 0.05914
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P23:345:XEL:FUTURE 8S84 NRH:::EHV: | 0.06399
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:PRI | 0.05582
ERAS-2025-011 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.05919
ERAS-2025-011 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.05919
ERAS-2025-011 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | Base Case | 0.05423
ERAS-2025-011 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | P55:345:MEC:ORIENT | 0.05767
ERAS-2025-011 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:138:EES:8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL1:HV: | 0.05919
ERAS-2025-011 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.05919
ERAS-2025-011 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | P55:345:MEC:CBEC | 0.067
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:WLM BUS 1 | 0.07945
ERAS-2025-011 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 | P12:345:XEL:HELENA3:SCOTTCO3:1 | 0.05232
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06848
ERAS-2025-011 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | Base Case | 0.0632
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:PRI1 | 0.06885
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P11:20:OTP:CENTER2G:1 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.0556
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI | 0.06351
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0558
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | 0.08931
ERAS-2025-011 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:HNA1 | 0.05549
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.05392
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.05392
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P13:20-230:OTP:CENTER2G:YNG24:1 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05721
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06222
ERAS-2025-011 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06912
ERAS-2025-011 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.05218
ERAS-2025-011 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:PRI1 | 0.05079
ERAS-2025-011 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:PRI | 0.05161
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | Base Case | 0.05754
ERAS-2025-011 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601022 PARKERS3 345 1 | P12:345:XEL:PARKERS3:EDENPR3:1AS:EHV: | 0.06256
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:PRI | 0.06492
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:PRI1 | 0.08485
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | Base Case | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | Base Case | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | Base Case | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P11:20:OTP:CENTER2G:1 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | Base Case | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05059
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:PRI | 0.08577
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06936
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P13:20-230:OTP:CENTER2G:YNG24:1 | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P11:26:XEL:SHERCO33G:3 | 0.05059
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.05593
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06391
ERAS-2025-011 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08289
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.06944
ERAS-2025-011 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601022 PARKERS3 345 1 | P13:345:XEL:EDP TR 10 | 0.06278
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | Base Case | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.08483
ERAS-2025-011 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | Base Case | 0.05642
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:CNC | 0.06582
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06391
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06391
ERAS-2025-011 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06391
ERAS-2025-011 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | Base Case | 0.07883
ERAS-2025-011 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI1 | 0.06127
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | Base Case | 0.07605
ERAS-2025-011 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P23:345:XEL:FUTURE 8S49 HMP:::EHV: | 0.08837
ERAS-2025-011 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05284
ERAS-2025-011 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P23:345:XEL:8P5 KING:::EHV: | 0.08179
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631270 LASALLE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06912
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:PRI | 0.06204
ERAS-2025-011 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P22:345:XEL-SMMPA:8H15 PRI:::EHV: | 0.06425
ERAS-2025-011 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P12:345:XEL:PRISLD3:HMPTCNR3:1 | 0.06425
ERAS-2025-011 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P12:345:XEL:ASK-ECL | 0.0835
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06348
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:CNC | 0.06582
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:CNC | 0.06582
ERAS-2025-011 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:CNC | 0.06582
ERAS-2025-011 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | Base Case | 0.06715
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 635398 REMSEN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06128
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:PRI1 | 0.06319
ERAS-2025-011 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI | 0.06142
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06918
ERAS-2025-011 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI | 0.06204
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:PRI | 0.06204
ERAS-2025-011 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI | 0.06204
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P12:500:MH:M602F | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P23:500:XEL:602LX FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P12:500:XEL:REI-ROU-ROU-FBS | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P23:500:XEL:602L FBS:::EHV: | 0.06268
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.06924
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI1 | 0.06319
ERAS-2025-011 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:PRI1 | 0.06319
ERAS-2025-011 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI1 | 0.06319
ERAS-2025-011 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.07832
ERAS-2025-011 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.07832
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230.0:UMZ:# N-1 #:: LINE BIGSTON4-BLAIR-ER4-1 :HV: | 0.08782
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BLAIR-ER41:HV: | 0.08782
ERAS-2025-011 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P55:115:XEL:FBS | 0.05357
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.05068
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P23:345:XEL:8S23 WLM:::EHV: | 0.05973
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P23:345:XEL:WILMART3:8S23::EHV: | 0.05973
ERAS-2025-011 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06128
ERAS-2025-011 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | Base Case | 0.11687
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | 0.08199
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | Base Case | 0.05538
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | Base Case | 0.05538
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:PRI1 | 0.05584
ERAS-2025-011 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | P55:345:MEC:ORIENT | 0.05767
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996582 C055765(2-4) 345 9 | P13:345:XEL:CHISCO2:CHISCO3:CHIST1910:EHV: | 0.07952
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996581 C073455(1-2) 345 10 | P13:345:XEL:CHISCO2:CHISCO3:CHIST299:EHV: | 0.07945
ERAS-2025-011 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996582 C055765(2-4) 345 9 | P13:345:XEL:CHISCO2:CHISCO3:CHIST1910:EHV: | 0.07952
ERAS-2025-011 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996581 C073455(1-2) 345 10 | P13:345:XEL:CHISCO2:CHISCO3:CHIST299:EHV: | 0.07945
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | Base Case | 0.06857
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P23:345:MDU:ELLENDALE345:4803-4813: | 0.06659
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P42:345:MDU:ELLENDALE345:BIG STONE SOUTH:4803-4813: | 0.06659
ERAS-2025-011 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | Base Case | 0.05463
ERAS-2025-011 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | Base Case | 0.05463
ERAS-2025-011 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | P55:345:MEC:CBEC | 0.067
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P12:345:XEL:LYONCO3:HAWKSNEST3:1 | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL1 | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P55:345:MEC:RAUN | 0.07902
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:CNC | 0.08807
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:PRI | 0.05666
ERAS-2025-011 | 01 NORTH | G00 29SP | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | Base Case | 0.06656
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.08334
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:HAWKSNEST3:8N82::EHV: | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL2 | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601028 EAU CL 3 345 694003 ARPIN B1 345 1 | P12:345:ATC-XEL:W-13:NMAB5_345:BRIGGSRDNLL:EHV: | 0.05238
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996581 C073455(1-2) 345 10 | P23:500:XEL:CHISCO3:8P36::EHV: | 0.07085
ERAS-2025-011 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996581 C073455(1-2) 345 10 | P23:500:XEL:CHISCO3:8P36::EHV: | 0.07085
ERAS-2025-011 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | Base Case | 0.05015
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:SH_EHV:B5022::EHV: | 0.05898
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.07396
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996582 C055765(2-4) 345 9 | P23:500:XEL:CHISCO3:8P42 AS::EHV: | 0.07373
ERAS-2025-011 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996582 C055765(2-4) 345 9 | P23:500:XEL:CHISCO3:8P42 AS::EHV: | 0.07373
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:CNC | 0.08807
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.08334
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SBL BUS 1 | 0.07635
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | Base Case | 0.06944
ERAS-2025-011 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:PRI1 | 0.08292
ERAS-2025-011 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8M45 EDP:::EHV: | 0.06343
ERAS-2025-011 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:PRI | 0.08443
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | Base Case | 0.05725
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI | 0.07868
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | Base Case | 0.08171
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P23:345:XEL:8P2 KING:::EHV: | 0.07958
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI1 | 0.08141
ERAS-2025-011 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Base Case | 0.06848
ERAS-2025-011 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | Base Case | 0.0696
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI | 0.07868
ERAS-2025-011 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.08294
ERAS-2025-011 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P12:69:ATC-XEL:8E5_GD:ARPINB4:EAUCL3NLL:HV: | 0.06088
ERAS-2025-011 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P12:345:MEC-ITCM:OBRIEN:LAKEFIELD:1REACTOR:EHV: | 0.1146
ERAS-2025-011 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Base Case | 0.05817
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P23:345:XEL:8P2 KING:::EHV: | 0.07958
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI1 | 0.08141
ERAS-2025-011 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8E5 ECL BS:::EHV: | 0.06051
ERAS-2025-011 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P12:345:ATC-XEL:800000:ARPINB4:EAUCL3NLL:EHV: | 0.06051
ERAS-2025-011 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | Base Case | 0.05263
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SBL BUS 1 | 0.07635
ERAS-2025-011 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | Base Case | 0.08204
ERAS-2025-011 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | Base Case | 0.08204
ERAS-2025-011 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | Base Case | 0.05059
ERAS-2025-011 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:PRI1 | 0.06885
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P55:345:GRE:CDRMT | 0.09522
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:LYONCO3:8N60::EHV: | 0.09461
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:8N60 LYC:::EHV: | 0.09455
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05066
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI1 | 0.05058
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL1 | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P12:345:XEL:LYONCO3:HAWKSNEST3:1 | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI | 0.05052
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE SPLT RK3-WHITE-SRX3-1 :EHV: | 0.07272
ERAS-2025-011 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P14:345:ITCM-MEC:LAKEFLD-OBRIEN 50MVAR:MN-SS | 0.0791
ERAS-2025-011 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P12:345:MEC-ITCM:OBRIEN:LAKEFIELD:1REACTOR:EHV: | 0.0791
ERAS-2025-011 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:PRI1 | 0.06127
ERAS-2025-011 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:PRI1 | 0.05277
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P55:345:OPPD:S3451 3::FN13:EHV: | 0.10902
ERAS-2025-011 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | Base Case | 0.06135
ERAS-2025-011 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5263:IA-MVP::EHV: | 0.05692
ERAS-2025-011 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5269:IA-MVP::EHV: | 0.05849
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:HAWKSNEST3:8N82::EHV: | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL2 | 0.07645
ERAS-2025-011 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:PRI | 0.06142
ERAS-2025-011 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8P6 KING:::EHV: | 0.05599
ERAS-2025-011 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8P5 KING:::EHV: | 0.05557
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P23:345:OPPD:S3451-RAUN:::EHV: | 0.10827
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P22:345:OPPD:S3451-RAUN:::EHV: | 0.10827
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | 0.10827
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | Base Case | 0.0848
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.07396
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | Base Case | 0.05056
ERAS-2025-011 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:PRI | 0.05164
ERAS-2025-011 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.07832
ERAS-2025-011 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.07832
ERAS-2025-011 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:PRI | 0.06492
ERAS-2025-011 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.0574
ERAS-2025-011 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5268:IA-MVP::EHV: | 0.05967
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Base Case | 0.05042
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601023 REDROCK3 345 1 | P12:345:XEL:ASK-ECL | 0.05078
ERAS-2025-011 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.05808
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL:8S98 NRH:::EHV: | 0.07845
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05066
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI1 | 0.05058
ERAS-2025-011 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P12:69:ATC-XEL:8E5_GD:ARPINB4:EAUCL3NLL:HV: | 0.06375
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI | 0.05052
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE WHITE-SRX3-WHITE 3-SX :EHV: | 0.07272
ERAS-2025-011 | 01 NORTH | G00 29SP | 694076 STONE LK B2 345 694139 JUMP RIVR B3 345 1 | P23:500:XEL:CHISCO3:9P1::EHV: | 0.05241
ERAS-2025-011 | 01 NORTH | G00 29SP | 694076 STONE LK B2 345 694139 JUMP RIVR B3 345 1 | P23:500:XEL:CHISCO3:9P20::EHV: | 0.05241
ERAS-2025-011 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | Base Case | 0.083
ERAS-2025-011 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P55:345:XEL:SHC BUS 1 | 0.06973
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P55:345:XEL:SHC BUS 1 | 0.06973
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0821
ERAS-2025-011 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P23:345:XEL:8N5 MNN:::EHV: | 0.05561
ERAS-2025-011 | 01 NORTH | G00 29SP | 694066 ROCKY RN B6 345 694082 WERNER W B4 345 1 | P12:345:ATC-XEL:W-13:NMAB5_345:BRIGGSRDNLL:EHV: | 0.05242
ERAS-2025-011 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | Base Case | 0.05605
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05929
ERAS-2025-011 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07152
ERAS-2025-011 | 01 NORTH | G00 29SP | 661053 MANDAN 4 230 661091 NAPOLEON SW4 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.0515
ERAS-2025-011 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P12:345:XEL:MNTCELO3:QUARRY3:1 | 0.05625
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:WLM BUS 1 | 0.09792
ERAS-2025-011 | 01 NORTH | G00 29SP | 627217 BLUEBILL3 345 631198 COLBY3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05834
ERAS-2025-011 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | Base Case | 0.0574
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601018 CHIS CO3 345 1 | P23:345:XEL:8P34 KOL:::EHV: | 0.0618
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | Base Case | 0.05042
ERAS-2025-011 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06918
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601018 CHIS CO3 345 1 | P23:345:XEL:8P41 CHI:::EHV: | 0.06131
ERAS-2025-011 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601018 CHIS CO3 345 1 | P12:345:XEL:CHISCO3:KOLMNLK3:1 AS | 0.06131
ERAS-2025-011 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | Base Case | 0.08799
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:NRH1 | 0.07335
ERAS-2025-011 | 01 NORTH | G00 29SP | 661053 MANDAN 4 230 661091 NAPOLEON SW4 230 1 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.0515
ERAS-2025-011 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | Base Case | 0.06924
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL-SMMPA:8H8 PRI AS:::EHV: | 0.09334
ERAS-2025-011 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | Base Case | 0.06848
ERAS-2025-011 | 01 NORTH | G00 29SP | 635999 IRVINGTON3 345 636000 WEBSTER3 345 1 | Base Case | 0.06313
ERAS-2025-011 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.06592
ERAS-2025-011 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.06592
ERAS-2025-011 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.06592
ERAS-2025-011 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P23:345:XEL:8N46- 8N45- 8N47 QRY:::EHV: | 0.06407
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL-SMMPA:8H9 PRI AS:::EHV: | 0.09402
ERAS-2025-011 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P55:345:MEC:IRVINGTON | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | Base Case | 0.05056
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.06503
ERAS-2025-011 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.06503
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:BOK2 | 0.05515
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:BOK1 | 0.05515
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P23:345:XEL:WILMART3:8S26 FUT::EHV: | 0.09442
ERAS-2025-011 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05991
ERAS-2025-011 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | Base Case | 0.06135
ERAS-2025-011 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 661950 ELN345SHNT 3 345 1 | Base Case | 0.0505
ERAS-2025-011 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661950 ELN345SHNT 3 345 Z | Base Case | 0.0505
ERAS-2025-011 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P11:26:XEL:SHERCO33G:3 | 0.06986
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P11:26:XEL:SHERCO33G:3 | 0.06986
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0701
ERAS-2025-011 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0701
ERAS-2025-011 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.05991
ERAS-2025-011 | 01 NORTH | G00 29SP | 635369 KOSSUTH 3 345 635999 IRVINGTON3 345 1 | Base Case | 0.06313
ERAS-2025-011 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.05767
ERAS-2025-011 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.05767
ERAS-2025-011 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.05767
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P11:24:XEL:SHERCO31G:1 | 0.06986
ERAS-2025-011 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P11:24:XEL:SHERCO31G:1 | 0.06986
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | Base Case | 0.07726
ERAS-2025-011 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P55:345:XEL:BIN | 0.06028
ERAS-2025-011 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P55:345:XEL:BIN | 0.06028
ERAS-2025-011 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P55:345:XEL:BIN | 0.06028
ERAS-2025-011 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P55:345:MEC:IRVINGTON | 0.05711
ERAS-2025-011 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631270 LASALLE 3 345 1 | Base Case | 0.06924
ERAS-2025-011 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1 | Base Case | 0.0505
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 635398 REMSEN 3 345 1 | Base Case | 0.06135
ERAS-2025-011 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | Base Case | 0.05289
ERAS-2025-011 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | Base Case | 0.06986
ERAS-2025-011 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | Base Case | 0.06986
ERAS-2025-011 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | Base Case | 0.05954
ERAS-2025-011 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | Base Case | 0.08192
ERAS-2025-011 | 01 NORTH | G00 29SP | 620480 DEUEL CO 3 345 620483 ASTORIA 3 345 1 | Base Case | 0.08091
ERAS-2025-011 | 01 NORTH | G00 29SP | 620417 BSSOUTH3 345 620480 DEUEL CO 3 345 1 | Base Case | 0.08091
ERAS-2025-011 | 01 NORTH | G00 29SP | 608602 SQBEAST4 230 657756 SQBUTTE4 230 Z2 | P12:230:MP-OTP:SQBEAST4:SQBUTTE4:Z1 | 0.05506
ERAS-2025-011 | 01 NORTH | G00 29SP | 608602 SQBEAST4 230 657756 SQBUTTE4 230 Z1 | P12:230:MP-OTP:SQBEAST4:SQBUTTE4:Z2 | 0.05506
ERAS-2025-011 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | Base Case | 0.0521
ERAS-2025-011 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | Base Case | 0.06924
ERAS-2025-011 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | Base Case | 0.07553
ERAS-2025-012 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P11:22:GRE:GRE-COAL42G:2 | 0.10343
ERAS-2025-012 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P11:22:GRE:GRE-COAL41G:1 | 0.10343
ERAS-2025-012 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P51:25:WERE:WOLFCRK7:EHV: | 0.06798
ERAS-2025-012 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.06671
ERAS-2025-012 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.06638
ERAS-2025-012 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P55:345:XEL:SHC BUS 1 | 0.06636
ERAS-2025-012 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.05759
ERAS-2025-012 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.05759
ERAS-2025-012 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05127
ERAS-2025-012 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05127
ERAS-2025-012 | 01 NORTH | G00 29SP | 635223 PLYMOUTH 5 161 652566 SIOUXCY5 161 1 | P55:345:MEC:RAUN | 0.05058
ERAS-2025-012 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:MEC:CBEC | 0.0546
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.10287
ERAS-2025-012 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06444
ERAS-2025-012 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | Base Case | 0.06638
ERAS-2025-012 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 657791 CENTER 3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.12323
ERAS-2025-012 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 657791 CENTER 3 345 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.1051
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601010 MNTCELO3 345 1 | P55:345:XEL:CNC | 0.05124
ERAS-2025-012 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:XEL:SHC BUS 1 | 0.06227
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:MEC:CBEC | 0.0546
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:MEC:OBRIEN | 0.12594
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:MEC:CBEC | 0.0546
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:906::EHV: | 0.12679
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05598
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.05598
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P55:345:XEL:CNC | 0.08531
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:903::EHV: | 0.12609
ERAS-2025-012 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.11162
ERAS-2025-012 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.0555
ERAS-2025-012 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.0555
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | 0.12338
ERAS-2025-012 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.11162
ERAS-2025-012 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | Base Case | 0.06229
ERAS-2025-012 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07183
ERAS-2025-012 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P11:345:MEC:LOUISA:1 | 0.06229
ERAS-2025-012 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P23:345:MEC:SUB 93:954::EHV: | 0.06236
ERAS-2025-012 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:MEC:CBEC | 0.06264
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P12:345:XEL-GRE:PARKERS3:GRE-DICKNSN3:1 | 0.07028
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:GRE:DKN 62JB4:::EHV: | 0.07028
ERAS-2025-012 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:XEL:PRI1 | 0.06226
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.05598
ERAS-2025-012 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.0791
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8M12 PKL:::EHV: | 0.06252
ERAS-2025-012 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338198 8DRIVER% 500 338400 8SANDYBAYOU% 500 1 | 0.0555
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | 0.05598
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.05598
ERAS-2025-012 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.07631
ERAS-2025-012 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.07631
ERAS-2025-012 | 01 NORTH | G00 29SP | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07221
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.05759
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.05759
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06473
ERAS-2025-012 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06376
ERAS-2025-012 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 657791 CENTER 3 345 1 | Base Case | 0.1104
ERAS-2025-012 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 0.06089
ERAS-2025-012 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0627
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Base Case | 0.10277
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05127
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05127
ERAS-2025-012 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0523
ERAS-2025-012 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:MEC:GDMEC | 0.05201
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.0791
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.0791
ERAS-2025-012 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06444
ERAS-2025-012 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06522
ERAS-2025-012 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05455
ERAS-2025-012 | 01 NORTH | G00 29SP | 657110 MPC4300 POI 345 657946 PRAIRIE3 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.0631
ERAS-2025-012 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.05639
ERAS-2025-012 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05639
ERAS-2025-012 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:XEL:SHC BUS 1 | 0.06227
ERAS-2025-012 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06823
ERAS-2025-012 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05674
ERAS-2025-012 | 01 NORTH | G00 29SP | 608607 NELSNLK4 230 615901 GRE-STANTON4 230 1 | Base Case | 0.10343
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0523
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0523
ERAS-2025-012 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.05468
ERAS-2025-012 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.05468
ERAS-2025-012 | 01 NORTH | G00 29SP | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07221
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:MEC:GDMEC | 0.05201
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:MEC:GDMEC | 0.05201
ERAS-2025-012 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.05468
ERAS-2025-012 | 01 NORTH | G00 29SP | 657110 MPC4300 POI 345 657946 PRAIRIE3 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.05085
ERAS-2025-012 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.05598
ERAS-2025-012 | 01 NORTH | G00 29SP | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | Base Case | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P55:345:XEL:BIN | 0.05542
ERAS-2025-012 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | Base Case | 0.05233
ERAS-2025-012 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI1 | 0.06269
ERAS-2025-012 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P11:345:MEC:LOUISA:1 | 0.06229
ERAS-2025-012 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI | 0.06283
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8P33 KOL:::EHV: | 0.06887
ERAS-2025-012 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P23:345:MEC:SUB 93:954::EHV: | 0.06236
ERAS-2025-012 | 01 NORTH | G00 29SP | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | P12:230:MDU:BADGER WIND:WISHEK:1: | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:MEC:CBEC | 0.06264
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI1 | 0.06525
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06967
ERAS-2025-012 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07991
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05778
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI | 0.07507
ERAS-2025-012 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:XEL:PRI1 | 0.06226
ERAS-2025-012 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.0796
ERAS-2025-012 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.0796
ERAS-2025-012 | 01 NORTH | G00 29SP | 652296 WARD 4 230 661053 MANDAN 4 230 1 | P12:230.0:UMZ:# N-1 #:: LINE HEBRON 4-DICKINSN-BE4-1 :HV: | 0.053
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07015
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::37LOOSECREEK:EHV: | 0.05384
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::20LOOSECREEK:EHV: | 0.05384
ERAS-2025-012 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI1 | 0.05448
ERAS-2025-012 | 01 NORTH | G00 29SP | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06775
ERAS-2025-012 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Base Case | 0.06229
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07048
ERAS-2025-012 | 01 NORTH | G00 29SP | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.0631
ERAS-2025-012 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06069
ERAS-2025-012 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI | 0.05364
ERAS-2025-012 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.06121
ERAS-2025-012 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.06121
ERAS-2025-012 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:SHC BUS 1 | 0.05137
ERAS-2025-012 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:901::EHV: | 0.07827
ERAS-2025-012 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P55:345:MEC:KOSSUTH | 0.07827
ERAS-2025-012 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:902::EHV: | 0.07827
ERAS-2025-012 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:904::EHV: | 0.07827
ERAS-2025-012 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P12:345:CE-ALTW:QUAD13-11:ROCKCK3:1 | 0.06069
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06496
ERAS-2025-012 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI1 | 0.06573
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08547
ERAS-2025-012 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P23:500:XEL:CHISCO3:9P1::EHV: | 0.05769
ERAS-2025-012 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P23:500:XEL:CHISCO3:9P20::EHV: | 0.05769
ERAS-2025-012 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P54:500:XEL:CHI | 0.05769
ERAS-2025-012 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P12:500:XEL-GRE-MP:FORBES-CHISAGO COUNTY 500 | 0.05769
ERAS-2025-012 | 01 NORTH | G00 29SP | 693502 SUPERIOR 345 694078 STONE LK B4 345 1 | P23:500:XEL:601LX FBS:::EHV: | 0.05769
ERAS-2025-012 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.08486
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.06519
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | Base Case | 0.05233
ERAS-2025-012 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI1 | 0.0677
ERAS-2025-012 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI | 0.07568
ERAS-2025-012 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Base Case | 0.05233
ERAS-2025-012 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.14235
ERAS-2025-012 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.09092
ERAS-2025-012 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI1 | 0.05667
ERAS-2025-012 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08092
ERAS-2025-012 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.14235
ERAS-2025-012 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07996
ERAS-2025-012 | 01 NORTH | G00 29SP | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.05085
ERAS-2025-012 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI | 0.06045
ERAS-2025-012 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06546
ERAS-2025-012 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI | 0.05579
ERAS-2025-012 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.0657
ERAS-2025-012 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06293
ERAS-2025-012 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P12:345:CE-ALTW:QUAD13-11:ROCKCK3:1 | 0.06293
ERAS-2025-012 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.06121
ERAS-2025-012 | 01 NORTH | G00 29SP | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | P11:230:MDU:BADGER WIND:W1: | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | P11:230:MDU:BADGER WIND:W2: | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P23:500:EES-EAI:KEO:B4931::EHV: | 0.05752
ERAS-2025-012 | 01 NORTH | G00 29SP | 631143 OTTUMWA3 345 635730 MONTEZUMA 3 345 1 | P55:345:MEC:SUB 93 | 0.05194
ERAS-2025-012 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | Base Case | 0.06101
ERAS-2025-012 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.06121
ERAS-2025-012 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P12:161:XEL-GRE:BYRON5:GRE-PLVLLY5:1 | 0.07457
ERAS-2025-012 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0683
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:PRI1 | 0.06901
ERAS-2025-012 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.11974
ERAS-2025-012 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | Base Case | 0.0811
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P13:230:OTP:SQBUTTE4:CENTER3:CENTR2TE2:HV: | 0.11304
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P13:230:OTP:SQBUTTE4:CENTER3:CENTR2TE2:HV: | 0.11304
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P23:345:AMMO:::17BLAND:EHV: | 0.05162
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P11:22:GRE:GRE-COAL42G:2 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P11:22:GRE:GRE-COAL41G:1 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 345445 7SKNKRVR 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:MONTEZUMA:901::EHV: | 0.0554
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.07203
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.07203
ERAS-2025-012 | 01 NORTH | G00 29SP | 345445 7SKNKRVR 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:MONTEZUMA:903::EHV: | 0.05639
ERAS-2025-012 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV: | 0.15682
ERAS-2025-012 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: | 0.15682
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.07104
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P12:345:OTP:CENTER3:COYOTE3:1 RAS OFF:EHV: | 0.07104
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AECI-AMMO:FRANKS:BLAND:1:: | 0.05146
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS3:EHV: | 0.05146
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS:EHV | 0.05146
ERAS-2025-012 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | 300041 7FRANKS 345 344154 7BLAND 345 1 | 0.05146
ERAS-2025-012 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | Base Case | 0.06277
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | Base Case | 0.06519
ERAS-2025-012 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0627
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 657951 CNTSHNT3 345 Z1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.0631
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P11:22:GRE:GRE-COAL42G:2 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 601022 PARKERS3 345 601025 EDEN PR3 345 1 | P12:345:XEL:BLUELK3:PARKERS3:1 | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P11:22:GRE:GRE-COAL41G:1 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 67020 MPC03839POI 345 657951 CNTSHNT3 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.0631
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 996517 IRRNTR1 230 1 | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 608622 IRONRNG4 230 996517 IRRNTR1 230 1 | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P23:500:EES-EAI:KEO:B4911::EHV: | 0.05525
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.06201
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.06201
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.06201
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.06201
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P23:345:XEL:8S85 NRH:::EHV: | 0.06785
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:PRI1 | 0.05769
ERAS-2025-012 | 01 NORTH | G00 29SP | 601022 PARKERS3 345 601025 EDEN PR3 345 1 | P23:345:XEL:8M27 BLL:::EHV: | 0.06369
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:PRI | 0.06044
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.05866
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P55:345:XEL:NRH1 | 0.06909
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.06116
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.06116
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P13:345:MDU:COYOTE:1:COYOTE GSU LOSS | 0.06116
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P13:24-345:OTP:COYOTE1G:COYOTE3:1 | 0.06116
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.07418
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.07418
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.05619
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.05619
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI1 | 0.07008
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08029
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.08946
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P12:115:XEL:ASKING7:WILOWRV7:1 | 0.06029
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P23:345:XEL:FUTURE 8S84 NRH:::EHV: | 0.06515
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:PRI | 0.05638
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.05542
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.05542
ERAS-2025-012 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.05942
ERAS-2025-012 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.05942
ERAS-2025-012 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | Base Case | 0.05459
ERAS-2025-012 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | P55:345:MEC:ORIENT | 0.05794
ERAS-2025-012 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:138:EES:8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL1:HV: | 0.05942
ERAS-2025-012 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.05942
ERAS-2025-012 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | P55:345:MEC:CBEC | 0.06732
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:WLM BUS 1 | 0.08135
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.05542
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.05542
ERAS-2025-012 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 | P12:345:XEL:HELENA3:SCOTTCO3:1 | 0.05508
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06974
ERAS-2025-012 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | Base Case | 0.0657
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:PRI1 | 0.06987
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P11:20:OTP:CENTER2G:1 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05582
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI | 0.06455
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05762
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 657951 CNTSHNT3 345 Z1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.05085
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | 0.08957
ERAS-2025-012 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:HNA1 | 0.05816
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.05418
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.05418
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | P13:20-230:OTP:CENTER2G:YNG24:1 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05781
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06285
ERAS-2025-012 | 01 NORTH | G00 29SP | 67020 MPC03839POI 345 657951 CNTSHNT3 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.05085
ERAS-2025-012 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07015
ERAS-2025-012 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.05442
ERAS-2025-012 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:PRI1 | 0.05158
ERAS-2025-012 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:PRI | 0.05243
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | Base Case | 0.05866
ERAS-2025-012 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601022 PARKERS3 345 1 | P12:345:XEL:PARKERS3:EDENPR3:1AS:EHV: | 0.0658
ERAS-2025-012 | 01 NORTH | G00 29SP | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | Base Case | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:PRI | 0.06585
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:PRI1 | 0.08546
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | Base Case | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | Base Case | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | Base Case | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P11:20:OTP:CENTER2G:1 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | Base Case | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05137
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:PRI | 0.0864
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.07054
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | P13:20-230:OTP:CENTER2G:YNG24:1 | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P11:26:XEL:SHERCO33G:3 | 0.05137
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.05621
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06742
ERAS-2025-012 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08402
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.07062
ERAS-2025-012 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601022 PARKERS3 345 1 | P13:345:XEL:EDP TR 10 | 0.06603
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 620379 RUGBY 4 230 1 | Base Case | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.08544
ERAS-2025-012 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | Base Case | 0.05679
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:CNC | 0.06933
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06742
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06742
ERAS-2025-012 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.06742
ERAS-2025-012 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | Base Case | 0.07993
ERAS-2025-012 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI1 | 0.06269
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | Base Case | 0.08045
ERAS-2025-012 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P23:345:XEL:FUTURE 8S49 HMP:::EHV: | 0.09046
ERAS-2025-012 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05338
ERAS-2025-012 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P23:345:XEL:8P5 KING:::EHV: | 0.08355
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631270 LASALLE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07015
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:PRI | 0.06547
ERAS-2025-012 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P22:345:XEL-SMMPA:8H15 PRI:::EHV: | 0.06621
ERAS-2025-012 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P12:345:XEL:PRISLD3:HMPTCNR3:1 | 0.06621
ERAS-2025-012 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P12:345:XEL:ASK-ECL | 0.08529
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.06697
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:CNC | 0.06933
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:CNC | 0.06933
ERAS-2025-012 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:CNC | 0.06933
ERAS-2025-012 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | Base Case | 0.06839
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 635398 REMSEN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0627
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601013 ROSEAUS2 500 1 | P55:345:XEL:PRI1 | 0.06666
ERAS-2025-012 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI | 0.06283
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0702
ERAS-2025-012 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI | 0.06547
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:PRI | 0.06547
ERAS-2025-012 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI | 0.06547
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P12:500:MH:M602F | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P23:500:XEL:602LX FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P12:500:XEL:REI-ROU-ROU-FBS | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P23:500:XEL:602L FBS:::EHV: | 0.06627
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.07027
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI1 | 0.06666
ERAS-2025-012 | 01 NORTH | G00 29SP | 601012 ROSEAUN2 500 667501 RIEL 2 500 1 | P55:345:XEL:PRI1 | 0.06666
ERAS-2025-012 | 01 NORTH | G00 29SP | 601013 ROSEAUS2 500 601038 ROSEAUM 2 500 1 | P55:345:XEL:PRI1 | 0.06666
ERAS-2025-012 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.0796
ERAS-2025-012 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.0796
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230.0:UMZ:# N-1 #:: LINE BIGSTON4-BLAIR-ER4-1 :HV: | 0.0954
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BLAIR-ER41:HV: | 0.0954
ERAS-2025-012 | 01 NORTH | G00 29SP | 608411 WARRVRM2 500 608412 WARRVRS2 500 1 | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 608411 WARRVRM2 500 1 | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 608412 WARRVRS2 500 608423 IRRN-RX2 500 1 | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 608410 WARRVRN2 500 667500 DORSEY 2 500 1 | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 608422 IRONRNG2 500 608423 IRRN-RX2 500 Z | P55:115:XEL:FBS | 0.05665
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.05093
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P23:345:XEL:8S23 WLM:::EHV: | 0.06224
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P23:345:XEL:WILMART3:8S23::EHV: | 0.06224
ERAS-2025-012 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0627
ERAS-2025-012 | 01 NORTH | G00 29SP | 615901 GRE-STANTON4 230 659106 LELAND_O-BE4 230 1 | Base Case | 0.13707
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | 0.08855
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995941 620:CENTER # 230 1 | Base Case | 0.06201
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995941 620:CENTER # 230 1 | Base Case | 0.06201
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:PRI1 | 0.05765
ERAS-2025-012 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | P55:345:MEC:ORIENT | 0.05794
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996582 C055765(2-4) 345 9 | P13:345:XEL:CHISCO2:CHISCO3:CHIST1910:EHV: | 0.08393
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996581 C073455(1-2) 345 10 | P13:345:XEL:CHISCO2:CHISCO3:CHIST299:EHV: | 0.08386
ERAS-2025-012 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996582 C055765(2-4) 345 9 | P13:345:XEL:CHISCO2:CHISCO3:CHIST1910:EHV: | 0.08393
ERAS-2025-012 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996581 C073455(1-2) 345 10 | P13:345:XEL:CHISCO2:CHISCO3:CHIST299:EHV: | 0.08386
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | Base Case | 0.06983
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P23:345:MDU:ELLENDALE345:4803-4813: | 0.07151
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P42:345:MDU:ELLENDALE345:BIG STONE SOUTH:4803-4813: | 0.07151
ERAS-2025-012 | 01 NORTH | G00 29SP | 657756 SQBUTTE4 230 995940 620:CENTER # 230 2 | Base Case | 0.06116
ERAS-2025-012 | 01 NORTH | G00 29SP | 657791 CENTER 3 345 995940 620:CENTER # 230 2 | Base Case | 0.06116
ERAS-2025-012 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | P55:345:MEC:CBEC | 0.06732
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P12:345:XEL:LYONCO3:HAWKSNEST3:1 | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL1 | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P55:345:MEC:RAUN | 0.08009
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:CNC | 0.09268
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:PRI | 0.05846
ERAS-2025-012 | 01 NORTH | G00 29SP | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | Base Case | 0.06784
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.08795
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:HAWKSNEST3:8N82::EHV: | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL2 | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601028 EAU CL 3 345 694003 ARPIN B1 345 1 | P12:345:ATC-XEL:W-13:NMAB5_345:BRIGGSRDNLL:EHV: | 0.0531
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996581 C073455(1-2) 345 10 | P23:500:XEL:CHISCO3:8P36::EHV: | 0.07481
ERAS-2025-012 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996581 C073455(1-2) 345 10 | P23:500:XEL:CHISCO3:8P36::EHV: | 0.07481
ERAS-2025-012 | 01 NORTH | G00 29SP | 602057 PEACE GARD 5 230 667085 G82RPHT1 230 1 | Base Case | 0.05308
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:SH_EHV:B5022::EHV: | 0.05926
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.07209
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 996582 C055765(2-4) 345 9 | P23:500:XEL:CHISCO3:8P42 AS::EHV: | 0.07774
ERAS-2025-012 | 01 NORTH | G00 29SP | 601018 CHIS CO3 345 996582 C055765(2-4) 345 9 | P23:500:XEL:CHISCO3:8P42 AS::EHV: | 0.07774
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:CNC | 0.09268
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:SHC BUS 1 | 0.08795
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SBL BUS 1 | 0.07436
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | Base Case | 0.07062
ERAS-2025-012 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:PRI1 | 0.08405
ERAS-2025-012 | 01 NORTH | G00 29SP | 601015 BLUE LK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8M45 EDP:::EHV: | 0.06671
ERAS-2025-012 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:PRI | 0.08557
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | Base Case | 0.05784
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI | 0.0831
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | Base Case | 0.08772
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P23:345:XEL:8P2 KING:::EHV: | 0.08396
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI1 | 0.08593
ERAS-2025-012 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Base Case | 0.06892
ERAS-2025-012 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | Base Case | 0.07113
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI | 0.0831
ERAS-2025-012 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.08407
ERAS-2025-012 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P12:69:ATC-XEL:8E5_GD:ARPINB4:EAUCL3NLL:HV: | 0.06194
ERAS-2025-012 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P12:345:MEC-ITCM:OBRIEN:LAKEFIELD:1REACTOR:EHV: | 0.11617
ERAS-2025-012 | 01 NORTH | G00 29SP | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Base Case | 0.06257
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P23:345:XEL:8P2 KING:::EHV: | 0.08396
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:PRI1 | 0.08593
ERAS-2025-012 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8E5 ECL BS:::EHV: | 0.06156
ERAS-2025-012 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P12:345:ATC-XEL:800000:ARPINB4:EAUCL3NLL:EHV: | 0.06156
ERAS-2025-012 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | Base Case | 0.05284
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SBL BUS 1 | 0.07436
ERAS-2025-012 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | Base Case | 0.08659
ERAS-2025-012 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | Base Case | 0.08659
ERAS-2025-012 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | Base Case | 0.05137
ERAS-2025-012 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:PRI1 | 0.06987
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P55:345:GRE:CDRMT | 0.09583
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:LYONCO3:8N60::EHV: | 0.09524
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:8N60 LYC:::EHV: | 0.09517
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL1 | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P12:345:XEL:LYONCO3:HAWKSNEST3:1 | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE SPLT RK3-WHITE-SRX3-1 :EHV: | 0.07164
ERAS-2025-012 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P14:345:ITCM-MEC:LAKEFLD-OBRIEN 50MVAR:MN-SS | 0.08064
ERAS-2025-012 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P12:345:MEC-ITCM:OBRIEN:LAKEFIELD:1REACTOR:EHV: | 0.08064
ERAS-2025-012 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:PRI1 | 0.06269
ERAS-2025-012 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:PRI1 | 0.0533
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P55:345:OPPD:S3451 3::FN13:EHV: | 0.10894
ERAS-2025-012 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | Base Case | 0.06277
ERAS-2025-012 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5263:IA-MVP::EHV: | 0.05759
ERAS-2025-012 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5269:IA-MVP::EHV: | 0.05917
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:HAWKSNEST3:8N82::EHV: | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL2 | 0.07446
ERAS-2025-012 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:PRI | 0.06283
ERAS-2025-012 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8P6 KING:::EHV: | 0.05697
ERAS-2025-012 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8P5 KING:::EHV: | 0.05652
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P23:345:OPPD:S3451-RAUN:::EHV: | 0.1082
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P22:345:OPPD:S3451-RAUN:::EHV: | 0.1082
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | 0.1082
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | Base Case | 0.08541
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.07209
ERAS-2025-012 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:PRI | 0.05215
ERAS-2025-012 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.0796
ERAS-2025-012 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.0796
ERAS-2025-012 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:PRI | 0.06585
ERAS-2025-012 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.05814
ERAS-2025-012 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5268:IA-MVP::EHV: | 0.06038
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601023 REDROCK3 345 1 | P12:345:XEL:ASK-ECL | 0.05325
ERAS-2025-012 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.05866
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL:8S98 NRH:::EHV: | 0.07959
ERAS-2025-012 | 01 NORTH | G00 29SP | 694076 STONE LK B2 345 694139 JUMP RIVR B3 345 1 | P23:345:XEL:8P6 KING:::EHV: | 0.05072
ERAS-2025-012 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P12:69:ATC-XEL:8E5_GD:ARPINB4:EAUCL3NLL:HV: | 0.06457
ERAS-2025-012 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE WHITE-SRX3-WHITE 3-SX :EHV: | 0.07164
ERAS-2025-012 | 01 NORTH | G00 29SP | 694076 STONE LK B2 345 694139 JUMP RIVR B3 345 1 | P23:500:XEL:CHISCO3:9P1::EHV: | 0.05435
ERAS-2025-012 | 01 NORTH | G00 29SP | 694076 STONE LK B2 345 694139 JUMP RIVR B3 345 1 | P23:500:XEL:CHISCO3:9P20::EHV: | 0.05435
ERAS-2025-012 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | Base Case | 0.08413
ERAS-2025-012 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P55:345:XEL:SHC BUS 1 | 0.07278
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P55:345:XEL:SHC BUS 1 | 0.07278
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:SHC BUS 1 | 0.08257
ERAS-2025-012 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P23:345:XEL:8N5 MNN:::EHV: | 0.05775
ERAS-2025-012 | 01 NORTH | G00 29SP | 694066 ROCKY RN B6 345 694082 WERNER W B4 345 1 | P12:345:ATC-XEL:W-13:NMAB5_345:BRIGGSRDNLL:EHV: | 0.0532
ERAS-2025-012 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | Base Case | 0.05788
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05993
ERAS-2025-012 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.0763
ERAS-2025-012 | 01 NORTH | G00 29SP | 661053 MANDAN 4 230 661091 NAPOLEON SW4 230 1 | P12:230:MDU:MANDAN:ROUGHRIDER:1: | 0.05507
ERAS-2025-012 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P12:345:XEL:MNTCELO3:QUARRY3:1 | 0.05842
ERAS-2025-012 | 01 NORTH | G00 29SP | 661053 MANDAN 4 230 661091 NAPOLEON SW4 230 1 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | 0.05136
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:WLM BUS 1 | 0.09927
ERAS-2025-012 | 01 NORTH | G00 29SP | 627217 BLUEBILL3 345 631198 COLBY3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05858
ERAS-2025-012 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | Base Case | 0.05814
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601018 CHIS CO3 345 1 | P23:345:XEL:8P34 KOL:::EHV: | 0.06529
ERAS-2025-012 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0702
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601018 CHIS CO3 345 1 | P23:345:XEL:8P41 CHI:::EHV: | 0.0648
ERAS-2025-012 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601018 CHIS CO3 345 1 | P12:345:XEL:CHISCO3:KOLMNLK3:1 AS | 0.0648
ERAS-2025-012 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | Base Case | 0.08893
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:NRH1 | 0.07448
ERAS-2025-012 | 01 NORTH | G00 29SP | 661053 MANDAN 4 230 661091 NAPOLEON SW4 230 1 | P12:230:OTP:ROUGHRIDER4:CENTER4:1 | 0.05507
ERAS-2025-012 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P23:345:MEC:WEBSTER:905::EHV: | 0.05023
ERAS-2025-012 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | Base Case | 0.07027
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL-SMMPA:8H8 PRI AS:::EHV: | 0.09471
ERAS-2025-012 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | Base Case | 0.06892
ERAS-2025-012 | 01 NORTH | G00 29SP | 635999 IRVINGTON3 345 636000 WEBSTER3 345 1 | Base Case | 0.0637
ERAS-2025-012 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07164
ERAS-2025-012 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07164
ERAS-2025-012 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07164
ERAS-2025-012 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P23:345:XEL:8N46- 8N45- 8N47 QRY:::EHV: | 0.06656
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL-SMMPA:8H9 PRI AS:::EHV: | 0.09543
ERAS-2025-012 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05766
ERAS-2025-012 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.05766
ERAS-2025-012 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P55:345:MEC:IRVINGTON | 0.05766
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.06754
ERAS-2025-012 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.06754
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:BOK2 | 0.05692
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:BOK1 | 0.05692
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P23:345:XEL:WILMART3:8S26 FUT::EHV: | 0.09535
ERAS-2025-012 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.0604
ERAS-2025-012 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | Base Case | 0.06277
ERAS-2025-012 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 661950 ELN345SHNT 3 345 1 | Base Case | 0.0541
ERAS-2025-012 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661950 ELN345SHNT 3 345 Z | Base Case | 0.0541
ERAS-2025-012 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P11:26:XEL:SHERCO33G:3 | 0.07292
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P11:26:XEL:SHERCO33G:3 | 0.07292
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.07317
ERAS-2025-012 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P23:345:XEL:8N28 SHC:::EHV: | 0.07317
ERAS-2025-012 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.0604
ERAS-2025-012 | 01 NORTH | G00 29SP | 635369 KOSSUTH 3 345 635999 IRVINGTON3 345 1 | Base Case | 0.0637
ERAS-2025-012 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.06296
ERAS-2025-012 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.06296
ERAS-2025-012 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.06296
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P11:24:XEL:SHERCO31G:1 | 0.07292
ERAS-2025-012 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P11:24:XEL:SHERCO31G:1 | 0.07292
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | Base Case | 0.07721
ERAS-2025-012 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P55:345:XEL:BIN | 0.06589
ERAS-2025-012 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P55:345:XEL:BIN | 0.06589
ERAS-2025-012 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P55:345:XEL:BIN | 0.06589
ERAS-2025-012 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.05766
ERAS-2025-012 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.05766
ERAS-2025-012 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P55:345:MEC:IRVINGTON | 0.05766
ERAS-2025-012 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631270 LASALLE 3 345 1 | Base Case | 0.07027
ERAS-2025-012 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1 | Base Case | 0.0541
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 635398 REMSEN 3 345 1 | Base Case | 0.06277
ERAS-2025-012 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | Base Case | 0.05343
ERAS-2025-012 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | Base Case | 0.07292
ERAS-2025-012 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | Base Case | 0.07292
ERAS-2025-012 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | Base Case | 0.0602
ERAS-2025-012 | 01 NORTH | G00 29SP | 661053 MANDAN 4 230 661091 NAPOLEON SW4 230 1 | Base Case | 0.05199
ERAS-2025-012 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | Base Case | 0.08239
ERAS-2025-012 | 01 NORTH | G00 29SP | 620480 DEUEL CO 3 345 620483 ASTORIA 3 345 1 | Base Case | 0.08678
ERAS-2025-012 | 01 NORTH | G00 29SP | 620417 BSSOUTH3 345 620480 DEUEL CO 3 345 1 | Base Case | 0.08678
ERAS-2025-012 | 01 NORTH | G00 29SP | 608602 SQBEAST4 230 657756 SQBUTTE4 230 Z2 | P12:230:MP-OTP:SQBEAST4:SQBUTTE4:Z1 | 0.06416
ERAS-2025-012 | 01 NORTH | G00 29SP | 608602 SQBEAST4 230 657756 SQBUTTE4 230 Z1 | P12:230:MP-OTP:SQBEAST4:SQBUTTE4:Z2 | 0.06416
ERAS-2025-012 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | Base Case | 0.05231
ERAS-2025-012 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | Base Case | 0.07027
ERAS-2025-012 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | Base Case | 0.07548
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:MEC:PONY CREEK OR SOUTHLAND | 0.05017
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05038
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.05923
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.05923
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05038
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05038
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.06749
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1 | 0.06112
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P11:24:AECI:1THLG3:1::: | 0.06112
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P21:345:AECI:THOMHL:THOMHLGSU3:1:: | 0.06112
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.05661
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.07724
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.05419
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.05451
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.06457
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.05673
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | P55:345:OPPD:S3740 3::FN13:EHV: | 0.05008
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 635014 OVERLAND 3 345 1 | P55:345:MEC:ORIENT | 0.05122
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | Base Case | 0.05419
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.10236
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.05747
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.05747
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | Base Case | 0.06112
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.08786
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | Base Case | 0.06447
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.08414
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.08451
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.08764
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P55:345:OPPD:S3451 3::FN13:EHV: | 0.06831
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P23:345:OPPD:S3451-RAUN:::EHV: | 0.06727
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P22:345:OPPD:S3451-RAUN:::EHV: | 0.06727
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | 0.06727
ERAS-2025-013 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Base Case | 0.08414
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.07905
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P11:24:AECI:1THLG3:1::: | 0.07034
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1 | 0.07034
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P21:345:AECI:THOMHL:THOMHLGSU3:1:: | 0.07034
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.06359
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.06305
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.07382
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.09297
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.06031
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.06079
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | Base Case | 0.06031
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | Base Case | 0.07034
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.09889
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.07766
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P22:345:GMO-OPPD:S3458-HOLT:::EHV: | 0.08157
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P23:345:OPPD:S3458-HOLT:::EHV: | 0.08157
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P44:345:OPPD:S3458-HOL&R1:::EHV: | 0.08157
ERAS-2025-019 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Base Case | 0.07322
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.0511
ERAS-2025-022 | 04 SOUTHEAST | G04 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.0511
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P51:25:WERE:WOLFCRK7:EHV: | 0.05714
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.05637
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.0564
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P55:345:XEL:SHC BUS 1 | 0.05639
ERAS-2025-023 | 04 SOUTHEAST | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | Base Case | 0.0564
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05784
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05784
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05784
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.07562
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P11:24:AECI:1THLG3:1::: | 0.0694
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1 | 0.0694
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P21:345:AECI:THOMHL:THOMHLGSU3:1:: | 0.0694
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.06197
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.0612
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.07329
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.09049
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.05823
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.05866
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | Base Case | 0.05823
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | Base Case | 0.0694
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.10083
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.08204
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P22:345:GMO-OPPD:S3458-HOLT:::EHV: | 0.08418
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P23:345:OPPD:S3458-HOLT:::EHV: | 0.08418
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P44:345:OPPD:S3458-HOL&R1:::EHV: | 0.08418
ERAS-2025-029 | 03 CENTRAL | G03 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Base Case | 0.07697
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05973
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05973
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.05973
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.07785
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1 | 0.07201
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P11:24:AECI:1THLG3:1::: | 0.07201
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P21:345:AECI:THOMHL:THOMHLGSU3:1:: | 0.07201
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.0637
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.09332
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.06028
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.06072
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.07549
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.06293
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345408 7OVERTON 345 1 | Base Case | 0.06028
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:22:KCPL:LACYGNE7:::EHV: | 0.10398
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 300044 7MCCRED 345 345230 7MONTGMRY 345 1 | Base Case | 0.07201
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:24:KCPL:IATAN 7:::EHV: | 0.08449
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.07983
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.08035
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | P51:26:WERE:JEC N 7:EHV: | 0.08345
ERAS-2025-031 | 03 CENTRAL | G00 29SP | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Base Case | 0.07983
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::37LOOSECREEK:EHV: | 0.0547
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::20LOOSECREEK:EHV: | 0.0547
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P23:345:AMMO:::17BLAND:EHV: | 0.05245
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AECI-AMMO:FRANKS:BLAND:1:: | 0.05242
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS3:EHV: | 0.05242
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS:EHV | 0.05242
ERAS-2025-034 | 03 CENTRAL | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | 300041 7FRANKS 345 344154 7BLAND 345 1 | 0.05242
ERAS-2025-035 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P51:25:WERE:WOLFCRK7:EHV: | 0.06877
ERAS-2025-035 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P23:345:WERE:WOLF-345-50:EHV: | 0.06748
ERAS-2025-035 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P11:345:WERE:WOLFU1-GEN:EHV: | 0.06714
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 661098 ELLENDL345 4 230 Z | Base Case | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | P55:345:XEL:SHC BUS 1 | 0.06714
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 661098 ELLENDL345 4 230 Z | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | 0.36365
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 661098 ELLENDL345 4 230 Z | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-ABR SIEBRCHT-1 :HV: | 0.46251
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 661098 ELLENDL345 4 230 Z | P43:034-230-345:MDU:ELLENDALE345:EL1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 661098 ELLENDL345 4 230 Z | P13:034-230-345:MDU:ELLENDALE345:1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 661098 ELLENDL345 4 230 Z | P23:345:MDU:ELLENDALE345:EL1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.05812
ERAS-2025-035 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.05812
ERAS-2025-035 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05175
ERAS-2025-035 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05175
ERAS-2025-035 | 01 NORTH | G00 29SP | 635223 PLYMOUTH 5 161 652566 SIOUXCY5 161 1 | P55:345:MEC:RAUN | 0.05433
ERAS-2025-035 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:MEC:CBEC | 0.05744
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.11341
ERAS-2025-035 | 01 NORTH | G00 29SP | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06503
ERAS-2025-035 | 01 NORTH | G00 29SP | 337909 8ANO% 500 515305 FTSMITH8 500 1 | Base Case | 0.06714
ERAS-2025-035 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:XEL:SHC BUS 1 | 0.06339
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:MEC:CBEC | 0.05744
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P55:345:MEC:OBRIEN | 0.13953
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:MEC:CBEC | 0.05744
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:906::EHV: | 0.14049
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05648
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.05648
ERAS-2025-035 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P55:345:XEL:CNC | 0.07023
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P23:345:MEC:OBRIEN:903::EHV: | 0.13967
ERAS-2025-035 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05603
ERAS-2025-035 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05603
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | 0.13653
ERAS-2025-035 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | Base Case | 0.06341
ERAS-2025-035 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P11:345:MEC:LOUISA:1 | 0.06341
ERAS-2025-035 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P23:345:MEC:SUB 93:954::EHV: | 0.0635
ERAS-2025-035 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:MEC:CBEC | 0.06381
ERAS-2025-035 | 01 NORTH | G00 29SP | 345435 7MAYWOOD 345 345992 7SPENCER 345 1 | P55:345:XEL:PRI1 | 0.06339
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.05648
ERAS-2025-035 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.08223
ERAS-2025-035 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338198 8DRIVER% 500 338400 8SANDYBAYOU% 500 1 | 0.05603
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | 0.05648
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.05648
ERAS-2025-035 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.07701
ERAS-2025-035 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.07701
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 0.05812
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8KEO%:8HOLND BTM%:1:EHV: | 0.05812
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05802
ERAS-2025-035 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06436
ERAS-2025-035 | 01 NORTH | G00 29SP | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 0.06146
ERAS-2025-035 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Base Case | 0.11333
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 338188 8SANS SOUCI% 500 338198 8DRIVER% 500 1 | 0.05175
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P12:500:EES:8SANS SOUCI%:8DRIVER%:1:EHV: | 0.05175
ERAS-2025-035 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05473
ERAS-2025-035 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | P55:345:MEC:GDMEC | 0.05441
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.08223
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:OPPD:S3458 3::FN13:EHV: | 0.08223
ERAS-2025-035 | 01 NORTH | G00 29SP | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | P23:500:EES:ISES:B6110::EHV: | 0.06503
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05831
ERAS-2025-035 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05627
ERAS-2025-035 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.05692
ERAS-2025-035 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05692
ERAS-2025-035 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:XEL:SHC BUS 1 | 0.06339
ERAS-2025-035 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06811
ERAS-2025-035 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05855
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05473
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05473
ERAS-2025-035 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.05519
ERAS-2025-035 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.05519
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | P55:345:MEC:GDMEC | 0.05441
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | P55:345:MEC:GDMEC | 0.05441
ERAS-2025-035 | 01 NORTH | G00 29SP | 338145 8ISES% 500 338156 8POWERLN_RD% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.05519
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 | 0.05047
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P12:345:AMMO::CALLAWAY:LOOSECREEK:EHV | 0.05047
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P12:345:AMMO::CALLAWAY:LOOSECREEK1:EHV: | 0.05047
ERAS-2025-035 | 01 NORTH | G00 29SP | 635018 NORTHBORO 3 345 635570 ORIENT 3 345 1 | Base Case | 0.05475
ERAS-2025-035 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 636398 HILLSSUBTRX3 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:WALCOTT:9-914::EHV: | 0.05111
ERAS-2025-035 | 01 NORTH | G00 29SP | 636398 HILLSSUBTRX3 345 636400 HILLS 3 345 Z | P23:345:MEC:WALCOTT:9-914::EHV: | 0.05111
ERAS-2025-035 | 01 NORTH | G00 29SP | 636398 HILLSSUBTRX3 345 636645 SUB T HSK 3 345 1 | P12:345:MEC:WALCOTT:HILLS-SUB 93:1 | 0.05111
ERAS-2025-035 | 01 NORTH | G00 29SP | 636398 HILLSSUBTRX3 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:SUB 93:944::EHV: | 0.05111
ERAS-2025-035 | 01 NORTH | G00 29SP | 636398 HILLSSUBTRX3 345 636400 HILLS 3 345 Z | P23:345:MEC:SUB 93:944::EHV: | 0.05111
ERAS-2025-035 | 01 NORTH | G00 29SP | 636398 HILLSSUBTRX3 345 636400 HILLS 3 345 Z | P12:345:MEC:WALCOTT:HILLS-SUB 93:1 | 0.05111
ERAS-2025-035 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P11:345:MEC:LOUISA:1 | 0.06341
ERAS-2025-035 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI | 0.07083
ERAS-2025-035 | 01 NORTH | G00 29SP | 601005 ELM CRK3 345 601022 PARKERS3 345 1 | P23:345:XEL:8P33 KOL:::EHV: | 0.05499
ERAS-2025-035 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P23:345:MEC:SUB 93:954::EHV: | 0.0635
ERAS-2025-035 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:MEC:CBEC | 0.06381
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI1 | 0.05844
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06961
ERAS-2025-035 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.09145
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05937
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI | 0.0687
ERAS-2025-035 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | P55:345:XEL:PRI1 | 0.06339
ERAS-2025-035 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.08922
ERAS-2025-035 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.08922
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07106
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::37LOOSECREEK:EHV: | 0.05452
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344154 7BLAND 345 1 | P23:345:AMMO:::20LOOSECREEK:EHV: | 0.05452
ERAS-2025-035 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI1 | 0.05622
ERAS-2025-035 | 01 NORTH | G00 29SP | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07226
ERAS-2025-035 | 01 NORTH | G00 29SP | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Base Case | 0.06341
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07077
ERAS-2025-035 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06255
ERAS-2025-035 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI | 0.05546
ERAS-2025-035 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.06177
ERAS-2025-035 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | 0.06177
ERAS-2025-035 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:SHC BUS 1 | 0.05001
ERAS-2025-035 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:901::EHV: | 0.08839
ERAS-2025-035 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P55:345:MEC:KOSSUTH | 0.08839
ERAS-2025-035 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:902::EHV: | 0.08839
ERAS-2025-035 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | P23:345:MEC:KOSSUTH:904::EHV: | 0.08839
ERAS-2025-035 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | P12:345:CE-ALTW:QUAD13-11:ROCKCK3:1 | 0.06255
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05821
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI1 | 0.05873
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:SHC BUS 1 | 0.10373
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.0584
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 635018 NORTHBORO 3 345 1 | Base Case | 0.05475
ERAS-2025-035 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI1 | 0.06773
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P55:345:XEL:PRI | 0.06916
ERAS-2025-035 | 01 NORTH | G00 29SP | 635017 ATCHISON 3 345 640139 COOPER 3 345 1 | Base Case | 0.05475
ERAS-2025-035 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.06551
ERAS-2025-035 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI1 | 0.0585
ERAS-2025-035 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06197
ERAS-2025-035 | 01 NORTH | G00 29SP | 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 | P23:345:AMMO:::17BLAND:EHV: | 0.05006
ERAS-2025-035 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI | 0.06086
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05852
ERAS-2025-035 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P55:345:XEL:PRI | 0.0577
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.05871
ERAS-2025-035 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06488
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 995834 661:ELLENDL 230 1 | P12:230:MDU:MERRICOURT:WISHEK:1: | 0.18039
ERAS-2025-035 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | P12:345:CE-ALTW:QUAD13-11:ROCKCK3:1 | 0.06488
ERAS-2025-035 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P12:500:EES-EAI:KEO:WMPEHV | 0.06177
ERAS-2025-035 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | P23:500:EES-EAI:KEO:B4931::EHV: | 0.05804
ERAS-2025-035 | 01 NORTH | G00 29SP | 631143 OTTUMWA3 345 635730 MONTEZUMA 3 345 1 | P55:345:MEC:SUB 93 | 0.05329
ERAS-2025-035 | 01 NORTH | G00 29SP | 338140 8HOLND BTM% 500 338145 8ISES% 500 1 | 337957 8KEO% 500 338056 CHALKBLUFFPV 500 1 | 0.06177
ERAS-2025-035 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P12:161:XEL-GRE:BYRON5:GRE-PLVLLY5:1 | 0.07427
ERAS-2025-035 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06817
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:PRI1 | 0.06914
ERAS-2025-035 | 01 NORTH | G00 29SP | 620358 BUFFALO3 345 620369 JAMESTN3 345 1 | Base Case | 0.06212
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P23:345:AMMO:::17BLAND:EHV: | 0.05226
ERAS-2025-035 | 01 NORTH | G00 29SP | 345445 7SKNKRVR 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:MONTEZUMA:901::EHV: | 0.05647
ERAS-2025-035 | 01 NORTH | G00 29SP | 345445 7SKNKRVR 345 636645 SUB T HSK 3 345 1 | P23:345:MEC:MONTEZUMA:903::EHV: | 0.05754
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AECI-AMMO:FRANKS:BLAND:1:: | 0.0521
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS3:EHV: | 0.0521
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | P12:345:AMMO::BLAND:FRANKS:EHV | 0.0521
ERAS-2025-035 | 01 NORTH | G00 29SP | 300041 7FRANKS 345 344327 7LOOSECRK 345 1 | 300041 7FRANKS 345 344154 7BLAND 345 1 | 0.0521
ERAS-2025-035 | 01 NORTH | G00 29SP | 635368 OBRIEN 3 345 635400 HIGHLAND 3 345 1 | Base Case | 0.07066
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 601072 SHEAS LK3 345 1 | Base Case | 0.0584
ERAS-2025-035 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | P23:500:EES-EAI:KEO:B4911::EHV: | 0.05576
ERAS-2025-035 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P23:345:XEL:8S85 NRH:::EHV: | 0.06543
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:PRI1 | 0.05931
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:PRI | 0.06104
ERAS-2025-035 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.05624
ERAS-2025-035 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P55:345:XEL:NRH1 | 0.06669
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | 337651 8WHT BLUFF% 500 337957 8KEO% 500 1 | 0.07486
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P12:500:EES:8WHT BLUFF%:8KEO%:1:EHV: | 0.07486
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI1 | 0.07049
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05897
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | 67020 MPC03839POI 345 657110 MPC4300 POI 345 1 | 0.06221
ERAS-2025-035 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P12:115:XEL:ASKING7:WILOWRV7:1 | 0.05779
ERAS-2025-035 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | P23:345:XEL:FUTURE 8S84 NRH:::EHV: | 0.0633
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P55:345:XEL:PRI | 0.05808
ERAS-2025-035 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES:8W.MEMPHIS%:8BHAM STEEL:1:EHV: | 0.05999
ERAS-2025-035 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338162 8W.MEMPHIS% 500 360075 8BHAM STEEL 500 1 | 0.05999
ERAS-2025-035 | 01 NORTH | G00 29SP | 660000 ABR JCT 115 661027 ELLENDL7 115 1 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | 0.36365
ERAS-2025-035 | 01 NORTH | G00 29SP | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | Base Case | 0.0563
ERAS-2025-035 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | P55:345:MEC:ORIENT | 0.06131
ERAS-2025-035 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:138:EES:8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL1:HV: | 0.05999
ERAS-2025-035 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTLNEWPORT:EHV: | 0.05999
ERAS-2025-035 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | P55:345:MEC:CBEC | 0.07108
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P55:345:XEL:WLM BUS 1 | 0.07874
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 995842 661:ELLENDL 115 1 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | 0.36365
ERAS-2025-035 | 01 NORTH | G00 29SP | 661027 ELLENDL7 115 995842 661:ELLENDL 115 1 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: | 0.36365
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06967
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601072 SHEAS LK3 345 1 | Base Case | 0.05871
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:PRI1 | 0.07086
ERAS-2025-035 | 01 NORTH | G00 29SP | 338156 8POWERLN_RD% 500 338187 8DELL% 500 1 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | 0.05635
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P55:345:XEL:PRI | 0.06524
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05461
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | 0.106
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P12:500:EES:8ANO%:8P.HILL%:1:EHV: | 0.05481
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | 337909 8ANO% 500 337922 8P.HILL% 500 1 | 0.05481
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.0594
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06455
ERAS-2025-035 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07106
ERAS-2025-035 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.1475
ERAS-2025-035 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:PRI1 | 0.05017
ERAS-2025-035 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P55:345:XEL:PRI | 0.05085
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 995834 661:ELLENDL 230 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.13722
ERAS-2025-035 | 01 NORTH | G00 29SP | 601014 AS KING3 345 601028 EAU CL 3 345 1 | Base Case | 0.05624
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P55:345:XEL:PRI | 0.06706
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:PRI1 | 0.10372
ERAS-2025-035 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.05001
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P55:345:XEL:PRI | 0.10466
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.07083
ERAS-2025-035 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | P11:26:XEL:SHERCO33G:3 | 0.05001
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337909 8ANO% 500 1 | P23:500:EES-EAI:8P.HILL%:B4335::EHV: | 0.05686
ERAS-2025-035 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:SHC BUS 1 | 0.09024
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.07089
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601083 TREMVAL3 345 1 | P12:345:XEL:ASK-ECL | 0.05165
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.10371
ERAS-2025-035 | 01 NORTH | G00 29SP | 631148 MORGN VLLY 3 345 636420 TIFFIN 3 345 1 | Base Case | 0.05858
ERAS-2025-035 | 01 NORTH | G00 29SP | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 | Base Case | 0.09147
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 995834 661:ELLENDL 230 1 | P12:230:MDU:NAPOLEON SW:WISHEK:1: | 0.18039
ERAS-2025-035 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 620358 BUFFALO3 345 1 | Base Case | 0.0591
ERAS-2025-035 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P23:345:XEL:FUTURE 8S49 HMP:::EHV: | 0.08537
ERAS-2025-035 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05485
ERAS-2025-035 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P23:345:XEL:8P5 KING:::EHV: | 0.08024
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631270 LASALLE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07106
ERAS-2025-035 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P22:345:XEL-SMMPA:8H15 PRI:::EHV: | 0.0581
ERAS-2025-035 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P12:345:XEL:PRISLD3:HMPTCNR3:1 | 0.0581
ERAS-2025-035 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | P12:345:XEL:ASK-ECL | 0.08197
ERAS-2025-035 | 01 NORTH | G00 29SP | 613060 BYRON 3 345 615306 GRE-PL VLLY3 345 1 | Base Case | 0.06824
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 635398 REMSEN 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 995842 661:ELLENDL 115 1 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-ABR SIEBRCHT-1 :HV: | 0.46251
ERAS-2025-035 | 01 NORTH | G00 29SP | 661027 ELLENDL7 115 995842 661:ELLENDL 115 1 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-ABR SIEBRCHT-1 :HV: | 0.46251
ERAS-2025-035 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P55:345:XEL:PRI | 0.07083
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.07111
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 995834 661:ELLENDL 230 1 | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.14102
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | P11:26:XEL:SHERCO33G:3 | 0.07116
ERAS-2025-035 | 01 NORTH | G00 29SP | 660000 ABR JCT 115 661027 ELLENDL7 115 1 | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-ABR SIEBRCHT-1 :HV: | 0.46251
ERAS-2025-035 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.08922
ERAS-2025-035 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.08922
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 995834 661:ELLENDL 230 1 | P12:230:MDU:BADGER WIND:WISHEK:1: | 0.15292
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230.0:UMZ:# N-1 #:: LINE BIGSTON4-BLAIR-ER4-1 :HV: | 0.07496
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P12:230:OTP:AUTO-SINGLE:BIGSTON4:BLAIR-ER41:HV: | 0.07496
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:MABELV:B5922::EHV: | 0.05151
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P23:345:XEL:8S23 WLM:::EHV: | 0.05518
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P23:345:XEL:WILMART3:8S23::EHV: | 0.05518
ERAS-2025-035 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:PRI1 | 0.05466
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615643 GRE-CEDRMT23 345 1 | P23:345:XEL:8N61 LYC:::EHV: | 0.06545
ERAS-2025-035 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | P55:345:MEC:ORIENT | 0.06131
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615643 GRE-CEDRMT23 345 1 | P23:345:XEL:LYONCO3:8N61::EHV: | 0.06545
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 613060 BYRON 3 345 1 | Base Case | 0.06975
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P23:345:MDU:ELLENDALE345:4803-4813: | 0.05401
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | P42:345:MDU:ELLENDALE345:BIG STONE SOUTH:4803-4813: | 0.05401
ERAS-2025-035 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | P55:345:MEC:CBEC | 0.07108
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P12:345:XEL:LYONCO3:HAWKSNEST3:1 | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL1 | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P55:345:MEC:RAUN | 0.11134
ERAS-2025-035 | 01 NORTH | G00 29SP | 601001 FORBES 2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:CNC | 0.05297
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | P55:345:XEL:PRI | 0.05573
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 995842 661:ELLENDL 115 1 | P13:034-230-345:MDU:ELLENDALE345:1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 995842 661:ELLENDL 115 1 | P23:345:MDU:ELLENDALE345:EL1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 661027 ELLENDL7 115 995842 661:ELLENDL 115 1 | P23:345:MDU:ELLENDALE345:EL1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 661027 ELLENDL7 115 995842 661:ELLENDL 115 1 | P13:034-230-345:MDU:ELLENDALE345:1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 636000 WEBSTER3 345 636010 LEHIGH 3 345 1 | Base Case | 0.07233
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601051 HMPT CNR3 345 2 | P55:345:XEL:PRI1 | 0.06102
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:HAWKSNEST3:8N82::EHV: | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL2 | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601028 EAU CL 3 345 694003 ARPIN B1 345 1 | P12:345:ATC-XEL:W-13:NMAB5_345:BRIGGSRDNLL:EHV: | 0.05279
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 995834 661:ELLENDL 230 1 | Base Case | 0.15292
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | P23:500:EES-EAI:SH_EHV:B5022::EHV: | 0.05992
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.11558
ERAS-2025-035 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | P21:345:MDU:ELLENDALE REACTOR:TWIN BROOKS:1: | 0.11722
ERAS-2025-035 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | P23:345:OTP:BSSOUTH3:3715::EHV: | 0.11722
ERAS-2025-035 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | P23:345:OTP:BSSOUTH3:3715(1)::EHV: | 0.11722
ERAS-2025-035 | 01 NORTH | G00 29SP | 601016 CHIS CO2 500 601017 CHIS-N 2 500 1 | P55:345:XEL:CNC | 0.05297
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615648 GRE-CDRMTL23 345 2 | P21:345:XEL:LYONCO3:GRE-CEDARMT23:1:EHV: | 0.07357
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615648 GRE-CDRMTL23 345 2 | P12:345:XEL:LYC-CMT | 0.07357
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615648 GRE-CDRMTL23 345 2 | P12:345:XEL:LYONCO3:GRE-CEDRMT23:1 | 0.07355
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SBL BUS 1 | 0.11969
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 615306 GRE-PL VLLY3 345 1 | Base Case | 0.07089
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:396 BKR SPK:::EHV: | 0.0626
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 615646 GRE-CDRMTH13 345 1 | P23:345:XEL:8S71 HNA:::EHV: | 0.06105
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 615646 GRE-CDRMTH13 345 1 | P23:345:XEL:HELENA3:8S71::EHV: | 0.06105
ERAS-2025-035 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:PRI1 | 0.09027
ERAS-2025-035 | 01 NORTH | G00 29SP | 660000 ABR JCT 115 661027 ELLENDL7 115 1 | P23:345:MDU:ELLENDALE345:EL1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 660000 ABR JCT 115 661027 ELLENDL7 115 1 | P43:034-230-345:MDU:ELLENDALE345:EL1: | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 615646 GRE-CDRMTH13 345 1 | P23:345:XEL:SPS 8S71 HNA:::EHV: | 0.06105
ERAS-2025-035 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P55:345:XEL:PRI | 0.09194
ERAS-2025-035 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.05115
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | Base Case | 0.05942
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 620483 ASTORIA 3 345 1 | Base Case | 0.07413
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615648 GRE-CDRMTL23 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.06372
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615648 GRE-CDRMTL23 345 2 | P23:345:XEL:LYONCO3:8N63::EHV: | 0.0637
ERAS-2025-035 | 01 NORTH | G00 29SP | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Base Case | 0.07291
ERAS-2025-035 | 01 NORTH | G00 29SP | 601003 PR ISLD3 345 601039 NROC 3 345 1 | Base Case | 0.06839
ERAS-2025-035 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.09028
ERAS-2025-035 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P12:69:ATC-XEL:8E5_GD:ARPINB4:EAUCL3NLL:HV: | 0.05927
ERAS-2025-035 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | P12:345:MEC-ITCM:OBRIEN:LAKEFIELD:1REACTOR:EHV: | 0.12699
ERAS-2025-035 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8E5 ECL BS:::EHV: | 0.05888
ERAS-2025-035 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P12:345:ATC-XEL:800000:ARPINB4:EAUCL3NLL:EHV: | 0.05888
ERAS-2025-035 | 01 NORTH | G00 29SP | 337860 8WRIGHTSVLE% 500 337957 8KEO% 500 1 | Base Case | 0.05336
ERAS-2025-035 | 01 NORTH | G00 29SP | 661098 ELLENDL345 4 230 995834 661:ELLENDL 230 1 | Base Case | 0.15292
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SBL BUS 1 | 0.11969
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 615643 GRE-CEDRMT23 345 1 | P23:345:GRE:CMT 302JB6:::EHV: | 0.05888
ERAS-2025-035 | 01 NORTH | G00 29SP | 615641 GRE-CDRMTCB3 345 615648 GRE-CDRMTL23 345 Z | P23:345:XEL:BKR:GRE_CEDARM:302JB7:EHV: | 0.05878
ERAS-2025-035 | 01 NORTH | G00 29SP | 615641 GRE-CDRMTCB3 345 615642 GRE-CEDRMT13 345 Z | P23:345:XEL:BKR:GRE_CEDARM:302JB7:EHV: | 0.05878
ERAS-2025-035 | 01 NORTH | G00 29SP | 694080 WERNER W B2 345 699359 N APPLETON 345 1 | Base Case | 0.05001
ERAS-2025-035 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:PRI1 | 0.07086
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P55:345:GRE:CDRMT | 0.13305
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:LYONCO3:8N60::EHV: | 0.13216
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | P23:345:XEL:8N60 LYC:::EHV: | 0.13207
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 620363 FORMAN 4 230 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.0722
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07924
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI1 | 0.07916
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL1 | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P12:345:XEL:LYONCO3:HAWKSNEST3:1 | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI | 0.07894
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE SPLT RK3-WHITE-SRX3-1 :EHV: | 0.1097
ERAS-2025-035 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P14:345:ITCM-MEC:LAKEFLD-OBRIEN 50MVAR:MN-SS | 0.08743
ERAS-2025-035 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | P12:345:MEC-ITCM:OBRIEN:LAKEFIELD:1REACTOR:EHV: | 0.08743
ERAS-2025-035 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:PRI1 | 0.0706
ERAS-2025-035 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:PRI1 | 0.0548
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P55:345:OPPD:S3451 3::FN13:EHV: | 0.11515
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601051 HMPT CNR3 345 2 | P55:345:XEL:PRI | 0.05617
ERAS-2025-035 | 01 NORTH | G00 29SP | 635399 CHEROKEE 3 345 635400 HIGHLAND 3 345 1 | Base Case | 0.07066
ERAS-2025-035 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5263:IA-MVP::EHV: | 0.05807
ERAS-2025-035 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5269:IA-MVP::EHV: | 0.05971
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:HAWKSNEST3:8N82::EHV: | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P55:345:XEL:HNL2 | 0.11985
ERAS-2025-035 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P55:345:XEL:PRI | 0.07083
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 615647 GRE-CDRMTH23 345 2 | P12:345:XEL:HELENA3:GRE-CDRMTH13:1 | 0.07048
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 615647 GRE-CDRMTH23 345 2 | P23:345:XEL:8S67 HNA:::EHV: | 0.07048
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 615647 GRE-CDRMTH23 345 2 | P22:345:GRE:CMT HEL 1:::EHV: | 0.07048
ERAS-2025-035 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8P6 KING:::EHV: | 0.0543
ERAS-2025-035 | 01 NORTH | G00 29SP | 694142 JUMP RIVR B6 345 699676 GARDR PK 345 1 | P23:345:XEL:8P5 KING:::EHV: | 0.05407
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P23:345:OPPD:S3451-RAUN:::EHV: | 0.11439
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P22:345:OPPD:S3451-RAUN:::EHV: | 0.11439
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | 0.11439
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652864 SIOUXCY-LNX3 345 1 | Base Case | 0.10368
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 620363 FORMAN 4 230 1 | P23:345:MDU:ELLENDALE345:EL1: | 0.0604
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 620363 FORMAN 4 230 1 | P13:034-230-345:MDU:ELLENDALE345:1: | 0.0604
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 620363 FORMAN 4 230 1 | P43:034-230-345:MDU:ELLENDALE345:EL1: | 0.0604
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | P23:345:XEL:8N63 LYC:::EHV: | 0.11558
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 661098 ELLENDL345 4 230 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.07268
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601087 STEEP BK LK3 345 2 | Base Case | 0.07926
ERAS-2025-035 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P55:345:XEL:PRI | 0.05372
ERAS-2025-035 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | 0.08922
ERAS-2025-035 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | P12:345:MEC-WAPA:RAUN:SIOUXCY:1 | 0.08922
ERAS-2025-035 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P55:345:XEL:PRI | 0.06706
ERAS-2025-035 | 01 NORTH | G00 29SP | 627217 BLUEBILL3 345 631198 COLBY3 345 1 | P23:345:MEC:WEBSTER:905::EHV: | 0.05541
ERAS-2025-035 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | 0.0584
ERAS-2025-035 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P23:345:ITCM:HCKRYCK3 5268:IA-MVP::EHV: | 0.06088
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 601077 HAWKSNEST 3 345 1 | Base Case | 0.07904
ERAS-2025-035 | 01 NORTH | G00 29SP | 661026 ELLENDL4 230 995842 661:ELLENDL 115 1 | Base Case | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 661027 ELLENDL7 115 995842 661:ELLENDL 115 1 | Base Case | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | P23:345:ITCM:ROCK CK3 182:IA-EC::EHV: | 0.06024
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL:8S98 NRH:::EHV: | 0.08233
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 661098 ELLENDL345 4 230 1 | P43:034-230-345:MDU:ELLENDALE345:EL1: | 0.06135
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 661098 ELLENDL345 4 230 1 | P23:345:MDU:ELLENDALE345:EL1: | 0.06135
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 661098 ELLENDL345 4 230 1 | P13:034-230-345:MDU:ELLENDALE345:1: | 0.06135
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:SHC BUS 1 | 0.07924
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI1 | 0.07916
ERAS-2025-035 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | P12:69:ATC-XEL:8E5_GD:ARPINB4:EAUCL3NLL:HV: | 0.06479
ERAS-2025-035 | 01 NORTH | G00 29SP | 627217 BLUEBILL3 345 631198 COLBY3 345 1 | P55:345:MEC:WEBSTER | 0.05322
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P55:345:XEL:PRI | 0.07894
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE WHITE-SRX3-WHITE 3-SX :EHV: | 0.1097
ERAS-2025-035 | 01 NORTH | G00 29SP | 631193 HUNTLEY3 345 631197 LEDYARD3 345 1 | Base Case | 0.09033
ERAS-2025-035 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P55:345:XEL:SHC BUS 1 | 0.06324
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P55:345:XEL:SHC BUS 1 | 0.06324
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:SHC BUS 1 | 0.10387
ERAS-2025-035 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P23:345:XEL:8N5 MNN:::EHV: | 0.05232
ERAS-2025-035 | 01 NORTH | G00 29SP | 694066 ROCKY RN B6 345 694082 WERNER W B4 345 1 | P12:345:ATC-XEL:W-13:NMAB5_345:BRIGGSRDNLL:EHV: | 0.05222
ERAS-2025-035 | 01 NORTH | G00 29SP | 601004 WILMART3 345 631193 HUNTLEY3 345 1 | Base Case | 0.05482
ERAS-2025-035 | 01 NORTH | G00 29SP | 615647 GRE-CDRMTH23 345 615648 GRE-CDRMTL23 345 Z | P23:345:XEL:BKR:GRE_CEDARM:302JB4:EHV: | 0.06174
ERAS-2025-035 | 01 NORTH | G00 29SP | 615642 GRE-CEDRMT13 345 615646 GRE-CDRMTH13 345 Z | P23:345:XEL:BKR:GRE_CEDARM:302JB7:EHV: | 0.06154
ERAS-2025-035 | 01 NORTH | G00 29SP | 620327 HANKSON4 230 620363 FORMAN 4 230 1 | P12:230:MDU:MERRICOURT:WISHEK:1: | 0.07903
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:SHC BUS 1 | 0.06415
ERAS-2025-035 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1 | P12:345:OTP:BUFFALO3:JAMESTN3:1 | 0.0883
ERAS-2025-035 | 01 NORTH | G00 29SP | 615647 GRE-CDRMTH23 345 615648 GRE-CDRMTL23 345 Z | P21:345:XEL:LYONCO3:GRE-CEDARMT23:1:EHV: | 0.05129
ERAS-2025-035 | 01 NORTH | G00 29SP | 615647 GRE-CDRMTH23 345 615648 GRE-CDRMTL23 345 Z | P12:345:XEL:LYC-CMT | 0.05129
ERAS-2025-035 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 661950 ELN345SHNT 3 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07399
ERAS-2025-035 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P12:345:XEL:MNTCELO3:QUARRY3:1 | 0.05288
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661950 ELN345SHNT 3 345 Z | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07399
ERAS-2025-035 | 01 NORTH | G00 29SP | 615647 GRE-CDRMTH23 345 615648 GRE-CDRMTL23 345 Z | P23:345:GRE:CMT 302JB4:::EHV: | 0.05055
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:WLM BUS 1 | 0.11721
ERAS-2025-035 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 661950 ELN345SHNT 3 345 1 | P55:345:XEL:BOK2 | 0.06103
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661950 ELN345SHNT 3 345 Z | P55:345:XEL:BOK1 | 0.06103
ERAS-2025-035 | 01 NORTH | G00 29SP | 627217 BLUEBILL3 345 631198 COLBY3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.06456
ERAS-2025-035 | 01 NORTH | G00 29SP | 601083 TREMVAL3 345 694098 NMA B5 345 345 1 | Base Case | 0.0584
ERAS-2025-035 | 01 NORTH | G00 29SP | 631197 LEDYARD3 345 635369 KOSSUTH 3 345 1 | Base Case | 0.05124
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601077 HAWKSNEST 3 345 1 | Base Case | 0.07904
ERAS-2025-035 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.07111
ERAS-2025-035 | 01 NORTH | G00 29SP | 601006 SPLT RK3 345 652536 WHITE-SRX3 345 1 | Base Case | 0.12096
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P55:345:XEL:NRH1 | 0.0766
ERAS-2025-035 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P23:345:MEC:WEBSTER:905::EHV: | 0.05455
ERAS-2025-035 | 01 NORTH | G00 29SP | 601002 ADAMS 3 345 631144 MITCHLCO3 345 1 | Base Case | 0.07116
ERAS-2025-035 | 01 NORTH | G00 29SP | 601050 HELENA 3 345 601051 HMPT CNR3 345 2 | Base Case | 0.05729
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL-SMMPA:8H8 PRI AS:::EHV: | 0.09783
ERAS-2025-035 | 01 NORTH | G00 29SP | 636003 BEAVER CRK 3 345 636010 LEHIGH 3 345 1 | Base Case | 0.07291
ERAS-2025-035 | 01 NORTH | G00 29SP | 620327 HANKSON4 230 620363 FORMAN 4 230 1 | P12:230:OTP::HANKSON4:WAHPETN4 | 0.06576
ERAS-2025-035 | 01 NORTH | G00 29SP | 620327 HANKSON4 230 620363 FORMAN 4 230 1 | P12:230:OTP:HANKSON4:WAHPETN4:1 | 0.06576
ERAS-2025-035 | 01 NORTH | G00 29SP | 635999 IRVINGTON3 345 636000 WEBSTER3 345 1 | Base Case | 0.06916
ERAS-2025-035 | 01 NORTH | G00 29SP | 601008 BG OAKS3 345 658047 ALEXMRES3 345 1 | P23:345:XEL:8N46- 8N45- 8N47 QRY:::EHV: | 0.06025
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | P23:345:XEL-SMMPA:8H9 PRI AS:::EHV: | 0.09824
ERAS-2025-035 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.06186
ERAS-2025-035 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P55:345:MEC:WEBSTER | 0.05098
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 2 | P13:345-18.0:UMZ:# N-1 #:: 3WND DEERCREK-BE3-DEERC_CT-BEG-DEERC_ST-BEG-1 DEERCRK KU1A:EHV: | 0.05561
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 2 | P12:345.0:UMZ:# N-1 #:: LINE WHITE 3-DEERCREK-BE3-1 :EHV: | 0.05561
ERAS-2025-035 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.06186
ERAS-2025-035 | 01 NORTH | G00 29SP | 631206 QUINN3 345 636197 N FRANKLIN 3 345 1 | P55:345:MEC:IRVINGTON | 0.06186
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 601087 STEEP BK LK3 345 2 | Base Case | 0.07926
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.06737
ERAS-2025-035 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P12:345:XEL-OTP:BISON3:MAPLER3:1 | 0.06737
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:BOK2 | 0.05763
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P55:345:XEL:BOK1 | 0.05763
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 1 | P13:345-18.0:UMZ:# N-1 #:: 3WND DEERCREK-BE3-DEERC_CT-BEG-DEERC_ST-BEG-1 DEERCRK KU1A:EHV: | 0.05005
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 1 | P12:345.0:UMZ:# N-1 #:: LINE WHITE 3-DEERCREK-BE3-1 :EHV: | 0.05005
ERAS-2025-035 | 01 NORTH | G00 29SP | 627062 BISON 3 345 627217 BLUEBILL3 345 1 | P23:345:MEC:WEBSTER:905::EHV: | 0.05541
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | P23:345:XEL:WILMART3:8S26 FUT::EHV: | 0.1155
ERAS-2025-035 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.06529
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 620363 FORMAN 4 230 1 | Base Case | 0.0604
ERAS-2025-035 | 01 NORTH | G00 29SP | 635398 REMSEN 3 345 635399 CHEROKEE 3 345 1 | Base Case | 0.07066
ERAS-2025-035 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 661950 ELN345SHNT 3 345 1 | Base Case | 0.07129
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661950 ELN345SHNT 3 345 Z | Base Case | 0.07129
ERAS-2025-035 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P11:26:XEL:SHERCO33G:3 | 0.06335
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P11:26:XEL:SHERCO33G:3 | 0.06335
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06355
ERAS-2025-035 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P23:345:XEL:8N28 SHC:::EHV: | 0.06355
ERAS-2025-035 | 01 NORTH | G00 29SP | 631198 COLBY3 345 631199 KILLDEER3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.06529
ERAS-2025-035 | 01 NORTH | G00 29SP | 660000 ABR JCT 115 661027 ELLENDL7 115 1 | Base Case | 0.25795
ERAS-2025-035 | 01 NORTH | G00 29SP | 635369 KOSSUTH 3 345 635999 IRVINGTON3 345 1 | Base Case | 0.06916
ERAS-2025-035 | 01 NORTH | G00 29SP | 627062 BISON 3 345 627217 BLUEBILL3 345 1 | P55:345:MEC:WEBSTER | 0.05322
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 2 | P55:345:MEC:RAUN | 0.05581
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07351
ERAS-2025-035 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07351
ERAS-2025-035 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:345:OTP:JAMESTN3:CENTER3:1 | 0.07351
ERAS-2025-035 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.05664
ERAS-2025-035 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.05664
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:345:XEL-OTP:BISON3:BUFFALO3:1 | 0.05664
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | P11:24:XEL:SHERCO31G:1 | 0.06335
ERAS-2025-035 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | P11:24:XEL:SHERCO31G:1 | 0.06335
ERAS-2025-035 | 01 NORTH | G00 29SP | 620362 OAKES 4 230 661098 ELLENDL345 4 230 1 | Base Case | 0.06135
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 1 | P55:345:MEC:RAUN | 0.05023
ERAS-2025-035 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P12:230:MDU:MERRICOURT:WISHEK:1: | 0.0993
ERAS-2025-035 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P12:230:MDU:MERRICOURT:WISHEK:1: | 0.0993
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P12:230:MDU:MERRICOURT:WISHEK:1: | 0.0993
ERAS-2025-035 | 01 NORTH | G00 29SP | 627062 BISON 3 345 631197 LEDYARD3 345 1 | P23:345:MEC:WEBSTER:905::EHV: | 0.05541
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | Base Case | 0.08163
ERAS-2025-035 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | P55:345:XEL:BIN | 0.05867
ERAS-2025-035 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | P55:345:XEL:BIN | 0.05867
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | P55:345:XEL:BIN | 0.05867
ERAS-2025-035 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P12:345:MEC:WEBSTER:IRVINGTON:1REACTOR:EHV: | 0.06186
ERAS-2025-035 | 01 NORTH | G00 29SP | 627062 BISON 3 345 631197 LEDYARD3 345 1 | P55:345:MEC:WEBSTER | 0.05322
ERAS-2025-035 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P23:345:MEC:IRVINGTON:903::EHV: | 0.06186
ERAS-2025-035 | 01 NORTH | G00 29SP | 631199 KILLDEER3 345 631206 QUINN3 345 1 | P55:345:MEC:IRVINGTON | 0.06186
ERAS-2025-035 | 01 NORTH | G00 29SP | 631139 HAZLTON3 345 631270 LASALLE 3 345 1 | Base Case | 0.07116
ERAS-2025-035 | 01 NORTH | G00 29SP | 620416 TWIN BRKS 3 345 620417 BSSOUTH3 345 1 | Base Case | 0.07129
ERAS-2025-035 | 01 NORTH | G00 29SP | 620327 HANKSON4 230 620363 FORMAN 4 230 1 | Base Case | 0.07064
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 635398 REMSEN 3 345 1 | Base Case | 0.07066
ERAS-2025-035 | 01 NORTH | G00 29SP | 631142 ARNOLD 3 345 631148 MORGN VLLY 3 345 1 | Base Case | 0.05489
ERAS-2025-035 | 01 NORTH | G00 29SP | 601067 BISON 3 345 658049 ALXLNRCTRT 345 1 | Base Case | 0.06335
ERAS-2025-035 | 01 NORTH | G00 29SP | 658047 ALEXMRES3 345 658049 ALXLNRCTRT 345 Z1 | Base Case | 0.06335
ERAS-2025-035 | 01 NORTH | G00 29SP | 601039 NROC 3 345 601051 HMPT CNR3 345 1 | Base Case | 0.06437
ERAS-2025-035 | 01 NORTH | G00 29SP | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | Base Case | 0.10372
ERAS-2025-035 | 01 NORTH | G00 29SP | 620480 DEUEL CO 3 345 620483 ASTORIA 3 345 1 | Base Case | 0.07458
ERAS-2025-035 | 01 NORTH | G00 29SP | 620417 BSSOUTH3 345 620480 DEUEL CO 3 345 1 | Base Case | 0.07458
ERAS-2025-035 | 01 NORTH | G00 29SP | 601031 BRKNGCO3 345 652537 WHITE 3 345 2 | Base Case | 0.05346
ERAS-2025-035 | 01 NORTH | G00 29SP | 620769 JMS SHUNT 3 345 661952 ELN345SHNT23 345 1 | Base Case | 0.08163
ERAS-2025-035 | 01 NORTH | G00 29SP | 620369 JAMESTN3 345 620769 JMS SHUNT 3 345 Z | Base Case | 0.08163
ERAS-2025-035 | 01 NORTH | G00 29SP | 661097 ELLENDL345 3 345 661952 ELN345SHNT23 345 Z | Base Case | 0.08163
ERAS-2025-035 | 01 NORTH | G00 29SP | 337808 8MABELVALE% 500 337860 8WRIGHTSVLE% 500 1 | Base Case | 0.05282
ERAS-2025-035 | 01 NORTH | G00 29SP | 631144 MITCHLCO3 345 631270 LASALLE 3 345 1 | Base Case | 0.07116
ERAS-2025-035 | 01 NORTH | G00 29SP | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | Base Case | 0.07981